## Cover
TIMES-Ireland Model
Document type: | New Technologies
Sector(s): | Power sector (PWR)
Purpose: | Specify DH extension costs
Original developer(s): | Jason Mc Guire ( MaREI, jason.mcguire@ucc.ie)
Olexandr Balyk ( MaREI, olexandr.balyk@ucc.ie)
Current maintainer(s): | Jason Mc Guire ( MaREI, jason.mcguire@ucc.ie)
Olexandr Balyk ( MaREI, olexandr.balyk@ucc.ie)
Part of TIM version: | 1
Model repository: | https://github.com/MaREI-EPMG/TIMES-Ireland-model
Licence: | CC BY-NC-SA 4.0 (unless specified otherwise)
https://creativecommons.org/licenses/by-nc-sa/4.0/

## Regions
|  | IE | National | IE-CW | IE-D | IE-KE | IE-KK | IE-LS | IE-LD | IE-LH | IE-MH | IE-OY | IE-WH | IE-WX | IE-WW | IE-CE | IE-CO | IE-KY | IE-LK | IE-TA | IE-WD | IE-G | IE-LM | IE-MO | IE-RN | IE-SO | IE-CN | IE-DL | IE-MN
1
Development |  | IE | National | IE-CW | IE-D | IE-KE | IE-KK | IE-LS | IE-LD | IE-LH | IE-MH | IE-OY | IE-WH | IE-WX | IE-WW | IE-CE | IE-CO | IE-KY | IE-LK | IE-TA | IE-WD | IE-G | IE-LM | IE-MO | IE-RN | IE-SO | IE-CN | IE-DL | IE-MN
Single-region |  | IE | *National | *IE-CW | *IE-D | *IE-KE | *IE-KK | *IE-LS | *IE-LD | *IE-LH | *IE-MH | *IE-OY | *IE-WH | *IE-WX | *IE-WW | *IE-CE | *IE-CO | *IE-KY | *IE-LK | *IE-TA | *IE-WD | *IE-G | *IE-LM | *IE-MO | *IE-RN | *IE-SO | *IE-CN | *IE-DL | *IE-MN
Multi-region |  | *IE | National | IE-CW | IE-D | IE-KE | IE-KK | IE-LS | IE-LD | IE-LH | IE-MH | IE-OY | IE-WH | IE-WX | IE-WW | IE-CE | IE-CO | IE-KY | IE-LK | IE-TA | IE-WD | IE-G | IE-LM | IE-MO | IE-RN | IE-SO | IE-CN | IE-DL | IE-MN
Code | County name
IE-CW | Carlow
IE-CN | Cavan
IE-CE | Clare
IE-CO | Cork
IE-DL | Donegal
IE-D | Dublin
IE-G | Galway
IE-KY | Kerry
IE-KE | Kildare
IE-KK | Kilkenny
IE-LS | Laois
IE-LM | Leitrim
IE-LK | Limerick
IE-LD | Longford
IE-LH | Louth
IE-MO | Mayo
IE-MH | Meath
IE-MN | Monaghan
IE-OY | Offaly
IE-RN | Roscommon
IE-SO | Sligo
IE-TA | Tipperary
IE-WD | Waterford
IE-WH | Westmeath
IE-WX | Wexford
IE-WW | Wicklow
Source: https://en.wikipedia.org/wiki/ISO_3166-2:IE

## Fuel Techs
Processes
|  |  | ~FI_T |  |  |  | ~FI_Process
Region | TechName | Comm-IN | Comm-OUT | NCAP_COST | CAP_BND | EFF | Sets | Region | TechName | TechDesc | Tact | Tcap | Tslvl | PrimaryCG | Vintage
Region Name | *Technology Name | Input Commodity | Output Commodity |  |  | Efficiency | *Process Set Membership | Region Name | Technology Name | Technology Description | Activity Unit | Capacity Unit | TimeSlice level of Process Activity | Primary Commodity Group | Vintage Tracking
| *Units | [5 empty] | *
IE,National,IE-CW,IE-D,IE-KE,IE-KK,IE-LS,IE-LD,IE-LH,IE-MH,IE-OY,IE-WH,IE-WX,IE-WW,IE-CE,IE-CO,IE-KY,IE-LK,IE-TA,IE-WD,IE-G,IE-LM,IE-MO,IE-RN,IE-SO,IE-CN,IE-DL,IE-MN | FT-RSDHET_C | HETD | RSDHET_Apt,RSDHET_Att,RSDHET_Det |  |  | 1 | PRE | IE,National,IE-CW,IE-D,IE-KE,IE-KK,IE-LS,IE-LD,IE-LH,IE-MH,IE-OY,IE-WH,IE-WX,IE-WW,IE-CE,IE-CO,IE-KY,IE-LK,IE-TA,IE-WD,IE-G,IE-LM,IE-MO,IE-RN,IE-SO,IE-CN,IE-DL,IE-MN | FT-RSDHET_C | RSD Heat to Residential City | PJ | PJa | DayNite
IE,National,IE-CW,IE-D,IE-KE,IE-KK,IE-LS,IE-LD,IE-LH,IE-MH,IE-OY,IE-WH,IE-WX,IE-WW,IE-CE,IE-CO,IE-KY,IE-LK,IE-TA,IE-WD,IE-G,IE-LM,IE-MO,IE-RN,IE-SO,IE-CN,IE-DL,IE-MN | FT-RSDHET_1 | HETD | RSDHET_Apt,RSDHET_Att,RSDHET_Det |  |  | 1 | PRE | IE,National,IE-CW,IE-D,IE-KE,IE-KK,IE-LS,IE-LD,IE-LH,IE-MH,IE-OY,IE-WH,IE-WX,IE-WW,IE-CE,IE-CO,IE-KY,IE-LK,IE-TA,IE-WD,IE-G,IE-LM,IE-MO,IE-RN,IE-SO,IE-CN,IE-DL,IE-MN | FT-RSDHET_1 | RSD Heat to Residential High Density Urban | PJ | PJa | DayNite
IE,National,IE-CW,IE-D,IE-KE,IE-KK,IE-LS,IE-LD,IE-LH,IE-MH,IE-OY,IE-WH,IE-WX,IE-WW,IE-CE,IE-CO,IE-KY,IE-LK,IE-TA,IE-WD,IE-G,IE-LM,IE-MO,IE-RN,IE-SO,IE-CN,IE-DL,IE-MN | FT-RSDHET_2 | HETD | RSDHET_Apt,RSDHET_Att,RSDHET_Det |  |  | 1 | PRE | IE,National,IE-CW,IE-D,IE-KE,IE-KK,IE-LS,IE-LD,IE-LH,IE-MH,IE-OY,IE-WH,IE-WX,IE-WW,IE-CE,IE-CO,IE-KY,IE-LK,IE-TA,IE-WD,IE-G,IE-LM,IE-MO,IE-RN,IE-SO,IE-CN,IE-DL,IE-MN | FT-RSDHET_2 | RSD Heat to Residential Medium Density Urban | PJ | PJa | DayNite
IE,National,IE-CW,IE-D,IE-KE,IE-KK,IE-LS,IE-LD,IE-LH,IE-MH,IE-OY,IE-WH,IE-WX,IE-WW,IE-CE,IE-CO,IE-KY,IE-LK,IE-TA,IE-WD,IE-G,IE-LM,IE-MO,IE-RN,IE-SO,IE-CN,IE-DL,IE-MN | FT-RSDHET_3 | HETD | RSDHET_Apt,RSDHET_Att,RSDHET_Det |  |  | 1 | PRE | IE,National,IE-CW,IE-D,IE-KE,IE-KK,IE-LS,IE-LD,IE-LH,IE-MH,IE-OY,IE-WH,IE-WX,IE-WW,IE-CE,IE-CO,IE-KY,IE-LK,IE-TA,IE-WD,IE-G,IE-LM,IE-MO,IE-RN,IE-SO,IE-CN,IE-DL,IE-MN | FT-RSDHET_3 | RSD Heat to Residential Low Density Urban | PJ | PJa | DayNite
IE,National,IE-CW,IE-D,IE-KE,IE-KK,IE-LS,IE-LD,IE-LH,IE-MH,IE-OY,IE-WH,IE-WX,IE-WW,IE-CE,IE-CO,IE-KY,IE-LK,IE-TA,IE-WD,IE-G,IE-LM,IE-MO,IE-RN,IE-SO,IE-CN,IE-DL,IE-MN | FT-SRVHET_C | HETD | SRVHET |  |  | 1 | PRE | IE,National,IE-CW,IE-D,IE-KE,IE-KK,IE-LS,IE-LD,IE-LH,IE-MH,IE-OY,IE-WH,IE-WX,IE-WW,IE-CE,IE-CO,IE-KY,IE-LK,IE-TA,IE-WD,IE-G,IE-LM,IE-MO,IE-RN,IE-SO,IE-CN,IE-DL,IE-MN | FT-SRVHET_C | District heating (SRV) in City | PJ | PJa | DayNite
IE,National,IE-CW,IE-D,IE-KE,IE-KK,IE-LS,IE-LD,IE-LH,IE-MH,IE-OY,IE-WH,IE-WX,IE-WW,IE-CE,IE-CO,IE-KY,IE-LK,IE-TA,IE-WD,IE-G,IE-LM,IE-MO,IE-RN,IE-SO,IE-CN,IE-DL,IE-MN | FT-SRVHET_1 | HETD | SRVHET |  |  | 1 | PRE | IE,National,IE-CW,IE-D,IE-KE,IE-KK,IE-LS,IE-LD,IE-LH,IE-MH,IE-OY,IE-WH,IE-WX,IE-WW,IE-CE,IE-CO,IE-KY,IE-LK,IE-TA,IE-WD,IE-G,IE-LM,IE-MO,IE-RN,IE-SO,IE-CN,IE-DL,IE-MN | FT-SRVHET_1 | District heating (SRV) in High Urban Density | PJ | PJa | DayNite
IE,National,IE-CW,IE-D,IE-KE,IE-KK,IE-LS,IE-LD,IE-LH,IE-MH,IE-OY,IE-WH,IE-WX,IE-WW,IE-CE,IE-CO,IE-KY,IE-LK,IE-TA,IE-WD,IE-G,IE-LM,IE-MO,IE-RN,IE-SO,IE-CN,IE-DL,IE-MN | FT-SRVHET_2 | HETD | SRVHET |  |  | 1 | PRE | IE,National,IE-CW,IE-D,IE-KE,IE-KK,IE-LS,IE-LD,IE-LH,IE-MH,IE-OY,IE-WH,IE-WX,IE-WW,IE-CE,IE-CO,IE-KY,IE-LK,IE-TA,IE-WD,IE-G,IE-LM,IE-MO,IE-RN,IE-SO,IE-CN,IE-DL,IE-MN | FT-SRVHET_2 | District heating (SRV) in Medium Urban Density | PJ | PJa | DayNite
IE,National,IE-CW,IE-D,IE-KE,IE-KK,IE-LS,IE-LD,IE-LH,IE-MH,IE-OY,IE-WH,IE-WX,IE-WW,IE-CE,IE-CO,IE-KY,IE-LK,IE-TA,IE-WD,IE-G,IE-LM,IE-MO,IE-RN,IE-SO,IE-CN,IE-DL,IE-MN | FT-SRVHET_3 | HETD | SRVHET |  |  | 1 | PRE | IE,National,IE-CW,IE-D,IE-KE,IE-KK,IE-LS,IE-LD,IE-LH,IE-MH,IE-OY,IE-WH,IE-WX,IE-WW,IE-CE,IE-CO,IE-KY,IE-LK,IE-TA,IE-WD,IE-G,IE-LM,IE-MO,IE-RN,IE-SO,IE-CN,IE-DL,IE-MN | FT-SRVHET_3 | District heating (SRV) in Low Urban Density | PJ | PJa | DayNite
IE,National,IE-CW,IE-D,IE-KE,IE-KK,IE-LS,IE-LD,IE-LH,IE-MH,IE-OY,IE-WH,IE-WX,IE-WW,IE-CE,IE-CO,IE-KY,IE-LK,IE-TA,IE-WD,IE-G,IE-LM,IE-MO,IE-RN,IE-SO,IE-CN,IE-DL,IE-MN | HET-GRID_EXP | HETC | HETD | 0.01 |  | 0.86 | PRE | IE,National,IE-CW,IE-D,IE-KE,IE-KK,IE-LS,IE-LD,IE-LH,IE-MH,IE-OY,IE-WH,IE-WX,IE-WW,IE-CE,IE-CO,IE-KY,IE-LK,IE-TA,IE-WD,IE-G,IE-LM,IE-MO,IE-RN,IE-SO,IE-CN,IE-DL,IE-MN | HET-GRID_EXP | Heat Grid expanison | PJ | PJa | DayNite

## DH_ Supply
https://www.seai.ie/publications/District-Heating-and-Cooling-Appendix-D-Geothermal.pdf | [7 empty] | Storage |  |  | https://iea-etsap.org/workshop/hybrid_winter_nov2021/07%20-%20ETSAP%20workshop_Dmytro%C2%A0Romanchenko.pdf
Data Centres setup in SubRES_SRV_DC_Excess Heat | [10 empty] | https://secure.dccae.gov.ie/GSI_DOWNLOAD/Geoenergy/Reports/GSI_Assessment_of_GeoDH_for_Ireland_Nov2020_v2.pdf
[6 empty] | ~FI_T | [13 empty] | ~FI_Process
TechName | TechDesc | Comm-IN | Comm-IN-A | Comm-OUT | CURR | START | *Min. Capacity | EFF | STG_EFF | STG_LOSS | INPUT | LIFE | AFA | INVCOST | FIXOM | VAROM | CAP2ACT | CAPBND | ILED | Sets | TechName | TechDesc | Tact | Tcap | Tslvl | PrimaryCG | Vintage
\I:Technology Name | Technology Description | Input Commodity |  | Output Commodity | Currency unit | technological data | Minimum Capacity for technology (MW) | Efficiency | Sorage Efficiency | Storage Loss | PJ | Lifetime | Annual Availability Factor | Investment Cost | Fixed O&M Cost | Variable O&M Cost | Units of activity/unit of capacity | Capacity Bound | Construction time | \I: Process Set Membership | Technology Name | Technology Description | Activity Unit | Capacity Unit | Timeslice Operational Level | Operational Commodity Group | Vintage Tracking
*Units | [5 empty] | Year | [5 empty] | Years |  | MEUR/GW | MEUR/GW/yr | MEUR/PJ | Factor |  | Years | *Units
DH_ELC_BLR_N1 | Electric Boiler for District Heating | PWRELC |  | HETC | MEUR2015 | 2022 | 5 | 0.99 |  |  |  | 20 | 0.99 | 70 | 1.07 | 0.028539 | 0.031536 |  | 1 | HPL | DH_ELC_BLR_N1 | Electric Boiler for District Heating | PJ | GW
DH_GAS_BLR_N1 | Gas Boiler for District Heating | PWRGAS,PWRBGS |  | HETC | MEUR2015 | 2022 | 0.5 | 0.94 |  |  |  | 25 | 0.99 | 60 | 1.95 | 0.034881 | 0.031536 |  | 1 | HPL | DH_GAS_BLR_N1 | Gas Boiler for District Heating | PJ | GW
DH_ELC_GEO1200_N1 | Geothermal and electric HP 1200m | PWRELC |  | HETC | MEUR2015 | 2022 | 10.93 | 5.4809 |  |  |  | 25 | 0.98 | 2970 | 23.2 | 0.17314 | 0.031536 | 15 | 5 | HPL | DH_ELC_GEO1200_N1 | Geothermal and electric HP 1200m | PJ | GW
|  |  | PWRAHT | [7 empty] | 0.81755 | [8 empty] | HPL | DH_SOL_N1 | Solar District Heating | PJ | GW
DH_SOL_N1 | Solar District Heating | PWRSOL |  | HETC | MEUR2015 | 2022 |  | 0.45 |  |  |  | 30 | 0.995 | 310 | 0.06081 | 0.0066591 | 0.031536 | 15 | 1 | HPL | DH_AHP_GEO1200_N1 | Geothermal and absorption HP 1200m | PJ | GW
DH_AHP_GEO1200_N1 | Geothermal and absorption HP 1200m | PWRGAS,PWRBGS,PWRBIO |  | HETC | MEUR2015 | 2022 | 22.66 | 1.6514 |  |  |  | 25 | 0.98 | 1386 | 11.1 | 0.065956 | 0.031536 | 15 | 5 | HPL | DH_ASHP_ELC_N1 | Air Source Heat Pump | PJ | GW
|  |  | PWRAHT | [7 empty] | 0.39444 | [8 empty] | HPL | DH_BIO_BLR_N1 | Biomass Boiler for District Heating | PJ | GW
DH_ASHP_ELC_N1 | Air Source Heat Pump | PWRELC |  | HETC | MEUR2015 | 2022 | 10 | 3.5 |  |  |  | 25 | 0.99 | 860 | 2 | 0.05359 | 0.031536 |  | 1 | HPL | DH_PWR_SURPLUS_HEAT | Power Generation Surplus Heat | PJ | GW
|  |  | PWRAHT | [7 empty] | 0.71429 | [8 empty] | HPL | DH_IND_SURPLUS_HEAT | Industrial Surplus Heat | PJ | GW
DH_BIO_BLR_N1 | Biomass Boiler for District Heating | PWRBIO |  | HETC | MEUR2015 | 2022 | 51.64 | 0.98 |  |  |  | 25 | 0.97 | 490 | 48.2 | 0.0983 | 0.031536 |  | 2 | STS | DH_STG_HETD_N1 | Thermal decentrialised water storage tank | PJ | GW
DH_IND_SURPLUS_HEAT | Industrial Surplus Heat |  |  | HETC | MEUR2015 | 2022 | 20 | 1 |  |  |  | 25 | 0.95 | 670 | 2 | 0.05359 | 0.031536 | 10.2577 |  | STG | DH_STG_HETC_N1 | Thermal Centrialised water storage tank | PJ | GW
DH_PWR_SURPLUS_HEAT | Power Generation Surplus Heat |  |  | HETC | MEUR2015 | 2022 | 50 | 1 |  |  |  | 25 | 0.95 | 670 | 2 | 0.05359 | 0.031536 | 44.6277
DH_STG_HETD_N1 | Thermal decentrialised water storage tank | HETD |  | HETD |  | 2022 |  |  | 0.98 | 0.68 |  | 40 | 0.95 | 823.6 | 2
DH_STG_HETC_N1 | Thermal Centrialised water storage tank | HETC |  | HETC |  | 2022 |  |  | 0.7 | 0.53 |  | 20 | 0.95 | 161 | 2
Note on X6: Sets declarations are NOT inherited. Possible Process Sets ELE (Thermal Electric Power Plant) CHP (Combined Heat and Power) STGTSS (Pump Storage) PRE (Genric Process/Technology) DMD (Demand Device) IMP (Import) EXP (Export) MIN (Mining Process) RNW (Renewable Technology) HPL (Heating Plant)
Note on J9: Mc Guire, Jason: From notes in tab - as the table includes a condensing economizer
Note on P10: Mc Guire, Jason: Add 15% as cost doesn’t include initial site assesment and some other misc costs
Note on T10: Mc Guire, Jason: Assumption
Note on J17: Mc Guire, Jason: Reduced from value in tab, similar to Gas Boiler

## Surplus Heat
Surplus Heat Capacity
~FI_T: CAP_BND
TechName | IE | IE-CW | IE-D | IE-KE | IE-KK | IE-LS | IE-LD | IE-LH | IE-MH | IE-OY | IE-WH | IE-WX | IE-WW | IE-CE | IE-CO | IE-KY | IE-LK | IE-TA | IE-WD | IE-G | IE-LM | IE-MO | IE-RN | IE-SO | IE-CN | IE-DL | IE-MN | National
DH_PWR_SURPLUS_HEAT | 44627.6928 | 0 | 29742.1037 | 0 | 0 | 0 | 0 | 0 | 2871.504 | 0 | 0 | 0 | 0 | 0 | 7697.0696 | 0 | 0 | 0 | 4317.0156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44627.6928
DH_IND_SURPLUS_HEAT | 10257.7404 | 0 | 1944 | 0 | 0 | 0 | 0 | 3077 | 0 | 0 | 0 | 0 | 0 | 0 | 2127.7404 | 0 | 1225 | 0 | 0 | 108 | 0 | 0 | 0 | 0 | 1776 | 0 | 0 | 10257.7404
SEAI Heat Report & Irish Heat Atlas Data
# | Installation Name | Type | Waste Heat Recovery Potential [MW] | Waste Heat Recovery Potential [TJ/year] | Region (Included) | Region (Excluded)
PS-1 | Dublin Bay Power Plant (Synergen) | Power Station | 266.5752 | 5468.1086 | IE-D
PS-2 | ESB Great Island Generating Station | Power Station | 210.4584 | 4317.0156 | IE-WD
| ESB Moneypoint Generating Station | Power Station | 1162.358 | 23842.7979 | Not Included | IE-CE
PS-3 | Huntstown Power Station | Power Station | 188.4508 | 3865.5854 | IE-D
| Huntstown Power Station (Phase II) CCGT HPC2 | Power Station | 206.697 | 4239.859 | IE-D
| Tynagh 400MW CCPP | Power Station | 217.1811 | 4454.9141 | Not Included | IE-G
PS-4 | ESB Poolbeg Generating Station CCGT | Power Station | 342.3467 | 7022.3655 | IE-D
PS-5 | ESB Aghada CCGT (AD2) | Power Station | 186.5702 | 3827.0092 | IE-CO
| ESB Aghada Thermal (CT1,2 & 4) | Power Station | 429.08 | 8801.4778 | Not Included | IE-CO
PS-6 | Whitegate Independent Power Plant | Power Station | 188.6689 | 3870.0604 | IE-CO
| ESB North Wall 5 Generating Station (Refurb) | Power Station | 196.9911 | 4040.7683 | Not Included | IE-D
Ind-2 | Huntstown Power Company Limited | Power Station |  | 822 | IE-D
Ind-8 | Synergen Power Limited | Power Station |  | 7227 | IE-D
EfW-1 | Indaver Ireland Limited (Duleek) | Energy from Waste |  | 2430 | IE-MH
EfW-2 | Dublin Waste to Energy | Energy from Waste | 34.7915 | 1097.1853 | IE-D
EfW-3 | Waste to Energy | Energy from Waste | 14 | 441.504 | IE-MH |  | # | MWth
DC-1 | All Dublin datacentres | Data centre | 63 | 1944 | IE-D |  | 18 | 3.5
DC-2 | All Cork datacentres | Data centre | 3.5 | 108 | IE-C |  | 1
DC-3 | All Galway datacentres | Data centre | 3.5 | 108 | IE-G |  | 1
Ind-3 | Premier Periclase Limited | Industrial - Non-metallic minerals ( plasterboard) |  | 612 | IE-LH
Ind-4 | Quinn Cement Limited | Industrial - Cement |  | 1776 | IE-CN
Ind-5 | Irish Cement Limited (Limerick) | Industrial - Cement |  | 1225 | IE-LK
Ind-6 | Irish Cement Limited (Platin) | Industrial - Cement |  | 2465 | IE-LH
Ind-9 | Phillips 66 Whitegate Refinery Limited | Refinery | 67.4702 | 2127.7404 | IE-CO
Note on J28: Mc Guire, Jason: Assumption from SEAI Heat Report

## DH_Grid_Extension
Variable O&M Cost | Share of Residential to Services heating energy
3% | 60%
|  | ~FI_T: SHARE-O~2019 | [29 empty] | ~FI_T: SHARE-O~0
| TechName | Comm-OUT | IE | IE-CW | IE-D | IE-KE | IE-KK | IE-LS | IE-LD | IE-LH | IE-MH | IE-OY | IE-WH | IE-WX | IE-WW | IE-CE | IE-CO | IE-KY | IE-LK | IE-TA | IE-WD | IE-G | IE-LM | IE-MO | IE-RN | IE-SO | IE-CN | IE-DL | IE-MN | National | TechName | Comm-OUT | IE | IE-CW | IE-D | IE-KE | IE-KK | IE-LS | IE-LD | IE-LH | IE-MH | IE-OY | IE-WH | IE-WX | IE-WW | IE-CE | IE-CO | IE-KY | IE-LK | IE-TA | IE-WD | IE-G | IE-LM | IE-MO | IE-RN | IE-SO | IE-CN | IE-DL | IE-MN | National
| FT-RSDHET_C | RSDHET_Att | 0.61362 | 0.69457 | 0.57412 | 0.73369 | 0.76045 | 0.59503 | 0.88073 | 0.81102 | 0.62095 | 0.77866 | 0.47006 | 0.73554 | 0.71286 | 0.74454 | 0.68338 | 0.64556 | 0.59629 | 0.77072 | 0.64813 | 0.56523 | 0.74046 | 0.71828 | 0.81013 | 0.67241 | 0.77778 | 0.54545 | 0.85989 | 0.61362 | FT-RSDHET_C | RSDHET_Att | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  | RSDHET_Det | 0.051434 | 0.074419 | 0.037936 | 0.10084 | 0.080226 | 0.15155 | 0.050459 | 0.06364 | 0.12007 | 0.039526 | 0.03949 | 0.099174 | 0.099038 | 0.077873 | 0.062419 | 0.08417 | 0.040532 | 0.071823 | 0.065067 | 0.074333 | 0.083969 | 0.064516 | 0.025316 | 0.03592 | 0.063492 | 0.070381 | 0.065934 | 0.051434 |  | RSDHET_Det | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  | RSDHET_Apt | 0.33495 | 0.23101 | 0.38794 | 0.16547 | 0.15932 | 0.25342 | 0.068807 | 0.12534 | 0.25898 | 0.18182 | 0.49045 | 0.16529 | 0.1881 | 0.17759 | 0.2542 | 0.27027 | 0.36318 | 0.15746 | 0.2868 | 0.36044 | 0.17557 | 0.2172 | 0.16456 | 0.29167 | 0.15873 | 0.38416 | 0.074176 | 0.33495 |  | RSDHET_Apt | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
| FT-RSDHET_1 | RSDHET_Att | 0.61362 | 0.69457 | 0.57412 | 0.73369 | 0.76045 | 0.59503 | 0.88073 | 0.81102 | 0.62095 | 0.77866 | 0.47006 | 0.73554 | 0.71286 | 0.74454 | 0.68338 | 0.64556 | 0.59629 | 0.77072 | 0.64813 | 0.56523 | 0.74046 | 0.71828 | 0.81013 | 0.67241 | 0.77778 | 0.54545 | 0.85989 | 0.61362 | FT-RSDHET_1 | RSDHET_Att | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  | RSDHET_Det | 0.051434 | 0.074419 | 0.037936 | 0.10084 | 0.080226 | 0.15155 | 0.050459 | 0.06364 | 0.12007 | 0.039526 | 0.03949 | 0.099174 | 0.099038 | 0.077873 | 0.062419 | 0.08417 | 0.040532 | 0.071823 | 0.065067 | 0.074333 | 0.083969 | 0.064516 | 0.025316 | 0.03592 | 0.063492 | 0.070381 | 0.065934 | 0.051434 |  | RSDHET_Det | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  | RSDHET_Apt | 0.33495 | 0.23101 | 0.38794 | 0.16547 | 0.15932 | 0.25342 | 0.068807 | 0.12534 | 0.25898 | 0.18182 | 0.49045 | 0.16529 | 0.1881 | 0.17759 | 0.2542 | 0.27027 | 0.36318 | 0.15746 | 0.2868 | 0.36044 | 0.17557 | 0.2172 | 0.16456 | 0.29167 | 0.15873 | 0.38416 | 0.074176 | 0.33495 |  | RSDHET_Apt | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
| FT-RSDHET_2 | RSDHET_Att | 0.61362 | 0.72127 | 0.68827 | 0.65055 | 0.69774 | 0.69097 | 0.64042 | 0.70898 | 0.6524 | 0.71935 | 0.64579 | 0.66745 | 0.64217 | 0.59632 | 0.68253 | 0.63496 | 0.73918 | 0.7761 | 0.69229 | 0.58284 | 0.60474 | 0.64798 | 0.66277 | 0.61085 | 0.68844 | 0.65046 | 0.7541 | 0.61362 | FT-RSDHET_2 | RSDHET_Att | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  | RSDHET_Det | 0.051434 | 0.1405 | 0.12741 | 0.21274 | 0.17232 | 0.2565 | 0.17156 | 0.1613 | 0.22637 | 0.17887 | 0.15068 | 0.1921 | 0.26584 | 0.22462 | 0.19334 | 0.18868 | 0.14688 | 0.14393 | 0.19354 | 0.21782 | 0.3004 | 0.1843 | 0.11891 | 0.15242 | 0.12764 | 0.20583 | 0.070258 | 0.051434 |  | RSDHET_Det | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  | RSDHET_Apt | 0.33495 | 0.13823 | 0.18432 | 0.13671 | 0.12994 | 0.052524 | 0.18801 | 0.12972 | 0.12124 | 0.10177 | 0.20352 | 0.14045 | 0.091992 | 0.17906 | 0.12413 | 0.17636 | 0.11394 | 0.079964 | 0.11417 | 0.19934 | 0.094862 | 0.16771 | 0.21832 | 0.23672 | 0.18392 | 0.14371 | 0.17564 | 0.33495 |  | RSDHET_Apt | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
| FT-RSDHET_3 | RSDHET_Att | 0.61362 | 0.54587 | 0.55502 | 0.55717 | 0.61782 | 0.63039 | 0.53876 | 0.57624 | 0.58766 | 0.63789 | 0.60311 | 0.44195 | 0.49887 | 0.58612 | 0.5329 | 0.47978 | 0.64353 | 0.66476 | 0.55327 | 0.44062 | 0.47601 | 0.54828 | 0.58586 | 0.55322 | 0.58722 | 0.48339 | 0.66513 | 0.61362 | FT-RSDHET_3 | RSDHET_Att | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  | RSDHET_Det | 0.051434 | 0.36984 | 0.19108 | 0.30185 | 0.31262 | 0.30314 | 0.36357 | 0.34464 | 0.32331 | 0.26619 | 0.24332 | 0.48417 | 0.38531 | 0.31287 | 0.36641 | 0.44163 | 0.25227 | 0.28832 | 0.36168 | 0.40212 | 0.37364 | 0.3695 | 0.35308 | 0.32593 | 0.3215 | 0.41376 | 0.22955 | 0.051434 |  | RSDHET_Det | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  | RSDHET_Apt | 0.33495 | 0.084289 | 0.2539 | 0.14098 | 0.069558 | 0.066472 | 0.097674 | 0.079126 | 0.089031 | 0.095923 | 0.15357 | 0.073879 | 0.11582 | 0.10101 | 0.1007 | 0.078589 | 0.10419 | 0.046921 | 0.08505 | 0.15726 | 0.15035 | 0.082218 | 0.061065 | 0.12086 | 0.091278 | 0.10285 | 0.10532 | 0.33495 |  | RSDHET_Apt | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Building projection data from Scen_B_SYS_Demands
|  | Year | IE | IE-CW | IE-D | IE-KE | IE-KK | IE-LS | IE-LD | IE-LH | IE-MH | IE-OY | IE-WH | IE-WX | IE-WW | IE-CE | IE-CO | IE-KY | IE-LK | IE-TA | IE-WD | IE-G | IE-LM | IE-MO | IE-RN | IE-SO | IE-CN | IE-DL | IE-MN
| RSD_Att | 2018 | 776.1044 | 9.0174 | 299.7399 | 38.1442 | 12.5084 | 11.5106 | 4.7463 | 24.2895 | 27.1034 | 10.2393 | 12.2642 | 18.3855 | 23.1673 | 15.119 | 91.4469 | 15.6867 | 31.6959 | 21.9542 | 21.7692 | 27.5895 | 2.7378 | 12.5197 | 5.3723 | 8.8896 | 7.7069 | 15.8816 | 6.6191
| RSD_Det | 2018 | 729.4994 | 10.817 | 56.1592 | 30.3045 | 20.8914 | 16.2956 | 9.7189 | 18.8667 | 34.3241 | 15.9662 | 16.8229 | 33.8783 | 22.5296 | 26.2215 | 88.7066 | 36.3766 | 32.7508 | 34.965 | 19.1427 | 55.3726 | 9.1012 | 34.6993 | 18.081 | 14.4942 | 18.1199 | 40.7385 | 14.1551
| RSD_Apt | 2018 | 211.7395 | 1.2721 | 123.3147 | 7.3638 | 1.7514 | 1.435 | 0.69143 | 3.0388 | 5.4114 | 1.1753 | 2.889 | 2.669 | 4.5132 | 2.4912 | 18.1646 | 2.9061 | 7.4611 | 2.3822 | 3.1992 | 9.8816 | 0.54302 | 2.1413 | 0.67645 | 1.6761 | 1.2711 | 2.393 | 1.0275
| RSD_Att | 2070 | 1122.281 | 14.8824 | 402.0335 | 67.8083 | 16.6883 | 17.248 | 6.5299 | 41.3043 | 45.5378 | 15.2609 | 16.3371 | 27.286 | 39.7583 | 22.9387 | 140.7041 | 22.1469 | 48.1298 | 28.1636 | 35.4143 | 36.9503 | 3.5192 | 16.251 | 7.1457 | 11.5789 | 9.9043 | 20.0629 | 8.6966
| RSD_Det | 2070 | 866.167 | 12.0327 | 48.7098 | 28.2084 | 27.5394 | 19.8781 | 12.76 | 19.2789 | 35.5158 | 19.6301 | 22.3412 | 40.4473 | 22.1932 | 31.9075 | 99.012 | 46.2555 | 36.3024 | 47.8133 | 20.7454 | 71.268 | 12.5127 | 47.5003 | 24.3942 | 18.4684 | 25.2831 | 56.9111 | 19.2584
| RSD_Apt | 2070 | 922.351 | 4.0187 | 620.502 | 25.3056 | 5.9205 | 4.6405 | 2.2614 | 10.1471 | 18.154 | 3.7879 | 9.6795 | 9.0071 | 15.4664 | 7.9381 | 63.4548 | 9.6239 | 26.7469 | 7.9987 | 10.6823 | 34.3895 | 1.804 | 7.0768 | 2.2176 | 6.1051 | 4.1272 | 7.9183 | 3.3772
`
~FI_T: SHARE-O~2070
| TechName | Comm-OUT | IE | IE-CW | IE-D | IE-KE | IE-KK | IE-LS | IE-LD | IE-LH | IE-MH | IE-OY | IE-WH | IE-WX | IE-WW | IE-CE | IE-CO | IE-KY | IE-LK | IE-TA | IE-WD | IE-G | IE-LM | IE-MO | IE-RN | IE-SO | IE-CN | IE-DL | IE-MN | National
| FT-RSDHET_C | RSDHET_Att | 0.52351 | 0.78216 | 0.34448 | 0.81502 | 0.71116 | 0.62423 | 0.85217 | 0.90074 | 0.7029 | 0.82154 | 0.41405 | 0.78141 | 0.79343 | 0.78863 | 0.68782 | 0.64209 | 0.58563 | 0.6982 | 0.69582 | 0.49284 | 0.66075 | 0.64976 | 0.77023 | 0.60711 | 0.68894 | 0.479 | 0.78613 | 0.52351
|  | RSDHET_Det | 0.036031 | 0.056483 | 0.014719 | 0.058654 | 0.074129 | 0.12943 | 0.046591 | 0.042472 | 0.083704 | 0.034401 | 0.034678 | 0.084756 | 0.063273 | 0.066154 | 0.045575 | 0.075401 | 0.029058 | 0.069357 | 0.046535 | 0.062286 | 0.080144 | 0.061548 | 0.024415 | 0.031725 | 0.061062 | 0.068348 | 0.062419 | 0.036031
|  | RSDHET_Apt | 0.44046 | 0.16136 | 0.6408 | 0.12633 | 0.21471 | 0.24634 | 0.10124 | 0.056789 | 0.2134 | 0.14406 | 0.55127 | 0.13384 | 0.1433 | 0.14522 | 0.26661 | 0.28251 | 0.38531 | 0.23244 | 0.25765 | 0.44487 | 0.25911 | 0.28869 | 0.20536 | 0.36117 | 0.25 | 0.45265 | 0.15145 | 0.44046
| FT-RSDHET_1 | RSDHET_Att | 0.52351 | 0.78216 | 0.34448 | 0.81502 | 0.71116 | 0.62423 | 0.85217 | 0.90074 | 0.7029 | 0.82154 | 0.41405 | 0.78141 | 0.79343 | 0.78863 | 0.68782 | 0.64209 | 0.58563 | 0.6982 | 0.69582 | 0.49284 | 0.66075 | 0.64976 | 0.77023 | 0.60711 | 0.68894 | 0.479 | 0.78613 | 0.52351
|  | RSDHET_Det | 0.036031 | 0.056483 | 0.014719 | 0.058654 | 0.074129 | 0.12943 | 0.046591 | 0.042472 | 0.083704 | 0.034401 | 0.034678 | 0.084756 | 0.063273 | 0.066154 | 0.045575 | 0.075401 | 0.029058 | 0.069357 | 0.046535 | 0.062286 | 0.080144 | 0.061548 | 0.024415 | 0.031725 | 0.061062 | 0.068348 | 0.062419 | 0.036031
|  | RSDHET_Apt | 0.44046 | 0.16136 | 0.6408 | 0.12633 | 0.21471 | 0.24634 | 0.10124 | 0.056789 | 0.2134 | 0.14406 | 0.55127 | 0.13384 | 0.1433 | 0.14522 | 0.26661 | 0.28251 | 0.38531 | 0.23244 | 0.25765 | 0.44487 | 0.25911 | 0.28869 | 0.20536 | 0.36117 | 0.25 | 0.45265 | 0.15145 | 0.44046
| FT-RSDHET_2 | RSDHET_Att | 0.52351 | 0.81222 | 0.41297 | 0.72266 | 0.65251 | 0.72489 | 0.61965 | 0.78741 | 0.73849 | 0.75897 | 0.56884 | 0.70908 | 0.71474 | 0.63163 | 0.68696 | 0.63155 | 0.72596 | 0.70308 | 0.74322 | 0.5082 | 0.53964 | 0.58617 | 0.63013 | 0.55153 | 0.60981 | 0.57122 | 0.68941 | 0.52351
|  | RSDHET_Det | 0.036031 | 0.10664 | 0.049435 | 0.12374 | 0.15922 | 0.21906 | 0.15841 | 0.10765 | 0.15781 | 0.15568 | 0.13232 | 0.16417 | 0.16984 | 0.19082 | 0.14117 | 0.16902 | 0.1053 | 0.13899 | 0.13842 | 0.18252 | 0.28671 | 0.17583 | 0.11467 | 0.13463 | 0.12275 | 0.19989 | 0.066512 | 0.036031
|  | RSDHET_Apt | 0.44046 | 0.081137 | 0.53759 | 0.1536 | 0.18827 | 0.056056 | 0.22193 | 0.10494 | 0.1037 | 0.085346 | 0.29884 | 0.12675 | 0.11542 | 0.17755 | 0.17187 | 0.19942 | 0.16874 | 0.15793 | 0.11836 | 0.30929 | 0.17365 | 0.23801 | 0.2552 | 0.31385 | 0.26744 | 0.22889 | 0.24408 | 0.44046
| FT-RSDHET_3 | RSDHET_Att | 0.52351 | 0.6147 | 0.33301 | 0.61893 | 0.57777 | 0.66132 | 0.52129 | 0.63998 | 0.66521 | 0.67302 | 0.53124 | 0.46951 | 0.55525 | 0.62083 | 0.53636 | 0.4772 | 0.63203 | 0.60221 | 0.59398 | 0.38419 | 0.42476 | 0.49597 | 0.557 | 0.49949 | 0.52015 | 0.4245 | 0.60808 | 0.52351
|  | RSDHET_Det | 0.036031 | 0.28071 | 0.074142 | 0.17558 | 0.28886 | 0.25889 | 0.3357 | 0.23 | 0.22538 | 0.23167 | 0.21367 | 0.41378 | 0.24616 | 0.26579 | 0.26753 | 0.39562 | 0.18086 | 0.27842 | 0.25867 | 0.33695 | 0.35662 | 0.35251 | 0.3405 | 0.28787 | 0.3092 | 0.40181 | 0.21731 | 0.036031
|  | RSDHET_Apt | 0.44046 | 0.10459 | 0.59284 | 0.20549 | 0.13337 | 0.079785 | 0.14302 | 0.13001 | 0.1094 | 0.095304 | 0.25509 | 0.1167 | 0.19858 | 0.11338 | 0.19611 | 0.12718 | 0.18711 | 0.11937 | 0.14735 | 0.27886 | 0.21862 | 0.15152 | 0.1025 | 0.21264 | 0.17065 | 0.17369 | 0.17461 | 0.44046
~FI_T: ACT_BND~UP
| TechName | IE | IE-CW | IE-D | IE-KE | IE-KK | IE-LS | IE-LD | IE-LH | IE-MH | IE-OY | IE-WH | IE-WX | IE-WW | IE-CE | IE-CO | IE-KY | IE-LK | IE-TA | IE-WD | IE-G | IE-LM | IE-MO | IE-RN | IE-SO | IE-CN | IE-DL | IE-MN | National
0 | FT-RSDHET_C | 19.1327 | 0 | 12.5941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7547 | 0 | 1.4024 | 0 | 0.83192 | 1.5495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.1327
1 | FT-RSDHET_1 | 14.4317 | 0 | 1.6856 | 1.6016 | 0.78574 | 0.44573 | 0.24962 | 0.96936 | 1.1012 | 0.44382 | 0.30328 | 0.77136 | 0.70642 | 0.57931 | 1.006 | 0 | 0.03195 | 0.69736 | 0.1903 | 0.1924 | 0.12723 | 0.35235 | 0.58316 | 0.46269 | 0.30501 | 0.69593 | 0.14428 | 14.4317
2 | FT-RSDHET_2 | 6.1748 | 0.33652 | 0.46933 | 0.45263 | 0.086256 | 0.024972 | 0.04827 | 0.038292 | 0.85798 | 0.12487 | 0 | 0.15551 | 0.4015 | 0.070692 | 0.66863 | 0.54047 | 0.31374 | 0.1589 | 0.18608 | 0.38372 | 0.023532 | 0.29724 | 0.06036 | 0.072894 | 0.12728 | 0.074346 | 0.20084 | 6.1748
3 | FT-RSDHET_3 | 1.5218 | 0.046458 | 0.007584 | 0.060912 | 0.031302 | 0.043116 | 0.014556 | 0.058818 | 0.020568 | 0.045786 | 0.020532 | 0.074742 | 0.08574 | 0.054012 | 0.16748 | 0.10767 | 0.13069 | 0.026472 | 0.046062 | 0.073134 | 0.033672 | 0.062226 | 0.027672 | 0.058968 | 0.0288 | 0.17214 | 0.022674 | 1.5218
~FI_T: ACT_BND~UP
| TechName | IE | IE-CW | IE-D | IE-KE | IE-KK | IE-LS | IE-LD | IE-LH | IE-MH | IE-OY | IE-WH | IE-WX | IE-WW | IE-CE | IE-CO | IE-KY | IE-LK | IE-TA | IE-WD | IE-G | IE-LM | IE-MO | IE-RN | IE-SO | IE-CN | IE-DL | IE-MN | National
0 | FT-SRVHET_C | 12.7552 | 0 | 8.3961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8365 | 0 | 0.93495 | 0 | 0.55462 | 1.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.7552
1 | FT-SRVHET_1 | 9.6211 | 0 | 1.1238 | 1.0677 | 0.52382 | 0.29715 | 0.16641 | 0.64624 | 0.73412 | 0.29588 | 0.20219 | 0.51424 | 0.47094 | 0.38621 | 0.67069 | 0 | 0.0213 | 0.4649 | 0.12686 | 0.12826 | 0.08482 | 0.2349 | 0.38877 | 0.30846 | 0.20334 | 0.46396 | 0.096184 | 9.6211
2 | FT-SRVHET_2 | 4.1166 | 0.22434 | 0.31288 | 0.30175 | 0.057504 | 0.016648 | 0.03218 | 0.025528 | 0.57199 | 0.083244 | 0 | 0.10367 | 0.26767 | 0.047128 | 0.44575 | 0.36032 | 0.20916 | 0.10593 | 0.12406 | 0.25581 | 0.015688 | 0.19816 | 0.04024 | 0.048596 | 0.084856 | 0.049564 | 0.13389 | 4.1166
3 | FT-SRVHET_3 | 1.0145 | 0.030972 | 0.005056 | 0.040608 | 0.020868 | 0.028744 | 0.009704 | 0.039212 | 0.013712 | 0.030524 | 0.013688 | 0.049828 | 0.05716 | 0.036008 | 0.11165 | 0.07178 | 0.087128 | 0.017648 | 0.030708 | 0.048756 | 0.022448 | 0.041484 | 0.018448 | 0.039312 | 0.0192 | 0.11476 | 0.015116 | 1.0145
~FI_T: INVCOST
| TechName | IE | IE-CW | IE-D | IE-KE | IE-KK | IE-LS | IE-LD | IE-LH | IE-MH | IE-OY | IE-WH | IE-WX | IE-WW | IE-CE | IE-CO | IE-KY | IE-LK | IE-TA | IE-WD | IE-G | IE-LM | IE-MO | IE-RN | IE-SO | IE-CN | IE-DL | IE-MN | National
0 | FT-RSDHET_C | 3.0407 | 0 | 3.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.94 | 0 | 3.23 | 0 | 2.45 | 2.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0407
1 | FT-RSDHET_1 | 3.231 | 0 | 4.3618 | 2.4504 | 2.5446 | 2.5751 | 3.3726 | 2.7561 | 2.6909 | 2.8991 | 2.8067 | 3.27 | 3.3485 | 4.3774 | 3.2276 | 0 | 1.2501 | 4.294 | 3.0074 | 3.6104 | 3.6 | 2.9591 | 3.7757 | 2.9177 | 2.4883 | 3.2851 | 3.6059 | 3.231
2 | FT-RSDHET_2 | 5.675 | 4.0793 | 6.6594 | 5.9572 | 8.9177 | 5.2125 | 7.2923 | 5.6396 | 5.3161 | 5.7257 | 0 | 7.0202 | 5.8743 | 7.9187 | 5.7904 | 3.7254 | 5.6968 | 6.0029 | 7.3234 | 5.6935 | 6.9997 | 5.5836 | 6.1849 | 5.9209 | 6.2626 | 6.5033 | 5.0329 | 5.675
3 | FT-RSDHET_3 | 12.178 | 10.6372 | 20.5 | 13.7959 | 12.431 | 12.0743 | 15.3381 | 12.9421 | 14.145 | 11.6696 | 11.7829 | 11.7498 | 14.2956 | 13.22 | 9.9403 | 11.5325 | 12.0091 | 12.4075 | 11.674 | 12.1723 | 10.7005 | 13.9949 | 11.4581 | 12.1638 | 12.73 | 12.3289 | 12.1805 | 12.178
~FI_T: INVCOST
| TechName | IE | IE-CW | IE-D | IE-KE | IE-KK | IE-LS | IE-LD | IE-LH | IE-MH | IE-OY | IE-WH | IE-WX | IE-WW | IE-CE | IE-CO | IE-KY | IE-LK | IE-TA | IE-WD | IE-G | IE-LM | IE-MO | IE-RN | IE-SO | IE-CN | IE-DL | IE-MN | National
0 | FT-SRVHET_C | 3.0407 | 0 | 3.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.94 | 0 | 3.23 | 0 | 2.45 | 2.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0407
1 | FT-SRVHET_1 | 3.231 | 0 | 4.3618 | 2.4504 | 2.5446 | 2.5751 | 3.3726 | 2.7561 | 2.6909 | 2.8991 | 2.8067 | 3.27 | 3.3485 | 4.3774 | 3.2276 | 0 | 1.2501 | 4.294 | 3.0074 | 3.6104 | 3.6 | 2.9591 | 3.7757 | 2.9177 | 2.4883 | 3.2851 | 3.6059 | 3.231
2 | FT-SRVHET_2 | 5.675 | 4.0793 | 6.6594 | 5.9572 | 8.9177 | 5.2125 | 7.2923 | 5.6396 | 5.3161 | 5.7257 | 0 | 7.0202 | 5.8743 | 7.9187 | 5.7904 | 3.7254 | 5.6968 | 6.0029 | 7.3234 | 5.6935 | 6.9997 | 5.5836 | 6.1849 | 5.9209 | 6.2626 | 6.5033 | 5.0329 | 5.675
3 | FT-SRVHET_3 | 12.178 | 10.6372 | 20.5 | 13.7959 | 12.431 | 12.0743 | 15.3381 | 12.9421 | 14.145 | 11.6696 | 11.7829 | 11.7498 | 14.2956 | 13.22 | 9.9403 | 11.5325 | 12.0091 | 12.4075 | 11.674 | 12.1723 | 10.7005 | 13.9949 | 11.4581 | 12.1638 | 12.73 | 12.3289 | 12.1805 | 12.178
~FI_T: VAROM
| TechName | IE | IE-CW | IE-D | IE-KE | IE-KK | IE-LS | IE-LD | IE-LH | IE-MH | IE-OY | IE-WH | IE-WX | IE-WW | IE-CE | IE-CO | IE-KY | IE-LK | IE-TA | IE-WD | IE-G | IE-LM | IE-MO | IE-RN | IE-SO | IE-CN | IE-DL | IE-MN | National
0 | FT-RSDHET_C | Building projection data from Scen_B_SYS_Demands Year: 0.091222; Building projection data from Scen_B_SYS_Demands IE-CW: 0.0939; Building projection data from Scen_B_SYS_Demands IE-CE: 0.0882; Building projection data from Scen_B_SYS_Demands IE-KY: 0.0969; Building projection data from Scen_B_SYS_Demands IE-TA: 0.0735; Building projection data from Scen_B_SYS_Demands IE-WD: 0.0792; Building projection data from Scen_B_SYS_Demands IE-MN: 0.091222
1 | FT-RSDHET_1 | 0.09693 |  | 0.13085 | 0.073511 | 0.076337 | 0.077254 | 0.10118 | 0.082682 | 0.080728 | 0.086973 | 0.084201 | 0.098101 | 0.10046 | 0.13132 | 0.096828 |  | 0.037503 | 0.12882 | 0.090223 | 0.10831 | 0.108 | 0.088772 | 0.11327 | 0.087531 | 0.07465 | 0.098554 | 0.10818 | 0.09693
2 | FT-RSDHET_2 | 0.17025 | 0.12238 | 0.19978 | 0.17872 | 0.26753 | 0.15637 | 0.21877 | 0.16919 | 0.15948 | 0.17177 |  | 0.21061 | 0.17623 | 0.23756 | 0.17371 | 0.11176 | 0.1709 | 0.18009 | 0.2197 | 0.17081 | 0.20999 | 0.16751 | 0.18555 | 0.17763 | 0.18788 | 0.1951 | 0.15099 | 0.17025
3 | FT-RSDHET_3 | 0.36534 | 0.31912 | 0.615 | 0.41388 | 0.37293 | 0.36223 | 0.46014 | 0.38826 | 0.42435 | 0.35009 | 0.35349 | 0.3525 | 0.42887 | 0.3966 | 0.29821 | 0.34597 | 0.36027 | 0.37222 | 0.35022 | 0.36517 | 0.32102 | 0.41985 | 0.34374 | 0.36491 | 0.3819 | 0.36987 | 0.36542 | 0.36534
~FI_T: VAROM
| TechName | IE | IE-CW | IE-D | IE-KE | IE-KK | IE-LS | IE-LD | IE-LH | IE-MH | IE-OY | IE-WH | IE-WX | IE-WW | IE-CE | IE-CO | IE-KY | IE-LK | IE-TA | IE-WD | IE-G | IE-LM | IE-MO | IE-RN | IE-SO | IE-CN | IE-DL | IE-MN | National
0 | FT-SRVHET_C | Building projection data from Scen_B_SYS_Demands Year: 0.091222; Building projection data from Scen_B_SYS_Demands IE-CW: 0.0939; Building projection data from Scen_B_SYS_Demands IE-CE: 0.0882; Building projection data from Scen_B_SYS_Demands IE-KY: 0.0969; Building projection data from Scen_B_SYS_Demands IE-TA: 0.0735; Building projection data from Scen_B_SYS_Demands IE-WD: 0.0792; Building projection data from Scen_B_SYS_Demands IE-MN: 0.091222
1 | FT-SRVHET_1 | 0.09693 |  | 0.13085 | 0.073511 | 0.076337 | 0.077254 | 0.10118 | 0.082682 | 0.080728 | 0.086973 | 0.084201 | 0.098101 | 0.10046 | 0.13132 | 0.096828 |  | 0.037503 | 0.12882 | 0.090223 | 0.10831 | 0.108 | 0.088772 | 0.11327 | 0.087531 | 0.07465 | 0.098554 | 0.10818 | 0.09693
2 | FT-SRVHET_2 | 0.17025 | 0.12238 | 0.19978 | 0.17872 | 0.26753 | 0.15637 | 0.21877 | 0.16919 | 0.15948 | 0.17177 |  | 0.21061 | 0.17623 | 0.23756 | 0.17371 | 0.11176 | 0.1709 | 0.18009 | 0.2197 | 0.17081 | 0.20999 | 0.16751 | 0.18555 | 0.17763 | 0.18788 | 0.1951 | 0.15099 | 0.17025
3 | FT-SRVHET_3 | 0.36534 | 0.31912 | 0.615 | 0.41388 | 0.37293 | 0.36223 | 0.46014 | 0.38826 | 0.42435 | 0.35009 | 0.35349 | 0.3525 | 0.42887 | 0.3966 | 0.29821 | 0.34597 | 0.36027 | 0.37222 | 0.35022 | 0.36517 | 0.32102 | 0.41985 | 0.34374 | 0.36491 | 0.3819 | 0.36987 | 0.36542 | 0.36534

## Data
Source: https://www.arcgis.com/home/item.html?id=0a076ea4f0874d43a592eed114a0291b&sublayer=0#data | [5 empty] | More info: https://heatroadmap.eu/wp-content/uploads/2018/11/D2.3_Revised-version_180928.pdf
Visulation: https://euf.maps.arcgis.com/apps/webappviewer/index.html?id=101b7da79a7d4e09a92402bd4ce8384c | [5 empty] | More info: https://heatroadmap.eu/wp-content/uploads/2018/11/D2.4-website-version.pdf
More Info: https://heatroadmap.eu/wp-content/uploads/2018/11/D6.5-Updated-Peta-atlas-for-each-MS-with-the-final-level-of-district-heating-recommended-in-WP6.pdf
| Unit & Symbol: | TJ (Heat demand (2015) by prospective supply areas and heat demand density class) [QL] |  |  |  |  | TJ [Q] | km2 | TJ/km2 | Average DH distribution capital costs (€/GJ annual heat demand - Y axis is Cd & X axis is % of total heat market) for cumulative DH potentials. | [9 empty] | €/GJ Annualised marginal distribution capital costs costs for district heating distribution pipe systems. Calculated based on heat demand densities [Cd]
PSD_ID | Placename_assigned | SumHD_0_20 | SumHD_20_50 | SumHD_50_120 | SumHD_120_300 | SumHD_morethan_300 | SumHD_TJ | Area_km2 | Heat density | Avg_DCCH_10percDH | Avg_DCCH_20percDH | Avg_DCCH_30percDH | Avg_DCCH_40percDH | Avg_DCCH_50percDH | Avg_DCCH_60percDH | Avg_DCCH_70percDH | Avg_DCCH_80percDH | Avg_DCCH_90percDH | Avg_DCCH_100percDH | DH_1€ | DH_2€ | DH_3€ | DH_4€ | DH_5€ | DH_6€ | DH_7€ | DH_8€ | DH_9€ | DH_10€ | DH_12€ | DH_15€ | DH_20€ | Shape__Area | Shape__Length | OBJECT ID | Country | County | Group | Region |  | Threshold ( TJ/km2) | Count
507 | Carlow | 2.57 | 102.27 | 193.27 | 168.21 | 45.8 | 512.12 | 6.98 | 73.3696 | 1.74 | 2.21 | 2.6 | 3.22 | 3.73 | 4.59 | 5.11 | 6.64 | 8.71 | 13.29 | 0 | 33.28 | 177.94 | 242.94 | 302.89 | 386.31 | 408.06 | 408.06 | 460 | 460 | 495.09 | 512.12 | 512.12 | 6980000 | 57400 | 507 | Ireland | County Carlow | 2 | IE-CW | Urban 1 | 50 | 114
520 | Tullow | 0.36 | 31.3 | 29.57 | 2.53 | 0 | 63.76 | 1.44 | 44.2778 | 6.01 | 6.78 | 7.65 | 8.99 | 10.21 | 10.21 | 15 | 15 | 15 | 25.6 | 0 | 0 | 0 | 0 | 0 | 2.13 | 9.09 | 16.7 | 25.39 | 25.39 | 29.36 | 29.36 | 43.46 | 1440000 | 19400 | 520 | Ireland | County Carlow | 3 | IE-CW | Urban 2 | 50.1-74.9 | 124
528 | Muine Bheag | 0 | 18.07 | 21.11 | 9.55 | 0 | 48.74 | 0.88 | 55.3864 | 5.75 | 6.32 | 6.93 | 7.37 | 7.75 | 8.34 | 9.4 | 9.4 | 11.87 | 16.38 | 0 | 0 | 0 | 0 | 0 | 1.59 | 13.89 | 23.57 | 31.5 | 33.64 | 39.97 | 39.97 | 48.73 | 880000 | 9600 | 528 | Ireland | County Carlow | 2 | IE-CW | Urban 3 | 75 | 126
523 | Leighlinbridge | 0 | 7.94 | 5.74 | 0 | 0 | 13.67 | 0.34 | 40.2059 | 11 | 12.63 | 12.63 | 12.63 | 12.63 | 20.92 | 20.92 | 26.73 | 26.73 | 26.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.73 | 2.5 | 2.5 | 340000 | 5800 | 523 | Ireland | County Carlow | 3 | IE-CW
291 | Cavan | 2.44 | 45.33 | 97.84 | 143.34 | 123.43 | 412.38 | 3.96 | 104.1364 | 1.1 | 1.71 | 1.91 | 2.28 | 2.59 | 3.01 | 3.72 | 4.34 | 5.48 | 9.83 | 0 | 113.31 | 222.63 | 286.3 | 346.76 | 363.33 | 382.9 | 382.9 | 402.97 | 412.38 | 412.38 | 412.38 | 412.38 | 3959999.98 | 40200 | 291 | Ireland | County Cavan | 1 | IE-CN
326 | Kingscourt | 0 | 14.56 | 41.88 | 21.23 | 0 | 77.67 | 1.13 | 68.7345 | 4.21 | 4.77 | 5.5 | 6.03 | 6.65 | 7.21 | 7.75 | 8.36 | 10.29 | 12.71 | 0 | 0 | 0 | 4.2 | 11.42 | 19.81 | 36.07 | 52.22 | 58.16 | 62.51 | 67.85 | 73.86 | 77.67 | 1130000 | 12000 | 326 | Ireland | County Cavan | 2 | IE-CN
322 | Bailieborough | 0.29 | 19.22 | 11.1 | 29.11 | 3.12 | 62.83 | 0.95 | 66.1368 | 2.59 | 2.91 | 3.24 | 3.81 | 4.24 | 4.89 | 6.82 | 6.82 | 10.12 | 17.3 | 0 | 0 | 11.54 | 24.88 | 34.83 | 38.17 | 41.73 | 41.73 | 41.73 | 41.73 | 51.01 | 59.87 | 62.83 | 950000.01 | 12400 | 322 | Ireland | County Cavan | 2 | IE-CN
282 | Cootehill | 0 | 11.46 | 17.55 | 6.88 | 0 | 35.88 | 0.65 | 55.2 | 5.25 | 5.79 | 6.36 | 6.86 | 8.58 | 9.24 | 10.91 | 12.83 | 12.83 | 17.66 | 0 | 0 | 0 | 0 | 0 | 6.88 | 11.4 | 15.54 | 17.71 | 19.77 | 24.4 | 28.25 | 34.35 | 650000 | 9800 | 282 | Ireland | County Cavan | 2 | IE-CN
263 | Belturbet | 0 | 13.44 | 10.01 | 0 | 0 | 23.45 | 0.58 | 40.431 | 9.5 | 10.43 | 11.37 | 13 | 15.36 | 15.36 | 15.36 | 25.37 | 25.37 | 35.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 5.82 | 8.76 | 10.9 | 580000 | 12000 | 263 | Ireland | County Cavan | 3 | IE-CN
258 | Ballyconnell | 0 | 8.86 | 5.24 | 0 | 6.41 | 20.51 | 0.39 | 52.5897 | 0 | 0 | 0 | 2.96 | 6.33 | 6.33 | 10.23 | 10.23 | 17.38 | 17.38 | 0 | 6.41 | 7.74 | 7.74 | 7.74 | 7.74 | 9.97 | 9.97 | 9.97 | 9.97 | 12.61 | 12.61 | 16.59 | 390000 | 8600 | 258 | Ireland | County Cavan | 2 | IE-CN
444 | Virginia, County Cavan | 0 | 4.08 | 4.72 | 22.15 | 32.44 | 63.39 | 0.33 | 192.0909 | 0 | 0 | 0.7 | 0.83 | 1.12 | 1.56 | 1.56 | 2.18 | 2.81 | 4.92 | 24.46 | 35.19 | 55.72 | 59.31 | 62.1 | 62.1 | 63.39 | 63.39 | 63.39 | 63.39 | 63.39 | 63.39 | 63.39 | 330000.01 | 5600 | 444 | Ireland | County Cavan | 1 | IE-CN
309 | Ballinagh | 0 | 4.87 | 8.05 | 0 | 0 | 12.92 | 0.26 | 49.6923 | 0 | 8.03 | 8.64 | 8.64 | 11.26 | 13.11 | 15.14 | 15.14 | 20.49 | 20.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.85 | 3.17 | 3.17 | 5.4 | 7.45 | 8.97 | 260000 | 4400 | 309 | Ireland | County Cavan | 3 | IE-CN
310 | Shercock | 0 | 7.01 | 4.63 | 0 | 0 | 11.63 | 0.26 | 44.7308 | 0 | 0 | 8.5 | 9.06 | 9.06 | 9.06 | 16.15 | 16.15 | 22.37 | 22.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.19 | 4.11 | 4.11 | 4.11 | 7.41 | 260000 | 4200 | 310 | Ireland | County Cavan | 3 | IE-CN
333 | Virginia, County Cavan | 0 | 4.11 | 11.14 | 0 | 0 | 15.25 | 0.26 | 58.6538 | 4.75 | 4.75 | 6.04 | 6.39 | 7.08 | 8.12 | 9.16 | 9.16 | 12.91 | 16.92 | 0 | 0 | 0 | 0 | 1.14 | 1.14 | 5 | 6.42 | 8.74 | 9.77 | 9.77 | 12.79 | 15.25 | 260000 | 5600 | 333 | Ireland | County Cavan | 2 | IE-CN
323 | Ballyjamesduff | 0 | 2.66 | 8.16 | 9.76 | 0 | 20.58 | 0.24 | 85.75 | 3.25 | 3.25 | 3.57 | 3.93 | 3.93 | 3.93 | 5.33 | 6.09 | 7.9 | 11.74 | 0 | 0 | 0 | 7.49 | 12.7 | 15.52 | 16.2 | 17.91 | 17.91 | 17.91 | 20.35 | 20.58 | 20.58 | 240000.01 | 4400 | 323 | Ireland | County Cavan | 1 | IE-CN
328 | Kingscourt | 0 | 0.72 | 0.61 | 10.67 | 0 | 12 | 0.08 | 150 | 0 | 0 | 0 | 0 | 3.75 | 3.75 | 3.75 | 3.98 | 4.29 | 5.27 | 0 | 0 | 0 | 9.33 | 11.28 | 11.73 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 79999.99 | 2200 | 328 | Ireland | County Cavan | 1 | IE-CN
446 | Ennis | 3.23 | 101.59 | 257.83 | 230.52 | 16.83 | 609.99 | 8.11 | 75.2145 | 2.48 | 3.22 | 3.69 | 4.16 | 4.52 | 4.98 | 5.78 | 6.69 | 7.19 | 12.74 | 0 | 0 | 64.67 | 208.84 | 332.87 | 417.65 | 486.07 | 508.58 | 554.96 | 554.96 | 593.63 | 609.99 | 609.99 | 8110000 | 62000 | 446 | Ireland | County Clare | 1 | IE-CE
475 | Shannon | 0.92 | 28.35 | 155.54 | 109.37 | 11.77 | 305.95 | 3.58 | 85.4609 | 2.61 | 3.46 | 3.98 | 4.34 | 4.34 | 4.91 | 5.45 | 6.12 | 6.76 | 9.86 | 0 | 11.77 | 24.12 | 91.7 | 155.59 | 220.57 | 272.99 | 293.99 | 301.32 | 305.95 | 305.95 | 305.95 | 305.95 | 3580000 | 34600 | 475 | Ireland | County Clare | 1 | IE-CE
472 | Kilrush | 0 | 22.6 | 15.72 | 1.62 | 0 | 39.94 | 0.92 | 43.413 | 6.44 | 7.36 | 8.89 | 10.04 | 11.3 | 11.3 | 15.53 | 15.53 | 15.53 | 23.31 | 0 | 0 | 0 | 0 | 0 | 1.62 | 3.76 | 8.4 | 11.7 | 11.7 | 17.14 | 17.14 | 24.78 | 920000 | 16000 | 472 | Ireland | County Clare | 3 | IE-CE
474 | Sixmilebridge | 0 | 11.96 | 32.3 | 0 | 0 | 44.26 | 0.82 | 53.9756 | 6.5 | 7.39 | 7.39 | 8.47 | 9.33 | 10.29 | 10.29 | 11.68 | 13.45 | 15.64 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1 | 7.5 | 15.42 | 21.91 | 32.18 | 37.11 | 40.43 | 820000 | 8800 | 474 | Ireland | County Clare | 2 | IE-CE
453 | Clarecastle | 0.15 | 14.2 | 15.94 | 7.04 | 0 | 37.33 | 0.7 | 53.3286 | 0 | 4.41 | 4.41 | 6.03 | 7.37 | 8.18 | 9.26 | 12.32 | 12.32 | 16.95 | 0 | 0 | 0 | 4.36 | 7.04 | 11.72 | 16.97 | 18.56 | 20.77 | 23.34 | 23.34 | 28.97 | 34.78 | 700000 | 9600 | 453 | Ireland | County Clare | 2 | IE-CE
460 | Kilkee | 0.09 | 7.85 | 20.92 | 7.38 | 0 | 36.23 | 0.58 | 62.4655 | 4.75 | 5.22 | 5.7 | 6.23 | 6.76 | 6.76 | 7.46 | 8.17 | 8.99 | 11.85 | 0 | 0 | 0 | 0 | 1.71 | 9.57 | 17.72 | 27.23 | 31.53 | 31.53 | 36.14 | 36.23 | 36.23 | 580000 | 7400 | 460 | Ireland | County Clare | 2 | IE-CE
467 | Newmarket-on-Fergus | 0 | 8.59 | 14.02 | 0 | 0 | 22.61 | 0.47 | 48.1064 | 6.97 | 7.42 | 8.53 | 10.22 | 11.83 | 11.83 | 15.75 | 15.75 | 20.99 | 20.99 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 2.69 | 6.93 | 6.93 | 11.07 | 11.07 | 15.77 | 470000 | 5800 | 467 | Ireland | County Clare | 3 | IE-CE
422 | Ennistymon | 0 | 8.51 | 5.54 | 0 | 0 | 14.05 | 0.33 | 42.5758 | 8.5 | 9.32 | 13.13 | 13.13 | 13.13 | 13.13 | 19.89 | 19.89 | 25.94 | 25.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.12 | 1.68 | 2.86 | 3.71 | 8.62 | 330000 | 5400 | 422 | Ireland | County Clare | 3 | IE-CE
457 | Quin | 0 | 9.16 | 4.26 | 0 | 0 | 13.42 | 0.33 | 40.6667 | 15 | 17.16 | 17.16 | 17.16 | 21.37 | 21.37 | 21.37 | 21.37 | 30.17 | 30.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.64 | 330000 | 6800 | 457 | Ireland | County Clare | 3 | IE-CE
451 | Scarriff | 0 | 3.17 | 3.11 | 4.07 | 8.61 | 18.96 | 0.17 | 111.5294 | 0 | 0 | 1.6 | 1.6 | 1.79 | 1.79 | 2.38 | 3.39 | 5.95 | 9.18 | 0 | 11.45 | 13.78 | 14.49 | 15.79 | 16.91 | 16.91 | 16.91 | 16.91 | 18.69 | 18.96 | 18.96 | 18.96 | 170000 | 3000 | 451 | Ireland | County Clare | 1 | IE-CE
616 | Whitegate | 0 | 0.22 | 8.75 | 5.55 | 0 | 14.52 | 0.15 | 96.8 | 0 | 5.25 | 5.25 | 5.25 | 6.19 | 6.19 | 6.61 | 6.78 | 7.12 | 7.75 | 0 | 0 | 0 | 0 | 0 | 1.66 | 10.95 | 14.3 | 14.52 | 14.52 | 14.52 | 14.52 | 14.52 | 150000 | 2800 | 616 | Ireland | County Clare | 1 | IE-CE
340 | Whitegate | 0 | 0.98 | 0.54 | 3.67 | 10.92 | 16.1 | 0.08 | 201.25 | 0 | 0 | 0 | 0 | 1.1 | 1.1 | 1.39 | 1.39 | 1.79 | 4.35 | 0 | 13.15 | 14.59 | 15.55 | 15.88 | 16.1 | 16.1 | 16.1 | 16.1 | 16.1 | 16.1 | 16.1 | 16.1 | 80000 | 1400 | 340 | Ireland | County Clare | 1 | IE-CE
600 | Ballincollig | 1.48 | 44.15 | 123.8 | 260.14 | 76.97 | 506.53 | 4.67 | 108.4647 | 1.63 | 1.98 | 2.39 | 2.74 | 3.24 | 3.45 | 3.74 | 4.24 | 4.98 | 8.22 | 0 | 82.22 | 179.24 | 322 | 448.57 | 468.13 | 484.42 | 498.14 | 506.53 | 506.53 | 506.53 | 506.53 | 506.53 | 4670000 | 28200 | 600 | Ireland | County Cork | 1 | IE-CO
567 | Mallow | 0.67 | 51.52 | 112.18 | 81.1 | 16.23 | 261.7 | 3.61 | 72.4931 | 2.19 | 2.84 | 3.38 | 4.2 | 4.67 | 5.22 | 6.52 | 7.66 | 9.88 | 14.01 | 0 | 0 | 55.34 | 84.33 | 117.84 | 162.17 | 190.94 | 205.29 | 205.29 | 235.35 | 235.35 | 261.69 | 261.69 | 3610000 | 32200 | 567 | Ireland | County Cork | 2 | IE-CO
602 | Midleton | 0.75 | 37.97 | 90.14 | 174.61 | 18.08 | 321.55 | 3.48 | 92.3994 | 1.98 | 2.54 | 3.41 | 3.75 | 4.03 | 4.33 | 4.94 | 5.4 | 6.27 | 10.61 | 0 | 28.53 | 41.63 | 113.14 | 223.2 | 271.43 | 280.07 | 300.6 | 313.61 | 313.61 | 321.55 | 321.55 | 321.55 | 3480000 | 31600 | 602 | Ireland | County Cork | 1 | IE-CO
609 | Youghal | 0.4 | 48.83 | 52.64 | 25.85 | 4.26 | 131.97 | 2.38 | 55.4496 | 2.93 | 4.24 | 4.75 | 5.98 | 6.59 | 7.86 | 8.41 | 12.04 | 12.04 | 20.95 | 0 | 0 | 10.83 | 17.17 | 30.27 | 49 | 59.24 | 76.86 | 81.3 | 81.3 | 81.3 | 104.08 | 120.34 | 2380000 | 26800 | 609 | Ireland | County Cork | 2 | IE-CO
601 | Glounthaune | 0 | 23.7 | 35.99 | 149.02 | 169.4 | 378.12 | 2.3 | 164.4 | 1.3 | 1.56 | 1.56 | 1.94 | 2.12 | 2.28 | 2.47 | 2.88 | 3.37 | 5.13 | 0 | 147.53 | 300.62 | 357.59 | 370.11 | 378.12 | 378.12 | 378.12 | 378.12 | 378.12 | 378.12 | 378.12 | 378.12 | 2300000 | 27000 | 601 | Ireland | County Cork | 1 | IE-CO
572 | Fermoy | 0.26 | 27.21 | 64.35 | 47.57 | 0 | 139.39 | 2.07 | 67.3382 | 3.56 | 4.5 | 4.76 | 5.32 | 5.71 | 6.24 | 7.74 | 8.75 | 10.93 | 14.99 | 0 | 0 | 2.45 | 8.31 | 34.56 | 61.75 | 85.36 | 96.61 | 107.16 | 107.16 | 123.83 | 139.35 | 139.39 | 2070000 | 18600 | 572 | Ireland | County Cork | 2 | IE-CO
612 | Carrigaline | 0 | 36.21 | 64.72 | 13.09 | 0 | 114.02 | 1.93 | 59.0777 | 3.85 | 4.32 | 4.67 | 5.01 | 5.63 | 6.09 | 6.78 | 7.79 | 8.46 | 17.81 | 0 | 0 | 0 | 10.64 | 32.71 | 53.6 | 77.96 | 88.53 | 92.13 | 92.13 | 102.92 | 102.92 | 114.02 | 1930000 | 27800 | 612 | Ireland | County Cork | 2 | IE-CO
611 | Cobh | 0.18 | 14.09 | 56.89 | 99.27 | 9.58 | 180.01 | 1.74 | 103.454 | 1.55 | 2.18 | 2.74 | 3.08 | 3.44 | 3.69 | 4.02 | 4.67 | 5.29 | 7.26 | 0 | 9.58 | 40.86 | 108.42 | 143.16 | 169.35 | 172.63 | 180.01 | 180.01 | 180.01 | 180.01 | 180.01 | 180.01 | 1740000 | 12200 | 611 | Ireland | County Cork | 1 | IE-CO
619 | Kinsale | 0.45 | 27.17 | 45.34 | 42.89 | 0 | 115.86 | 1.64 | 70.6463 | 2.93 | 3.57 | 4.12 | 4.23 | 5.16 | 5.87 | 6.63 | 7.5 | 10.34 | 13.18 | 0 | 0 | 6.7 | 28.46 | 47.96 | 69.34 | 78.82 | 85.34 | 85.34 | 85.34 | 101.87 | 115.86 | 115.86 | 1640000 | 16600 | 619 | Ireland | County Cork | 2 | IE-CO
615 | Bandon | 0.14 | 32.02 | 38.44 | 2.65 | 0 | 73.25 | 1.53 | 47.8758 | 4.75 | 6.02 | 6.37 | 7.34 | 8.71 | 9.58 | 13.4 | 13.4 | 18.38 | 26.67 | 0 | 0 | 0 | 0 | 3.78 | 8.69 | 16.49 | 23.89 | 34.47 | 38.06 | 38.06 | 50.56 | 62.23 | 1530000 | 26000 | 615 | Ireland | County Cork | 3 | IE-CO
603 | Carrigtwohill | 0.19 | 12.09 | 58.55 | 34.04 | 0 | 104.86 | 1.33 | 78.8421 | 3.25 | 3.9 | 4.29 | 4.95 | 4.95 | 5.71 | 6.07 | 6.93 | 7.71 | 11.33 | 0 | 0 | 0 | 18.79 | 40.27 | 57.4 | 83.86 | 92.67 | 97.6 | 97.6 | 104.86 | 104.86 | 104.86 | 1330000 | 14600 | 603 | Ireland | County Cork | 1 | IE-CO
560 | Mitchelstown | 0 | 20.97 | 34.82 | 9.92 | 30.63 | 96.35 | 1.26 | 76.4683 | 1.1 | 1.37 | 1.56 | 2.2 | 3.09 | 4.32 | 5.45 | 6.26 | 8.39 | 11.95 | 0 | 33.55 | 38.93 | 51.96 | 62.69 | 65.85 | 70.38 | 70.38 | 79.4 | 79.4 | 89.49 | 89.49 | 96.34 | 1260000 | 16800 | 560 | Ireland | County Cork | 1 | IE-CO
606 | Passage West | 0 | 10.51 | 42.76 | 15.27 | 0 | 68.54 | 0.97 | 70.6598 | 4.48 | 5.01 | 5.01 | 5.8 | 5.8 | 6.21 | 6.57 | 7.44 | 9.53 | 12.21 | 0 | 0 | 0 | 0 | 10.28 | 26.59 | 48.56 | 55.51 | 55.51 | 61.14 | 61.14 | 68.54 | 68.54 | 970000 | 13000 | 606 | Ireland | County Cork | 2 | IE-CO
607 | Bantry | 0.34 | 21.36 | 21.7 | 1.89 | 0 | 45.3 | 0.97 | 46.701 | 5.69 | 6.83 | 7.87 | 8.82 | 9.97 | 9.97 | 15.34 | 15.34 | 21.71 | 28.48 | 0 | 0 | 0 | 0 | 0 | 3.88 | 8.23 | 13.51 | 16.55 | 18.91 | 18.91 | 18.91 | 29.42 | 970000 | 12800 | 607 | Ireland | County Cork | 3 | IE-CO
596 | Tower | 0 | 13.87 | 27.74 | 1.24 | 0 | 42.85 | 0.82 | 52.2561 | 5.2 | 5.85 | 7.23 | 7.23 | 8.01 | 8.86 | 9.56 | 12.22 | 12.22 | 16.29 | 0 | 0 | 0 | 0 | 3.35 | 5.95 | 5.95 | 12.42 | 25.24 | 27.99 | 27.99 | 33.82 | 39.62 | 820000 | 9600 | 596 | Ireland | County Cork | 2 | IE-CO
555 | Kanturk | 0.19 | 16.36 | 21.13 | 0 | 0 | 37.67 | 0.8 | 47.0875 | 8.07 | 8.07 | 9.25 | 9.25 | 10.07 | 11.54 | 11.54 | 14.31 | 14.31 | 18.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77 | 1.82 | 17.08 | 22.36 | 28.15 | 33.96 | 800000 | 12400 | 555 | Ireland | County Cork | 3 | IE-CO
621 | Skibbereen | 0 | 13.89 | 15.39 | 1.74 | 0 | 31.01 | 0.66 | 46.9848 | 4.75 | 5.05 | 6.24 | 6.8 | 8.23 | 9.68 | 9.68 | 12.57 | 17.26 | 25.35 | 0 | 0 | 0 | 0 | 3.92 | 6.44 | 10.63 | 13.08 | 15.89 | 17.8 | 17.8 | 21.94 | 26.46 | 660000 | 14200 | 621 | Ireland | County Cork | 3 | IE-CO
595 | Blarney | 0 | 10.47 | 24.27 | 2.85 | 0 | 37.59 | 0.63 | 59.6667 | 5.54 | 5.95 | 6.78 | 7.27 | 7.27 | 7.9 | 9.05 | 9.05 | 11.62 | 15.19 | 0 | 0 | 0 | 0 | 0 | 4.82 | 10.33 | 20.12 | 24.08 | 26.17 | 31.19 | 31.19 | 37.59 | 630000 | 8400 | 595 | Ireland | County Cork | 2 | IE-CO
620 | Clonakilty | 0.2 | 9.75 | 20.69 | 1.23 | 3.29 | 35.16 | 0.59 | 59.5932 | 2.4 | 3.59 | 4.51 | 5.46 | 6.55 | 7.19 | 8.54 | 8.54 | 11.4 | 18.74 | 0 | 0 | 4.53 | 7.67 | 9.36 | 12.29 | 16.83 | 22.04 | 23.63 | 23.63 | 28.59 | 28.59 | 35.16 | 590000 | 8200 | 620 | Ireland | County Cork | 2 | IE-CO
610 | Dunmanway | 0 | 13.13 | 13.67 | 0 | 0 | 26.8 | 0.58 | 46.2069 | 6.96 | 7.69 | 7.69 | 9.28 | 9.89 | 9.89 | 14.5 | 14.5 | 22.25 | 28.78 | 0 | 0 | 0 | 0 | 0 | 0 | 1.72 | 3.28 | 9.69 | 11.27 | 11.27 | 16.22 | 16.22 | 580000 | 11600 | 610 | Ireland | County Cork | 3 | IE-CO
588 | Macroom | 0 | 9.27 | 20.01 | 0 | 0 | 29.28 | 0.55 | 53.2364 | 4.75 | 5.31 | 5.62 | 6.38 | 7.03 | 8.13 | 9.02 | 11.18 | 11.18 | 20.68 | 0 | 0 | 0 | 0 | 1.14 | 6.57 | 9.99 | 15.79 | 18.03 | 18.87 | 21.81 | 21.81 | 26.51 | 550000 | 9200 | 588 | Ireland | County Cork | 2 | IE-CO
569 | Millstreet | 0 | 8.87 | 12.51 | 6.12 | 6.23 | 33.72 | 0.5 | 67.44 | 0 | 1.3 | 2.58 | 2.58 | 4.71 | 5.6 | 7.17 | 7.17 | 10.46 | 14.22 | 0 | 8.54 | 9.87 | 13.49 | 16.2 | 18.87 | 21.29 | 22.59 | 22.59 | 22.59 | 27.69 | 31.73 | 33.72 | 500000 | 9400 | 569 | Ireland | County Cork | 2 | IE-CO
608 | Castlemartyr | 0 | 5.5 | 15.59 | 3.25 | 0 | 24.34 | 0.42 | 57.9524 | 0 | 5.75 | 6.1 | 7.03 | 7.03 | 7.96 | 8.47 | 9.97 | 11.01 | 14.17 | 0 | 0 | 0 | 0 | 0 | 2.71 | 5.14 | 13.43 | 17.1 | 19.19 | 20.62 | 23.14 | 24.34 | 420000 | 4400 | 608 | Ireland | County Cork | 2 | IE-CO
614 | Cloyne | 0 | 4.9 | 15.82 | 1.22 | 0 | 21.94 | 0.39 | 56.2564 | 5.9 | 5.9 | 5.9 | 7.69 | 7.69 | 8.42 | 9.04 | 9.86 | 13.24 | 13.24 | 0 | 0 | 0 | 0 | 1.22 | 2.09 | 2.09 | 6.72 | 11.29 | 16.66 | 18.38 | 19.73 | 21.94 | 390000 | 5600 | 614 | Ireland | County Cork | 2 | IE-CO
613 | Ringaskiddy | 0 | 1.67 | 10.98 | 30.53 | 11.23 | 54.41 | 0.36 | 151.1389 | 0 | 1.3 | 1.79 | 2.3 | 2.64 | 3.1 | 3.75 | 4.05 | 4.57 | 5.77 | 0 | 14.02 | 23.06 | 37.01 | 52.04 | 54.19 | 54.41 | 54.41 | 54.41 | 54.41 | 54.41 | 54.41 | 54.41 | 360000 | 7800 | 613 | Ireland | County Cork | 1 | IE-CO
617 | Crosshaven | 0 | 5.3 | 13.25 | 0 | 3.4 | 21.95 | 0.35 | 62.7143 | 0 | 2 | 3.27 | 4.5 | 5.21 | 5.21 | 6.95 | 9.93 | 9.93 | 13.71 | 0 | 0 | 4.58 | 6.65 | 8.24 | 10.03 | 14.65 | 14.65 | 14.65 | 17.54 | 17.54 | 20.07 | 21.95 | 350000 | 8200 | 617 | Ireland | County Cork | 2 | IE-CO
550 | Newmarket, County Cork | 0 | 8.7 | 2.14 | 4.47 | 0 | 15.31 | 0.33 | 46.3939 | 0 | 3.75 | 4.36 | 5.92 | 6.83 | 6.83 | 13.17 | 13.17 | 13.17 | 20.61 | 0 | 0 | 0 | 2.65 | 4.47 | 6.11 | 6.61 | 6.61 | 6.61 | 6.61 | 6.61 | 10.15 | 10.15 | 330000 | 5200 | 550 | Ireland | County Cork | 3 | IE-CO
571 | Kilworth | 0 | 5.92 | 9.61 | 0 | 0 | 15.53 | 0.33 | 47.0606 | 0 | 9.5 | 10.45 | 11.58 | 11.58 | 14.37 | 14.37 | 16.45 | 20.8 | 20.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.75 | 5.02 | 8.86 | 11.02 | 330000 | 5400 | 571 | Ireland | County Cork | 3 | IE-CO
554 | Buttevant | 0 | 7.48 | 3.87 | 0 | 0 | 11.35 | 0.31 | 36.6129 | 6.5 | 8.26 | 12.52 | 12.52 | 17.25 | 17.25 | 17.25 | 26.11 | 26.11 | 26.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.9 | 1.47 | 1.47 | 2.58 | 3.22 | 5.19 | 310000 | 5200 | 554 | Ireland | County Cork | 3 | IE-CO
605 | Killeagh | 0 | 5.19 | 7.37 | 0 | 0 | 12.56 | 0.29 | 43.3103 | 8.5 | 9.55 | 10.47 | 11.95 | 13.66 | 13.66 | 13.66 | 17.94 | 20.92 | 28.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.44 | 2.02 | 4.09 | 5.7 | 9.15 | 290000 | 4200 | 605 | Ireland | County Cork | 3 | IE-CO
587 | Watergrasshill | 0 | 5.24 | 5.08 | 3.22 | 0 | 13.55 | 0.27 | 50.1852 | 0 | 3.75 | 4.39 | 5.33 | 6.21 | 7.22 | 8.36 | 10.26 | 10.26 | 16.21 | 0 | 0 | 0 | 1.85 | 4.18 | 5.06 | 6.97 | 8.2 | 8.78 | 8.78 | 9.91 | 9.91 | 12.4 | 270000 | 4000 | 587 | Ireland | County Cork | 2 | IE-CO
570 | Dromahane | 0 | 3.7 | 6.65 | 0 | 0 | 10.35 | 0.21 | 49.2857 | 0 | 9.5 | 10.34 | 11.27 | 12.91 | 12.91 | 12.91 | 17.13 | 17.13 | 21.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.33 | 3.76 | 4.96 | 7.63 | 210000 | 4600 | 570 | Ireland | County Cork | 3 | IE-CO
580 | Little Island | 0 | 2.27 | 0.53 | 5.73 | 3.16 | 11.7 | 0.12 | 97.5 | 0 | 0 | 2.4 | 2.4 | 2.78 | 2.78 | 3.42 | 3.96 | 5.16 | 8.6 | 0 | 0 | 5.77 | 8.89 | 9.43 | 9.86 | 9.86 | 10.99 | 11.48 | 11.7 | 11.7 | 11.7 | 11.7 | 120000 | 2800 | 580 | Ireland | County Cork | 1 | IE-CO
406 | Newtownshandrum | 0 | 0.74 | 0 | 7.31 | 3.65 | 11.7 | 0.07 | 167.1429 | 0 | 0 | 0 | 3.25 | 3.25 | 3.25 | 3.25 | 3.25 | 3.86 | 4.49 | 0 | 0 | 0 | 9.49 | 10.97 | 10.97 | 10.97 | 10.97 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 70000 | 2000 | 406 | Ireland | County Cork | 1 | IE-CO
559 | Gortroe | 0 | 0.8 | 2.52 | 4.15 | 4.03 | 11.5 | 0.1 | 115 | 0 | 0 | 0 | 2 | 2 | 2.82 | 2.82 | 3.37 | 4.45 | 6.02 | 0 | 0 | 6.32 | 8.17 | 9.52 | 10.7 | 11.05 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 100000 | 1600 | 559 | Ireland | County Cork | 1 | IE-CO
618 | Hughes Cross roads | 0 | 3.28 | 4.35 | 3.02 | 0 | 10.65 | 0.17 | 62.6471 | 0 | 0 | 6.5 | 6.5 | 7.33 | 7.65 | 8.76 | 8.76 | 12.07 | 17.25 | 0 | 0 | 0 | 0 | 0 | 0 | 3.02 | 6.06 | 7.15 | 7.15 | 7.15 | 9.7 | 10.22 | 170000 | 3600 | 618 | Ireland | County Cork | 2 | IE-CO
622 | Trineens | 0 | 3.87 | 8.01 | 0 | 0 | 11.87 | 0.21 | 56.5238 | 5.25 | 5.49 | 6.36 | 7.35 | 8.41 | 9.15 | 9.55 | 10.83 | 12.66 | 12.66 | 0 | 0 | 0 | 0 | 0 | 1.95 | 2.75 | 4.01 | 5.65 | 7.24 | 8.52 | 9.78 | 11.87 | 210000 | 3800 | 622 | Ireland | County Cork | 2 | IE-CO
20 | Letterkenny | 0.58 | 123.44 | 150.39 | 175.21 | 126.34 | 575.96 | 7.25 | 79.4428 | 1.3 | 1.74 | 1.99 | 2.54 | 3.1 | 3.9 | 4.88 | 5.55 | 7.98 | 15.37 | 0 | 148.59 | 260.06 | 339.32 | 398.13 | 421.29 | 421.29 | 481.29 | 481.29 | 481.29 | 541.33 | 541.33 | 575.96 | 7250000 | 90400 | 20 | Ireland | County Donegal | 1 | IE-DL
3 | Buncrana | 0.7 | 41.65 | 69.83 | 110.38 | 29.48 | 252.05 | 2.9 | 86.9138 | 2.02 | 2.69 | 2.96 | 3.59 | 4.03 | 4.69 | 5.19 | 6.12 | 6.68 | 12.06 | 0 | 9.77 | 65.21 | 106.84 | 148.68 | 192.71 | 209.1 | 209.1 | 226.86 | 226.86 | 246.25 | 252.05 | 252.05 | 2900000.02 | 32800 | 3 | Ireland | County Donegal | 1 | IE-DL
47 | Ballybofey | 0.18 | 43.54 | 27.72 | 10.68 | 3.16 | 85.27 | 1.83 | 46.5956 | 3.52 | 5.22 | 6.07 | 7.99 | 9.66 | 9.66 | 13.31 | 13.31 | 20.46 | 20.46 | 0 | 0 | 3.16 | 9.65 | 11.23 | 16.16 | 25.68 | 33.24 | 33.24 | 39.88 | 39.88 | 52.32 | 52.32 | 1830000 | 34200 | 47 | Ireland | County Donegal | 3 | IE-DL
21 | Iscaheen | 0 | 0 | 0 | 6.83 | 7.78 | 14.61 | 0.05 | 292.2 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 2.31 | 2.31 | 2.31 | 0 | 0 | 14.61 | 14.61 | 14.61 | 14.61 | 14.61 | 14.61 | 14.61 | 14.61 | 14.61 | 14.61 | 14.61 | 50000 | 1800 | 21 | Ireland | County Donegal | 1 | IE-DL
65 | Donegal | 0 | 15.43 | 22.9 | 15.82 | 4.21 | 58.35 | 0.97 | 60.1546 | 2.71 | 3.82 | 3.82 | 5.59 | 6.15 | 6.71 | 7.48 | 9.79 | 9.79 | 13.98 | 0 | 0 | 5.67 | 8.94 | 8.94 | 22.3 | 33.18 | 38.37 | 41.37 | 45.56 | 45.56 | 52.91 | 58.36 | 970000 | 18400 | 65 | Ireland | County Donegal | 2 | IE-DL
1 | Carndonagh | 0.11 | 22.49 | 10.68 | 0 | 0 | 33.27 | 0.85 | 39.1412 | 12.11 | 12.11 | 12.11 | 21.41 | 21.41 | 21.41 | 21.41 | 32.06 | 32.06 | 40.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0.79 | 0.79 | 0.79 | 0.79 | 1.93 | 3.11 | 3.11 | 850000 | 17800 | 1 | Ireland | County Donegal | 3 | IE-DL
93 | Bundoran | 0 | 11 | 12.47 | 49.16 | 0 | 72.64 | 0.8 | 90.8 | 3.25 | 3.49 | 4.03 | 4.32 | 4.58 | 4.58 | 5.07 | 5.54 | 6.77 | 10.12 | 0 | 0 | 0 | 16.12 | 34.63 | 61.07 | 64.1 | 64.1 | 64.1 | 64.1 | 72.64 | 72.64 | 72.64 | 800000 | 15200 | 93 | Ireland | County Donegal | 1 | IE-DL
22 | Iscaheen | 0.14 | 4.95 | 30.49 | 21.86 | 16.02 | 73.46 | 0.66 | 111.303 | 0 | 1.1 | 1.82 | 2.49 | 2.73 | 3.21 | 4.12 | 4.81 | 5.4 | 8.06 | 0 | 18.9 | 33.52 | 38.38 | 57.87 | 68.35 | 68.35 | 68.35 | 73.46 | 73.46 | 73.46 | 73.46 | 73.46 | 660000 | 7800 | 22 | Ireland | County Donegal | 1 | IE-DL
4 | Moville | 0 | 13.47 | 10.6 | 2.85 | 0 | 26.93 | 0.62 | 43.4355 | 6.5 | 7.41 | 8.52 | 9.51 | 10.78 | 10.78 | 15.51 | 15.51 | 22.11 | 22.11 | 0 | 0 | 0 | 0 | 0 | 0 | 2.85 | 3.98 | 7.52 | 9.65 | 11.34 | 11.34 | 17 | 620000 | 9200 | 4 | Ireland | County Donegal | 3 | IE-DL
25 | Iscaheen | 0 | 0 | 0 | 6.88 | 3.91 | 10.79 | 0.04 | 269.75 | 0 | 0 | 0 | 2 | 2 | 2 | 2.5 | 2.5 | 2.82 | 2.82 | 0 | 0 | 8.76 | 10.79 | 10.79 | 10.79 | 10.79 | 10.79 | 10.79 | 10.79 | 10.79 | 10.79 | 10.79 | 40000 | 1000 | 25 | Ireland | County Donegal | 1 | IE-DL
91 | Ballyshannon | 0 | 13.93 | 9.11 | 4.99 | 0 | 28.03 | 0.6 | 46.7167 | 4.25 | 4.25 | 6.11 | 6.93 | 8.6 | 8.6 | 12.11 | 12.11 | 12.11 | 20.56 | 0 | 0 | 0 | 0 | 2.27 | 5.92 | 11.14 | 12.85 | 14.01 | 14.01 | 14.01 | 17.83 | 17.83 | 600000.01 | 11200 | 91 | Ireland | County Donegal | 3 | IE-DL
26 | Iscaheen | 0 | 4.39 | 7.76 | 12.87 | 3.06 | 28.09 | 0.31 | 90.6129 | 0 | 2.8 | 3.38 | 3.38 | 3.7 | 3.85 | 4.45 | 5.15 | 6.27 | 9.96 | 0 | 0 | 3.06 | 14.53 | 21.37 | 23.62 | 24.37 | 24.37 | 24.37 | 27.36 | 28.09 | 28.09 | 28.09 | 310000 | 5200 | 26 | Ireland | County Donegal | 1 | IE-DL
13 | Ramelton | 0 | 15.19 | 5 | 0 | 0 | 20.19 | 0.52 | 38.8269 | 8.5 | 10.7 | 12.45 | 12.45 | 12.45 | 19.17 | 19.17 | 19.17 | 26.69 | 26.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.13 | 2.99 | 3.8 | 5 | 10.75 | 519999.99 | 9800 | 13 | Ireland | County Donegal | 3 | IE-DL
41 | Convoy, County Donegal | 0.19 | 10.03 | 8.72 | 3.16 | 0 | 22.11 | 0.5 | 44.22 | 6.5 | 6.98 | 8.69 | 9.9 | 11.08 | 11.08 | 15.86 | 15.86 | 21.78 | 21.78 | 0 | 0 | 0 | 0 | 0 | 0 | 3.16 | 4.51 | 6.36 | 7.87 | 9.22 | 9.22 | 14.05 | 500000 | 8800 | 41 | Ireland | County Donegal | 3 | IE-DL
52 | Lifford | 0 | 8.56 | 8.8 | 19.65 | 0 | 37.01 | 0.48 | 77.1042 | 3.75 | 4.05 | 4.48 | 4.8 | 5.08 | 5.64 | 6.28 | 7.1 | 8.95 | 13.73 | 0 | 0 | 0 | 2.66 | 13.83 | 20.8 | 26.76 | 27.33 | 30.48 | 30.48 | 30.48 | 36.02 | 37.01 | 480000 | 8000 | 52 | Ireland | County Donegal | 1 | IE-DL
15 | Muff, County Donegal | 0 | 8.87 | 11.84 | 3.02 | 0 | 23.74 | 0.46 | 51.6087 | 4.75 | 6.06 | 6.06 | 8 | 9.35 | 11.01 | 11.01 | 13.87 | 18.89 | 18.89 | 0 | 0 | 0 | 0 | 1.7 | 3.02 | 4.18 | 7.78 | 8.69 | 10.75 | 13.31 | 16.72 | 20.7 | 460000 | 6400 | 15 | Ireland | County Donegal | 2 | IE-DL
23 | Newtown Cunningham | 0 | 10.75 | 6.66 | 0 | 3.35 | 20.76 | 0.43 | 48.2791 | 0 | 2.4 | 4.19 | 5.53 | 8.77 | 8.77 | 12.93 | 12.93 | 21.04 | 21.04 | 0 | 0 | 3.35 | 3.35 | 6.33 | 6.95 | 6.95 | 6.95 | 9.39 | 9.39 | 9.39 | 12.64 | 12.64 | 430000 | 7400 | 23 | Ireland | County Donegal | 3 | IE-DL
5 | Milford, County Donegal | 0 | 9.02 | 4.81 | 4.07 | 0 | 17.9 | 0.39 | 45.8974 | 0 | 3.75 | 5.85 | 5.85 | 7.82 | 9.86 | 9.86 | 18.13 | 18.13 | 18.13 | 0 | 0 | 0 | 2.63 | 2.63 | 5.26 | 5.26 | 8.88 | 8.88 | 10.08 | 10.08 | 10.08 | 13.89 | 389999.99 | 9000 | 5 | Ireland | County Donegal | 3 | IE-DL
40 | Raphoe | 0.15 | 7.95 | 7.4 | 5.86 | 3.77 | 25.13 | 0.38 | 66.1316 | 0 | 2 | 3.07 | 4.2 | 4.67 | 6.51 | 6.51 | 11.1 | 11.1 | 16.24 | 0 | 0 | 3.77 | 8.14 | 10.81 | 13.86 | 14.64 | 14.64 | 14.64 | 14.64 | 19.47 | 19.47 | 25.13 | 379999.99 | 6000 | 40 | Ireland | County Donegal | 2 | IE-DL
92 | Tievemore | 0 | 0 | 0 | 0 | 33.28 | 33.28 | 0.01 | 3328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.28 | 33.28 | 33.28 | 33.28 | 33.28 | 33.28 | 33.28 | 33.28 | 33.28 | 33.28 | 33.28 | 33.28 | 33.28 | 10000 | 400 | 92 | Ireland | County Donegal | 1 | IE-DL
61 | Killybegs | 0 | 4.85 | 5.61 | 6.22 | 0 | 16.69 | 0.3 | 55.6333 | 0 | 0 | 5.25 | 5.79 | 6.45 | 7.46 | 7.87 | 8.99 | 12.84 | 12.84 | 0 | 0 | 0 | 0 | 0 | 6.22 | 8.87 | 10.53 | 11.84 | 11.84 | 13.35 | 14.35 | 14.35 | 300000 | 5600 | 61 | Ireland | County Donegal | 2 | IE-DL
10 | Kilmacrennan | 0 | 7.98 | 2.5 | 0 | 0 | 10.48 | 0.29 | 36.1379 | 9.5 | 13.81 | 13.81 | 20.52 | 20.52 | 20.52 | 30.1 | 30.1 | 30.1 | 30.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69 | 0.69 | 1.4 | 1.4 | 290000 | 7600 | 10 | Ireland | County Donegal | 3 | IE-DL
56 | Castlefin | 0 | 7.26 | 3.72 | 0 | 0 | 10.98 | 0.28 | 39.2143 | 13 | 16.54 | 16.54 | 21.48 | 21.48 | 21.48 | 21.48 | 21.48 | 31.64 | 31.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1.71 | 280000 | 5400 | 56 | Ireland | County Donegal | 3 | IE-DL
317 | Greencastle | 0 | 7.01 | 3.97 | 0 | 0 | 10.98 | 0.28 | 39.2143 | 5.25 | 6.18 | 9.35 | 9.35 | 18.26 | 18.26 | 18.26 | 26.14 | 26.14 | 36.32 | 0 | 0 | 0 | 0 | 0 | 0.98 | 1.68 | 1.68 | 1.68 | 2.29 | 2.29 | 2.29 | 5.33 | 279999.99 | 6000 | 317 | Ireland | County Donegal | 3 | IE-DL
167 | Laghy | 0 | 0 | 9.81 | 4.35 | 0 | 14.16 | 0.14 | 101.1429 | 0 | 0 | 3.67 | 4.86 | 5.34 | 5.34 | 5.34 | 6.97 | 7.37 | 8.6 | 0 | 0 | 2.97 | 3.88 | 5.63 | 6.49 | 10.68 | 11.85 | 13.39 | 14.16 | 14.16 | 14.16 | 14.16 | 139999.99 | 2800 | 167 | Ireland | County Donegal | 1 | IE-DL
327 | Ballykenny | 0 | 0.85 | 0 | 0 | 14.98 | 15.83 | 0.04 | 395.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.9 | 0.9 | 1.91 | 9.65 | 15.47 | 15.83 | 15.83 | 15.83 | 15.83 | 15.83 | 15.83 | 15.83 | 15.83 | 15.83 | 15.83 | 15.83 | 40000 | 1000 | 327 | Ireland | County Donegal | 1 | IE-DL
2 | Bunbeg | 0 | 1.3 | 1.3 | 11.49 | 4.85 | 18.94 | 0.13 | 145.6923 | 0 | 0 | 1.6 | 2.34 | 2.34 | 2.8 | 3.13 | 3.78 | 4.09 | 5.66 | 0 | 4.85 | 9.71 | 14.96 | 17.64 | 18.47 | 18.94 | 18.94 | 18.94 | 18.94 | 18.94 | 18.94 | 18.94 | 130000 | 2600 | 2 | Ireland | County Donegal | 1 | IE-DL
62 | Killybegs | 0 | 0 | 3.68 | 9.39 | 0 | 13.07 | 0.1 | 130.7 | 0 | 0 | 3.25 | 3.25 | 3.25 | 3.25 | 4.26 | 4.94 | 4.94 | 5.83 | 0 | 0 | 0 | 2.62 | 10.32 | 12.56 | 13.07 | 13.07 | 13.07 | 13.07 | 13.07 | 13.07 | 13.07 | 100000 | 3000 | 62 | Ireland | County Donegal | 1 | IE-DL
417 | Blanchardstown | 5.01 | 166.25 | 754.57 | 469.99 | 19.13 | 1414.95 | 18.41 | 76.8577 | 2.83 | 3.33 | 3.67 | 4.15 | 4.34 | 4.82 | 5.24 | 5.56 | 6.38 | 9.86 | 0 | 16 | 103.13 | 457.77 | 814.41 | 1151.38 | 1291.68 | 1346.41 | 1390.03 | 1414.95 | 1414.95 | 1414.95 | 1414.95 | 18410000.02 | 89200 | 417 | Ireland | County Dublin | 1 | IE-D
401 | Swords | 1.99 | 64.43 | 378.81 | 250.61 | 23.94 | 719.79 | 8.35 | 86.2024 | 2.65 | 3.17 | 3.56 | 3.79 | 4.31 | 4.31 | 4.75 | 5.42 | 6.04 | 8.77 | 0 | 23.95 | 66.27 | 244.96 | 438.47 | 606.12 | 670.16 | 710.93 | 719.79 | 719.79 | 719.79 | 719.79 | 719.79 | 8350000.02 | 44600 | 401 | Ireland | County Dublin | 1 | IE-D
410 | Malahide | 0.59 | 60.48 | 246.94 | 33.76 | 0 | 341.77 | 5.33 | 64.122 | 4.29 | 4.94 | 5.51 | 6.13 | 6.58 | 6.58 | 7.6 | 8.15 | 10.1 | 14.91 | 0 | 0 | 0 | 7.95 | 59.57 | 93.3 | 167.94 | 247.22 | 277.86 | 277.86 | 301.76 | 341.77 | 341.77 | 5329999.99 | 42200 | 410 | Ireland | County Dublin | 2 | IE-D
379 | Balbriggan | 0.8 | 35.65 | 169.85 | 117.02 | 3.22 | 326.53 | 3.92 | 83.2985 | 3.07 | 3.49 | 3.79 | 4.12 | 4.3 | 4.78 | 5.19 | 5.82 | 6.63 | 10.11 | 0 | 0 | 5.55 | 90.3 | 183.75 | 260.55 | 289.4 | 309.17 | 309.17 | 325.92 | 326.53 | 326.53 | 326.53 | 3920000 | 23600 | 379 | Ireland | County Dublin | 1 | IE-D
393 | Rush | 0.3 | 45.55 | 97.92 | 8 | 3.04 | 154.81 | 2.76 | 56.0906 | 4.47 | 4.47 | 5.85 | 6.45 | 7.27 | 8.21 | 8.89 | 10.14 | 12.53 | 16.01 | 0 | 0 | 3.04 | 11.04 | 15.39 | 37.88 | 48.99 | 77.41 | 93.89 | 93.89 | 108.81 | 129.62 | 154.81 | 2760000.01 | 24400 | 393 | Ireland | County Dublin | 2 | IE-D
381 | Skerries, Dublin | 1.06 | 16.96 | 106.89 | 10.34 | 0 | 135.26 | 2.08 | 65.0288 | 4.41 | 5.25 | 5.25 | 5.68 | 6.15 | 6.74 | 7.26 | 7.9 | 8.77 | 13.92 | 0 | 0 | 0 | 0 | 13.67 | 40.96 | 73.63 | 105.31 | 116.39 | 124.54 | 131.68 | 135.25 | 135.25 | 2079999.99 | 9200 | 381 | Ireland | County Dublin | 2 | IE-D
398 | Donabate | 0 | 16.32 | 68.32 | 8.19 | 0 | 92.83 | 1.38 | 67.2681 | 4.22 | 4.74 | 5.02 | 5.61 | 5.94 | 6.52 | 7.2 | 8.46 | 8.46 | 12.46 | 0 | 0 | 0 | 4.34 | 13.92 | 39 | 58.85 | 69.51 | 73.75 | 73.75 | 84.5 | 92.83 | 92.83 | 1380000 | 9000 | 398 | Ireland | County Dublin | 2 | IE-D
392 | Lusk | 0 | 9.4 | 62.11 | 22.84 | 0 | 94.35 | 1.16 | 81.3362 | 3.75 | 4.13 | 4.59 | 4.84 | 4.84 | 5.37 | 5.67 | 6.03 | 6.91 | 8.79 | 0 | 0 | 0 | 3.09 | 36.1 | 61.35 | 84.45 | 85.98 | 93.28 | 94.35 | 94.35 | 94.35 | 94.35 | 1159999.99 | 9000 | 392 | Ireland | County Dublin | 1 | IE-D
137 | Crumlin, Dublin | 0 | 2.18 | 80.73 | 16.6 | 3.58 | 103.09 | 1.15 | 89.6435 | 3.76 | 5.15 | 5.15 | 6.37 | 6.37 | 7.04 | 7.04 | 7.65 | 8.24 | 9.58 | 0 | 0 | 6.05 | 9.52 | 9.52 | 19.36 | 40.17 | 77.92 | 99.08 | 103.09 | 103.09 | 103.09 | 103.09 | 1150000 | 8400 | 137 | Ireland | County Dublin | 1 | IE-D
436 | Rathcoole | 0.14 | 5.78 | 33.38 | 2.68 | 0 | 41.99 | 0.64 | 65.6094 | 4.53 | 5.51 | 5.51 | 6.39 | 7.07 | 7.07 | 7.73 | 8.31 | 8.89 | 13.77 | 0 | 0 | 0 | 0 | 3.75 | 7.42 | 13.28 | 27 | 34.87 | 34.87 | 37.81 | 41.99 | 41.99 | 640000 | 5800 | 436 | Ireland | County Dublin | 2 | IE-D
397 | Portrane | 0 | 7.73 | 4.91 | 0 | 0 | 12.64 | 0.32 | 39.5 | 12.8 | 14.95 | 14.95 | 20.5 | 20.5 | 20.5 | 29.94 | 29.94 | 29.94 | 29.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.64 | 1.97 | 1.97 | 320000 | 6600 | 397 | Ireland | County Dublin | 3 | IE-D
399 | Grattan Lodge | 0 | 0.35 | 1.6 | 6.34 | 17.97 | 26.26 | 0.11 | 238.7273 | 0 | 0 | 0 | 1.6 | 1.6 | 1.6 | 1.79 | 1.97 | 2.18 | 2.9 | 0 | 19.82 | 25.91 | 26.26 | 26.26 | 26.26 | 26.26 | 26.26 | 26.26 | 26.26 | 26.26 | 26.26 | 26.26 | 110000 | 2000 | 399 | Ireland | County Dublin | 1 | IE-D
409 | Ward Cross | 0 | 4.39 | 11.16 | 0 | 0 | 15.55 | 0.3 | 51.8333 | 0 | 7.8 | 8.42 | 9.02 | 9.94 | 11.6 | 11.6 | 15.07 | 18.86 | 18.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.55 | 4 | 6.8 | 8.57 | 8.57 | 13.63 | 300000 | 6200 | 409 | Ireland | County Dublin | 2 | IE-D
413 | Ward Cross | 0 | 0.7 | 4.18 | 7.13 | 8.91 | 20.92 | 0.13 | 160.9231 | 0 | 0 | 1.6 | 1.6 | 1.79 | 1.94 | 2.21 | 2.7 | 2.93 | 3.87 | 0 | 11.66 | 17.09 | 20.22 | 20.93 | 20.93 | 20.93 | 20.93 | 20.93 | 20.93 | 20.93 | 20.93 | 20.93 | 130000 | 3200 | 413 | Ireland | County Dublin | 1 | IE-D
414 | Ward Cross | 0 | 2.93 | 17.18 | 48.26 | 0 | 68.38 | 0.62 | 110.2903 | 3.25 | 3.25 | 3.25 | 3.71 | 3.71 | 3.95 | 3.95 | 4.13 | 4.33 | 5.9 | 0 | 0 | 0 | 39.5 | 66.24 | 68.11 | 68.38 | 68.38 | 68.38 | 68.38 | 68.38 | 68.38 | 68.38 | 620000 | 5200 | 414 | Ireland | County Dublin | 1 | IE-D
419 | Grattan Lodge | 0 | 0.78 | 20.38 | 13.96 | 0 | 35.12 | 0.34 | 103.2941 | 0 | 3.41 | 3.91 | 4.28 | 4.56 | 4.56 | 5.01 | 5.01 | 5.5 | 6.31 | 0 | 0 | 0 | 10.12 | 17.36 | 32.67 | 35.12 | 35.12 | 35.12 | 35.12 | 35.12 | 35.12 | 35.12 | 340000 | 4200 | 419 | Ireland | County Dublin | 1 | IE-D
339 | Tuam | 3.49 | 44.66 | 74.88 | 78.09 | 10.38 | 211.5 | 3.28 | 64.4817 | 2.5 | 3.27 | 3.86 | 4.15 | 4.69 | 5.39 | 6.42 | 7.29 | 9.2 | 16.09 | 0 | 0 | 30.67 | 60.49 | 92.55 | 131.76 | 151.93 | 160.81 | 160.81 | 180.26 | 180.26 | 201.18 | 211.5 | 3280000 | 28600 | 339 | Ireland | County Galway | 2 | IE-G
387 | Loughrea | 0.36 | 26.17 | 60.91 | 84.73 | 10.37 | 182.54 | 2.13 | 85.6995 | 2.24 | 3.19 | 3.9 | 4.26 | 4.67 | 5.32 | 5.93 | 6.68 | 7.49 | 11.44 | 0 | 0 | 18.56 | 53.29 | 80.97 | 125.44 | 147.71 | 156.31 | 170.46 | 170.46 | 182.54 | 182.54 | 182.54 | 2130000 | 17600 | 387 | Ireland | County Galway | 1 | IE-G
371 | Athenry | 0.16 | 25.64 | 37.71 | 32.8 | 10.53 | 106.84 | 1.56 | 68.4872 | 1.64 | 2.95 | 3.22 | 4.42 | 5.11 | 5.79 | 6.83 | 8.03 | 10.55 | 13.2 | 0 | 10.53 | 20.96 | 32.22 | 46.2 | 59.78 | 71.74 | 71.74 | 80.38 | 80.38 | 94.41 | 106.84 | 106.84 | 1560000 | 15200 | 371 | Ireland | County Galway | 2 | IE-G
377 | Ballinasloe | 0 | 24.34 | 35.67 | 43.59 | 0 | 103.6 | 1.5 | 69.0667 | 4.36 | 4.85 | 5.25 | 5.73 | 5.73 | 6.3 | 6.73 | 7.57 | 8.87 | 12.79 | 0 | 0 | 0 | 2.43 | 13.8 | 40.14 | 70.23 | 80.6 | 87.12 | 87.12 | 87.12 | 99.67 | 103.6 | 1500000 | 19600 | 377 | Ireland | County Galway | 2 | IE-G
373 | Oranmore | 0 | 14.08 | 40.56 | 22.72 | 0 | 77.37 | 1.11 | 69.7027 | 4.04 | 4.63 | 4.63 | 5.64 | 6.28 | 6.71 | 7.38 | 8.47 | 10.97 | 13.14 | 0 | 0 | 0 | 3.92 | 12.77 | 32.86 | 43.88 | 54.28 | 58.41 | 58.41 | 68.81 | 74.36 | 77.37 | 1110000 | 12200 | 373 | Ireland | County Galway | 2 | IE-G
408 | Gort | 0 | 10.36 | 39.83 | 13.46 | 0 | 63.65 | 0.93 | 68.4409 | 4.25 | 5.34 | 5.77 | 6.5 | 6.97 | 7.39 | 8.09 | 9.46 | 11.05 | 13.64 | 0 | 0 | 0 | 0 | 2.25 | 13.11 | 29.62 | 38.97 | 46.93 | 50.48 | 56.23 | 61.74 | 63.65 | 930000 | 12000 | 408 | Ireland | County Galway | 2 | IE-G
370 | Oranmore | 0.28 | 4.18 | 20.68 | 70.25 | 42.74 | 138.12 | 0.88 | 156.9545 | 1.1 | 1.38 | 1.61 | 1.88 | 2.21 | 2.42 | 2.71 | 3.11 | 3.56 | 5.47 | 0 | 45.62 | 100.77 | 129.17 | 135.94 | 138.12 | 138.12 | 138.12 | 138.12 | 138.12 | 138.12 | 138.12 | 138.12 | 880000 | 7800 | 370 | Ireland | County Galway | 1 | IE-G
378 | Ballinasloe | 0.75 | 13.28 | 16.85 | 0 | 0 | 30.89 | 0.72 | 42.9028 | 8.5 | 9.23 | 10.49 | 11.16 | 13.41 | 13.41 | 17.02 | 17.02 | 17.02 | 27.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.14 | 6.32 | 9.47 | 14.13 | 20.51 | 720000 | 8400 | 378 | Ireland | County Galway | 3 | IE-G
425 | Portumna | 0 | 10.35 | 16.82 | 1.21 | 0 | 28.38 | 0.6 | 47.3 | 7.5 | 8.12 | 8.82 | 9.85 | 10.53 | 12.1 | 12.1 | 15.11 | 15.11 | 19.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.21 | 6.5 | 11.25 | 12.95 | 16.39 | 26.3 | 600000 | 8600 | 425 | Ireland | County Galway | 3 | IE-G
312 | Clifden | 0 | 13.72 | 5.05 | 11.9 | 0 | 30.66 | 0.59 | 51.9661 | 2.4 | 2.79 | 4.4 | 5.1 | 5.99 | 6.83 | 10.53 | 10.53 | 10.53 | 19.36 | 0 | 0 | 5.16 | 5.16 | 9.13 | 14.82 | 15.93 | 15.93 | 15.93 | 15.93 | 20 | 20 | 28.57 | 590000 | 9400 | 312 | Ireland | County Galway | 2 | IE-G
352 | Moycullen | 0 | 7.39 | 14.32 | 3.17 | 0 | 24.88 | 0.47 | 52.9362 | 4.75 | 5 | 6.8 | 9.52 | 9.52 | 9.52 | 12.76 | 12.76 | 15.24 | 19.63 | 0 | 0 | 0 | 0 | 3.17 | 3.17 | 5.3 | 5.3 | 8.3 | 9.84 | 9.84 | 15.91 | 24.25 | 470000 | 5200 | 352 | Ireland | County Galway | 2 | IE-G
357 | Claregalway | 0 | 4.95 | 13.33 | 2.74 | 0 | 21.03 | 0.38 | 55.3421 | 4.75 | 4.75 | 7.59 | 7.59 | 7.59 | 8.55 | 9.28 | 9.28 | 11.49 | 16.43 | 0 | 0 | 0 | 0 | 1.45 | 1.45 | 1.45 | 5.98 | 13.84 | 14.49 | 16.86 | 16.86 | 21.03 | 380000 | 6200 | 357 | Ireland | County Galway | 2 | IE-G
365 | Barna | 0 | 5.71 | 9.13 | 1.29 | 0 | 16.13 | 0.34 | 47.4412 | 5.75 | 5.75 | 7.18 | 7.18 | 7.18 | 8.36 | 9.89 | 11.62 | 11.62 | 17.02 | 0 | 0 | 0 | 0 | 0 | 1.29 | 3.94 | 4.69 | 8.76 | 10.42 | 11.76 | 11.76 | 14.53 | 340000 | 5000 | 365 | Ireland | County Galway | 3 | IE-G
344 | Headford | 0 | 8.3 | 4.32 | 1.61 | 0 | 14.23 | 0.32 | 44.4688 | 0 | 8.21 | 8.21 | 12.76 | 12.76 | 12.76 | 18.81 | 18.81 | 18.81 | 25.45 | 0 | 0 | 0 | 0 | 0 | 0 | 1.61 | 1.61 | 2.59 | 2.59 | 2.59 | 4.85 | 9.59 | 320000 | 5400 | 344 | Ireland | County Galway | 3 | IE-G
345 | Oughterard | 0 | 6.88 | 4.61 | 0 | 0 | 11.49 | 0.3 | 38.3 | 8.5 | 9.08 | 11.73 | 11.73 | 11.73 | 17.3 | 17.3 | 24.41 | 24.41 | 24.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 1.88 | 3.41 | 3.41 | 5.88 | 300000 | 7000 | 345 | Ireland | County Galway | 3 | IE-G
390 | Kinvara | 0 | 5.88 | 4.6 | 0 | 0 | 10.48 | 0.26 | 40.3077 | 13 | 13.94 | 13.94 | 16.23 | 16.23 | 19.88 | 19.88 | 25.14 | 25.14 | 25.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.53 | 6.03 | 260000 | 5000 | 390 | Ireland | County Galway | 3 | IE-G
485 | Meelick, County Galway | 0 | 5.54 | 4.75 | 0 | 0 | 10.29 | 0.24 | 42.875 | 0 | 9.5 | 9.5 | 11.77 | 16.36 | 16.36 | 16.36 | 25.31 | 25.31 | 25.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.95 | 3.32 | 3.32 | 5.08 | 240000 | 4600 | 485 | Ireland | County Galway | 3 | IE-G
526 | Tralee | 4.08 | 139 | 127.17 | 120.61 | 126.73 | 517.59 | 7.38 | 70.1341 | 1.6 | 1.94 | 2.24 | 2.48 | 3.25 | 3.88 | 5.16 | 6.25 | 8.15 | 15.08 | 0 | 63.1 | 232.04 | 293.54 | 344.88 | 374.14 | 396.09 | 396.09 | 440.8 | 440.8 | 493.17 | 516.98 | 517.59 | 7380000 | 66200 | 526 | Ireland | County Kerry | 2 | IE-KY
558 | Killarney | 1 | 85.32 | 80.06 | 124.45 | 6.89 | 297.73 | 4.36 | 68.2867 | 2.33 | 2.82 | 3.05 | 3.64 | 4.3 | 4.96 | 6.05 | 6.89 | 9.49 | 16.97 | 0 | 0 | 58.32 | 131.67 | 167.43 | 186.03 | 209.74 | 209.74 | 209.74 | 244.87 | 244.87 | 280.7 | 297.73 | 4360000 | 44600 | 558 | Ireland | County Kerry | 2 | IE-KY
510 | Listowel | 0.71 | 35.1 | 20.85 | 16.26 | 3.06 | 75.99 | 1.56 | 48.7115 | 2.57 | 3.3 | 4.45 | 5.22 | 7.19 | 8.05 | 8.05 | 12.45 | 12.45 | 23.78 | 0 | 0 | 5.42 | 19.32 | 22.36 | 26.42 | 34.31 | 36.51 | 39.67 | 39.67 | 39.67 | 53.57 | 68.73 | 1560000 | 17400 | 510 | Ireland | County Kerry | 3 | IE-KY
576 | Kenmare | 0 | 17.97 | 7.97 | 0 | 0 | 25.94 | 0.75 | 34.5867 | 9.5 | 12.11 | 14.19 | 17.44 | 17.44 | 17.44 | 17.44 | 29.5 | 29.5 | 29.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.89 | 2.7 | 6.44 | 9.21 | 750000 | 14000 | 576 | Ireland | County Kerry | 3 | IE-KY
547 | Killorglin | 0.13 | 17.84 | 7.84 | 4.3 | 0 | 30.1 | 0.68 | 44.2647 | 0 | 6.79 | 7.82 | 9.12 | 10.13 | 12.78 | 12.78 | 12.78 | 22.65 | 22.65 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 8.06 | 11.28 | 11.71 | 13.22 | 16.09 | 16.09 | 680000 | 11200 | 547 | Ireland | County Kerry | 3 | IE-KY
532 | Dingle | 0 | 11.1 | 12.76 | 23.38 | 0 | 47.24 | 0.65 | 72.6769 | 2.8 | 3.1 | 3.35 | 3.92 | 4.46 | 5.05 | 5.82 | 6.56 | 8.08 | 12.18 | 0 | 0 | 2.65 | 18.03 | 24.53 | 33.42 | 35.63 | 35.63 | 38.85 | 38.85 | 38.85 | 44.56 | 47.24 | 650000 | 11800 | 532 | Ireland | County Kerry | 2 | IE-KY
539 | Castleisland | 0 | 11.75 | 11.4 | 15.07 | 0 | 38.23 | 0.63 | 60.6825 | 0 | 3.75 | 3.75 | 4.22 | 4.78 | 6.01 | 7.29 | 7.66 | 9.39 | 14.27 | 0 | 0 | 0 | 4.16 | 17.74 | 19.26 | 22.88 | 27.61 | 27.61 | 30.68 | 30.68 | 36.5 | 38.23 | 630000.01 | 10600 | 539 | Ireland | County Kerry | 2 | IE-KY
561 | Cahersiveen | 0 | 6.89 | 5.75 | 3.05 | 0 | 15.68 | 0.34 | 46.1176 | 0 | 6.53 | 7.49 | 8.57 | 9.12 | 11.03 | 14.1 | 14.1 | 14.1 | 20.68 | 0 | 0 | 0 | 0 | 0 | 1.7 | 3.04 | 5.2 | 5.91 | 6.47 | 8.24 | 10.56 | 10.56 | 340000 | 4600 | 561 | Ireland | County Kerry | 3 | IE-KY
490 | Ballybunion | 0 | 7.67 | 3.29 | 0 | 0 | 10.97 | 0.32 | 34.2812 | 8.5 | 9.37 | 9.37 | 9.37 | 19.92 | 19.92 | 19.92 | 19.92 | 29.64 | 29.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.05 | 1.61 | 1.61 | 1.61 | 4.96 | 320000 | 7800 | 490 | Ireland | County Kerry | 3 | IE-KY
508 | Ballyheigue | 0 | 6.5 | 2.88 | 1.25 | 0 | 10.63 | 0.28 | 37.9643 | 0 | 11.44 | 11.44 | 18.87 | 18.87 | 18.87 | 18.87 | 29.35 | 29.35 | 29.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.25 | 1.25 | 1.81 | 1.81 | 4 | 280000 | 5600 | 508 | Ireland | County Kerry | 3 | IE-KY
545 | Milltown | 0 | 7.87 | 2.27 | 0 | 0 | 10.14 | 0.27 | 37.5556 | 11 | 11 | 16.45 | 16.45 | 20.09 | 20.09 | 20.09 | 29.44 | 29.44 | 29.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.53 | 0.53 | 2.39 | 269999.99 | 6400 | 545 | Ireland | County Kerry | 3 | IE-KY
447 | Newbridge | 0.9 | 73.55 | 186.3 | 69 | 458.11 | 787.86 | 5.94 | 132.6364 | 0.73 | 0.89 | 1.05 | 1.05 | 1.25 | 1.53 | 1.89 | 2.76 | 3.63 | 7.12 | 121.35 | 527.72 | 626.76 | 718.22 | 747.01 | 774.74 | 774.74 | 787.87 | 787.87 | 787.87 | 787.87 | 787.87 | 787.87 | 5939999.99 | 42000 | 447 | Ireland | County Kildare | 1 | IE-KE
439 | Naas | 1.71 | 73.31 | 167.14 | 119.5 | 122.84 | 484.51 | 5.52 | 87.7736 | 0.84 | 1.36 | 2.05 | 2.54 | 3.07 | 3.49 | 4.19 | 5.25 | 6.07 | 11.73 | 44.83 | 109.5 | 226.88 | 296.72 | 345.66 | 388.92 | 409.92 | 441.6 | 441.6 | 466.68 | 484.5 | 484.5 | 484.5 | 5520000.01 | 48400 | 439 | Ireland | County Kildare | 1 | IE-KE
423 | Celbridge | 0.69 | 44.68 | 167.15 | 47.29 | 16.37 | 276.18 | 3.78 | 73.0635 | 2.59 | 3.71 | 4.03 | 4.47 | 5.08 | 5.59 | 6.02 | 6.65 | 7.37 | 12.59 | 0 | 9.59 | 21.64 | 51.23 | 87.03 | 157.3 | 230 | 238.94 | 249.65 | 249.65 | 265.79 | 276.18 | 276.18 | 3780000.02 | 25800 | 423 | Ireland | County Kildare | 2 | IE-KE
476 | Athy | 0.43 | 21.82 | 66.89 | 226.04 | 185.38 | 500.56 | 3.17 | 157.9054 | 1.6 | 1.83 | 2.05 | 2.24 | 2.58 | 2.83 | 3.17 | 3.54 | 3.95 | 6.13 | 0 | 81.39 | 290.95 | 435.31 | 478.11 | 497.15 | 500.56 | 500.56 | 500.56 | 500.56 | 500.56 | 500.56 | 500.56 | 3170000 | 27600 | 476 | Ireland | County Kildare | 1 | IE-KE
412 | Maynooth | 1.1 | 43.52 | 91.94 | 46.18 | 41.3 | 224.04 | 2.94 | 76.2041 | 1.48 | 2 | 2.59 | 3.23 | 3.88 | 4.57 | 5.41 | 6.03 | 7.75 | 12.63 | 0 | 40.53 | 71.68 | 101.11 | 135.81 | 153.17 | 189.15 | 199.38 | 199.38 | 199.38 | 215.01 | 224.04 | 224.04 | 2940000 | 26400 | 412 | Ireland | County Kildare | 1 | IE-KE
450 | Kildare | 1.26 | 22.4 | 59.45 | 129.29 | 32.62 | 245.02 | 2.3 | 106.5304 | 1.1 | 2.11 | 2.63 | 3.08 | 3.39 | 3.63 | 3.92 | 4.34 | 5.14 | 9.44 | 0 | 27.98 | 65.68 | 148.15 | 210.69 | 221.02 | 228.57 | 238.76 | 238.76 | 245.02 | 245.02 | 245.02 | 245.02 | 2300000 | 17200 | 450 | Ireland | County Kildare | 1 | IE-KE
429 | Clane | 0.33 | 31.65 | 56.52 | 21.06 | 17.13 | 126.69 | 1.88 | 67.3883 | 1.6 | 2.02 | 2.86 | 3.37 | 4.72 | 5.57 | 6.68 | 7.49 | 9.22 | 16.19 | 0 | 17.13 | 35.59 | 43.21 | 60.84 | 73.97 | 87.99 | 94.81 | 94.81 | 105.18 | 105.18 | 120.03 | 126.69 | 1879999.98 | 17600 | 429 | Ireland | County Kildare | 2 | IE-KE
449 | Monasterevin | 0.19 | 24.45 | 30.19 | 19.57 | 6.94 | 81.34 | 1.34 | 60.7015 | 2.4 | 3.34 | 4.07 | 5.14 | 6.01 | 6.75 | 7.51 | 10.94 | 10.94 | 14.35 | 0 | 0 | 9.29 | 18.13 | 25.08 | 35.18 | 47.21 | 52.15 | 52.15 | 52.15 | 64.85 | 73.47 | 73.47 | 1340000 | 16600 | 449 | Ireland | County Kildare | 2 | IE-KE
404 | Kilcock | 0 | 14.36 | 50.91 | 18.59 | 11 | 94.86 | 1.21 | 78.3967 | 2.21 | 2.66 | 3.22 | 3.72 | 4.14 | 4.72 | 5.19 | 6.25 | 6.98 | 10.51 | 0 | 0 | 15.95 | 36.15 | 51.54 | 66.6 | 79.51 | 79.51 | 88.16 | 88.16 | 94.86 | 94.86 | 94.86 | 1210000 | 9600 | 404 | Ireland | County Kildare | 1 | IE-KE
435 | Sallins | 0.33 | 17.35 | 48.61 | 4.39 | 0 | 70.69 | 1.21 | 58.4215 | 4.72 | 5.48 | 5.48 | 6.52 | 7.06 | 7.51 | 8.22 | 9.26 | 10.98 | 18.55 | 0 | 0 | 0 | 0 | 6.41 | 11.18 | 23.12 | 44.02 | 46.4 | 51.94 | 58.28 | 64.75 | 70.69 | 1210000.01 | 12000 | 435 | Ireland | County Kildare | 2 | IE-KE
458 | Kilcullen | 0 | 19.66 | 23.78 | 4.15 | 3.58 | 51.17 | 0.92 | 55.6196 | 2 | 3.72 | 4.67 | 5.74 | 7.1 | 8.41 | 8.41 | 12.89 | 12.89 | 22 | 0 | 0 | 6.29 | 11.2 | 16.32 | 19.57 | 22.68 | 26.31 | 28.93 | 28.93 | 28.93 | 39.65 | 46.16 | 920000 | 15000 | 458 | Ireland | County Kildare | 2 | IE-KE
433 | Rathangan | 0 | 16.28 | 20.88 | 13.45 | 0 | 50.61 | 0.87 | 58.1724 | 4.25 | 4.71 | 5.25 | 6.57 | 7.55 | 8.7 | 9.76 | 11.73 | 11.73 | 17.23 | 0 | 0 | 0 | 0 | 7.31 | 15.25 | 18.68 | 23.98 | 29.37 | 33.13 | 38.05 | 38.05 | 47.24 | 870000.01 | 15200 | 433 | Ireland | County Kildare | 2 | IE-KE
440 | Kill, County Kildare | 0 | 15.93 | 28.65 | 1.98 | 0 | 46.55 | 0.84 | 55.4167 | 4.43 | 5.29 | 6.85 | 6.85 | 8.19 | 9.32 | 9.32 | 13.17 | 13.17 | 18.45 | 0 | 0 | 0 | 0 | 3.1 | 5.29 | 13.26 | 19.09 | 25.15 | 26.97 | 26.97 | 35.74 | 44.49 | 840000.01 | 10000 | 440 | Ireland | County Kildare | 2 | IE-KE
428 | Prosperous | 0.22 | 12.56 | 18.94 | 6.3 | 0 | 38.02 | 0.68 | 55.9118 | 4.25 | 5.11 | 5.66 | 6.36 | 6.98 | 8.19 | 8.19 | 11.52 | 11.52 | 20.64 | 0 | 0 | 0 | 0 | 4.44 | 11.09 | 18.37 | 22.09 | 22.8 | 22.8 | 28.44 | 28.44 | 35.57 | 680000.01 | 7600 | 428 | Ireland | County Kildare | 2 | IE-KE
443 | Ladytown Crossroads | 0.07 | 0.43 | 9.86 | 46.85 | 120.25 | 177.46 | 0.59 | 300.7797 | 0.7 | 0.78 | 1 | 1.15 | 1.15 | 1.51 | 1.63 | 2.02 | 2.31 | 3 | 48.51 | 131.8 | 177.39 | 177.46 | 177.46 | 177.46 | 177.46 | 177.46 | 177.46 | 177.46 | 177.46 | 177.46 | 177.46 | 590000 | 7600 | 443 | Ireland | County Kildare | 1 | IE-KE
411 | Derrinturn | 0 | 10.24 | 12.42 | 0 | 0 | 22.67 | 0.48 | 47.2292 | 7.95 | 8.38 | 10.79 | 10.79 | 12.87 | 16.35 | 16.35 | 16.35 | 24.21 | 29.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.71 | 2.38 | 5.32 | 6.78 | 9.53 | 13.36 | 480000 | 7800 | 411 | Ireland | County Kildare | 3 | IE-KE
487 | Newbridge | 0.02 | 0 | 17.56 | 42.03 | 0 | 59.62 | 0.48 | 124.2083 | 3.25 | 3.65 | 3.65 | 3.9 | 4.17 | 4.17 | 4.44 | 4.62 | 4.9 | 5.42 | 0 | 0 | 0 | 19.22 | 50.91 | 59.62 | 59.62 | 59.62 | 59.62 | 59.62 | 59.62 | 59.62 | 59.62 | 480000.01 | 8600 | 487 | Ireland | County Kildare | 1 | IE-KE
501 | Castledermot | 0 | 10.24 | 7.53 | 0 | 0 | 17.76 | 0.42 | 42.2857 | 7.5 | 8.92 | 10.42 | 12.21 | 12.21 | 15.81 | 15.81 | 15.81 | 24.46 | 33.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83 | 2.86 | 4.56 | 5.05 | 6.61 | 9.2 | 420000 | 9000 | 501 | Ireland | County Kildare | 3 | IE-KE
432 | Kilmeage | 0 | 8.92 | 8.65 | 0 | 0 | 17.57 | 0.41 | 42.8537 | 8.97 | 10.48 | 12.09 | 13.89 | 13.89 | 13.89 | 19.14 | 19.14 | 22.99 | 22.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.48 | 2.13 | 2.87 | 6.42 | 12.17 | 410000 | 7400 | 432 | Ireland | County Kildare | 3 | IE-KE
452 | Athgarvan | 0 | 5.78 | 5.24 | 0 | 0 | 11.02 | 0.27 | 40.8148 | 0 | 0 | 0 | 11 | 11.47 | 14.02 | 14.02 | 22.43 | 22.43 | 22.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.66 | 5.74 | 5.74 | 270000.01 | 5400 | 452 | Ireland | County Kildare | 3 | IE-KE
426 | Allenwood | 0 | 4.76 | 6.72 | 0 | 0 | 11.48 | 0.26 | 44.1538 | 9.5 | 10.46 | 11.13 | 12.46 | 12.46 | 14.23 | 16.7 | 16.7 | 21.16 | 21.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73 | 2.75 | 6.17 | 8 | 260000.01 | 5600 | 426 | Ireland | County Kildare | 3 | IE-KE
437 | Caragh | 0 | 4.98 | 8.15 | 0 | 0 | 13.13 | 0.26 | 50.5 | 7.5 | 7.5 | 8.22 | 8.61 | 8.61 | 10.34 | 10.34 | 12.84 | 17.87 | 17.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 4.63 | 7.02 | 7.86 | 9.48 | 11.63 | 260000 | 4000 | 437 | Ireland | County Kildare | 2 | IE-KE
427 | Straffan | 0 | 5.59 | 5.28 | 0 | 0 | 10.87 | 0.25 | 43.48 | 0 | 18 | 18 | 18 | 18 | 23 | 23 | 27.73 | 27.73 | 27.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.62 | 250000 | 5400 | 427 | Ireland | County Kildare | 3 | IE-KE
396 | Johnstownbridge | 0 | 2.88 | 7.27 | 0 | 0 | 10.15 | 0.22 | 46.1364 | 9.5 | 10.43 | 11.01 | 11.01 | 18.01 | 18.01 | 18.01 | 18.01 | 27.81 | 27.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69 | 2.36 | 2.36 | 4.71 | 220000 | 4600 | 396 | Ireland | County Kildare | 3 | IE-KE
403 | Moyglare | 0 | 0.41 | 2.32 | 1.3 | 18.46 | 22.48 | 0.07 | 321.1429 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 1.49 | 2.32 | 18.46 | 20.92 | 21.57 | 22.48 | 22.48 | 22.48 | 22.48 | 22.48 | 22.48 | 22.48 | 22.48 | 22.48 | 22.48 | 70000 | 1200 | 403 | Ireland | County Kildare | 1 | IE-KE
420 | Bond Bridge | 0 | 2.2 | 0 | 3.85 | 11.27 | 17.32 | 0.11 | 157.4545 | 0 | 0 | 0 | 0 | 1.3 | 1.3 | 1.82 | 2.44 | 3.02 | 7.34 | 0 | 11.27 | 13.38 | 15.12 | 15.12 | 15.12 | 15.12 | 17.11 | 17.32 | 17.32 | 17.32 | 17.32 | 17.32 | 110000 | 1400 | 420 | Ireland | County Kildare | 1 | IE-KE
455 | Lumville Cross | 0 | 1.99 | 14.08 | 20.29 | 7.23 | 43.59 | 0.35 | 124.5429 | 0 | 2.8 | 3.19 | 3.67 | 4.25 | 4.42 | 4.75 | 5.41 | 5.99 | 7.07 | 0 | 0 | 7.23 | 14.29 | 26.31 | 37.23 | 41.6 | 43.59 | 43.59 | 43.59 | 43.59 | 43.59 | 43.59 | 350000 | 6800 | 455 | Ireland | County Kildare | 1 | IE-KE
445 | Rathmore | 0 | 0 | 1.11 | 1.92 | 8.91 | 11.94 | 0.04 | 298.5 | 0 | 0 | 0 | 0 | 2 | 2 | 2 | 2.34 | 2.34 | 2.86 | 0 | 0 | 10.83 | 11.94 | 11.94 | 11.94 | 11.94 | 11.94 | 11.94 | 11.94 | 11.94 | 11.94 | 11.94 | 40000 | 800 | 445 | Ireland | County Kildare | 1 | IE-KE
527 | Kilkenny | 2.1 | 57.97 | 249.52 | 669.98 | 248.85 | 1228.42 | 9.19 | 133.6692 | 1.51 | 1.7 | 2.09 | 2.36 | 2.62 | 3.11 | 3.42 | 3.77 | 4.26 | 6.4 | 0 | 268.65 | 627.09 | 941.37 | 1171.76 | 1221.62 | 1228.42 | 1228.42 | 1228.42 | 1228.42 | 1228.42 | 1228.42 | 1228.42 | 9190000 | 46400 | 527 | Ireland | County Kilkenny | 1 | IE-KK
540 | Callan, County Kilkenny | 0 | 16.91 | 24.29 | 0 | 0 | 41.2 | 0.82 | 50.2439 | 6.93 | 7.9 | 8.68 | 8.68 | 9.56 | 11.06 | 11.06 | 14.7 | 14.7 | 18.56 | 0 | 0 | 0 | 0 | 0 | 0 | 2.09 | 5.44 | 10.62 | 17.1 | 24.2 | 32.78 | 38.66 | 820000 | 11600 | 540 | Ireland | County Kilkenny | 2 | IE-KK
546 | Thomastown | 0 | 16.66 | 15.42 | 0 | 0 | 32.08 | 0.73 | 43.9452 | 7.02 | 7.9 | 10.31 | 12.25 | 12.25 | 12.25 | 17.79 | 17.79 | 23.34 | 23.34 | 0 | 0 | 0 | 0 | 0 | 0 | 1.07 | 4.38 | 4.38 | 7.67 | 9.11 | 12.17 | 21.52 | 730000 | 11200 | 546 | Ireland | County Kilkenny | 3 | IE-KK
548 | Graiguenamanagh | 0 | 10.75 | 9.34 | 0 | 0 | 20.09 | 0.48 | 41.8542 | 6.5 | 9.17 | 10.34 | 11.23 | 12.72 | 16.15 | 16.15 | 16.15 | 24.88 | 24.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98 | 0.98 | 2.35 | 3.52 | 6.27 | 8.05 | 11.16 | 480000 | 8000 | 548 | Ireland | County Kilkenny | 3 | IE-KK
512 | Castlecomer | 0 | 7.29 | 15.06 | 1.49 | 0 | 23.84 | 0.44 | 54.1818 | 5.25 | 7.09 | 7.09 | 7.09 | 9.01 | 10.37 | 10.37 | 10.37 | 15.14 | 17.52 | 0 | 0 | 0 | 0 | 0 | 1.49 | 1.49 | 3.44 | 9.7 | 12.21 | 13.81 | 13.81 | 22.66 | 440000 | 6200 | 512 | Ireland | County Kilkenny | 2 | IE-KK
441 | Johnstown | 0 | 6.11 | 6.39 | 6.49 | 0 | 18.99 | 0.32 | 59.3437 | 3.75 | 4.83 | 5.24 | 5.79 | 6.94 | 7.87 | 7.87 | 12.16 | 12.16 | 16.96 | 0 | 0 | 0 | 1.71 | 3.7 | 6.5 | 9.47 | 11 | 11 | 11 | 11 | 14.67 | 17.73 | 320000 | 4800 | 441 | Ireland | County Kilkenny | 2 | IE-KK
517 | Urlingford | 0 | 3.79 | 14.02 | 5.52 | 0 | 23.33 | 0.32 | 72.9062 | 5.25 | 6.05 | 6.3 | 7.27 | 7.27 | 7.27 | 8.13 | 8.66 | 8.81 | 12.8 | 0 | 0 | 0 | 0 | 0 | 1.54 | 5.15 | 9.19 | 19.03 | 19.03 | 21.29 | 23.33 | 23.33 | 320000 | 5000 | 517 | Ireland | County Kilkenny | 2 | IE-KK
139 | Stoneyford | 0 | 4.88 | 0 | 9.52 | 40.42 | 54.83 | 0.29 | 189.069 | 0 | 0 | 0.7 | 0.86 | 1.06 | 1.06 | 1.4 | 1.88 | 2.18 | 4.94 | 20.81 | 42.59 | 49.95 | 51.54 | 53.93 | 53.93 | 54.83 | 54.83 | 54.83 | 54.83 | 54.83 | 54.83 | 54.83 | 290000 | 5000 | 139 | Ireland | County Kilkenny | 1 | IE-KK
511 | Ballyragget | 0 | 4.52 | 10.07 | 0 | 0 | 14.59 | 0.29 | 50.3103 | 0 | 9.5 | 9.5 | 10.54 | 11.37 | 11.37 | 13 | 13 | 15.77 | 18.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.66 | 7.13 | 9.47 | 13.93 | 290000 | 3600 | 511 | Ireland | County Kilkenny | 2 | IE-KK
536 | Gowran | 0 | 4.58 | 6.76 | 0 | 0 | 11.34 | 0.22 | 51.5455 | 0 | 9.97 | 10.62 | 10.62 | 12.64 | 13.86 | 13.86 | 13.86 | 17.64 | 21.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.97 | 2.51 | 6.03 | 9.13 | 220000 | 3400 | 536 | Ireland | County Kilkenny | 2 | IE-KK
574 | Mooncoin | 0 | 3.44 | 7.03 | 0 | 0 | 10.47 | 0.18 | 58.1667 | 0 | 4.98 | 5.25 | 5.51 | 5.99 | 6.43 | 7.2 | 8.55 | 9.74 | 14.65 | 0 | 0 | 0 | 0 | 2.03 | 4.67 | 5.34 | 6.43 | 7.78 | 8.38 | 8.38 | 10 | 10.47 | 180000 | 4000 | 574 | Ireland | County Kilkenny | 2 | IE-KK
506 | Clontubrid | 0 | 0.99 | 0.81 | 1.48 | 7.01 | 10.29 | 0.07 | 147 | 0 | 0 | 0 | 2 | 2 | 2 | 2.19 | 2.19 | 2.94 | 5.01 | 0 | 0 | 8.49 | 9.3 | 9.3 | 10.29 | 10.29 | 10.29 | 10.29 | 10.29 | 10.29 | 10.29 | 10.29 | 70000 | 1600 | 506 | Ireland | County Kilkenny | 1 | IE-KK
604 | Courtstown | 0 | 0.42 | 2.48 | 5.54 | 7.58 | 16.02 | 0.09 | 178 | 0 | 0 | 2 | 2 | 2.19 | 2.19 | 2.64 | 3.08 | 3.83 | 4.57 | 0 | 0 | 9.72 | 14 | 15.6 | 16.02 | 16.02 | 16.02 | 16.02 | 16.02 | 16.02 | 16.02 | 16.02 | 90000 | 2200 | 604 | Ireland | County Kilkenny | 1 | IE-KK
461 | Portlaoise | 2.92 | 49.28 | 110.19 | 402.47 | 124.87 | 689.73 | 5.65 | 122.0761 | 1.54 | 1.85 | 2.26 | 2.5 | 2.5 | 2.8 | 3.24 | 3.56 | 4.2 | 7.47 | 0 | 95.44 | 350.49 | 590.85 | 637.74 | 659.54 | 680.31 | 689.73 | 689.73 | 689.73 | 689.73 | 689.73 | 689.73 | 5650000 | 44000 | 461 | Ireland | County Laois | 1 | IE-LS
481 | Abbeyleix | 0 | 11.46 | 8.19 | 3.34 | 0 | 22.99 | 0.51 | 45.0784 | 4.75 | 5.79 | 7.78 | 9.01 | 10.78 | 14.33 | 14.33 | 14.33 | 22.61 | 22.61 | 0 | 0 | 0 | 0 | 2.08 | 3.33 | 3.33 | 6.57 | 6.57 | 7.92 | 9.86 | 13.14 | 13.14 | 510000 | 9000 | 481 | Ireland | County Laois | 3 | IE-LS
442 | Mountmellick | 0 | 5.4 | 8.28 | 39.47 | 0 | 53.15 | 0.49 | 108.4694 | 2.8 | 2.8 | 3.06 | 3.38 | 3.55 | 3.55 | 3.55 | 4.2 | 4.95 | 7.21 | 0 | 0 | 4.74 | 39.13 | 47.08 | 50.3 | 50.3 | 52.18 | 53.15 | 53.15 | 53.15 | 53.15 | 53.15 | 490000 | 7400 | 442 | Ireland | County Laois | 1 | IE-LS
489 | Rathdowney | 0 | 7.07 | 13.76 | 6.76 | 3.82 | 31.4 | 0.44 | 71.3636 | 0 | 2.94 | 3.62 | 4.42 | 5.35 | 6.64 | 7.55 | 7.84 | 11.39 | 13.71 | 0 | 0 | 5.79 | 7.64 | 10.58 | 13.72 | 18.7 | 22.23 | 22.23 | 22.23 | 28.03 | 30.5 | 31.4 | 440000 | 6200 | 489 | Ireland | County Laois | 2 | IE-LS
469 | Stradbally | 0 | 8.67 | 6.88 | 0 | 0 | 15.56 | 0.38 | 40.9474 | 8.93 | 9.91 | 10.82 | 16.63 | 16.63 | 16.63 | 16.63 | 16.63 | 28.42 | 28.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.36 | 2.58 | 3.66 | 3.66 | 6.2 | 380000 | 7000 | 469 | Ireland | County Laois | 3 | IE-LS
486 | Ballylinan | 0 | 7.15 | 10.23 | 0 | 0 | 17.38 | 0.37 | 46.973 | 8.38 | 8.38 | 10.5 | 10.5 | 10.5 | 13.66 | 13.66 | 17.66 | 17.66 | 21.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88 | 1.57 | 1.57 | 5.02 | 8.69 | 13.43 | 370000 | 4800 | 486 | Ireland | County Laois | 3 | IE-LS
498 | Durrow | 0 | 7.14 | 8.8 | 0 | 0 | 15.93 | 0.33 | 48.2727 | 8.5 | 8.5 | 9.67 | 9.67 | 11.21 | 12.97 | 12.97 | 16.01 | 16.01 | 21.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.02 | 4.54 | 6.38 | 8.62 | 11.53 | 330000 | 5600 | 498 | Ireland | County Laois | 3 | IE-LS
464 | Mountrath | 0 | 2.88 | 3.83 | 3.51 | 0 | 10.22 | 0.16 | 63.875 | 0 | 4.25 | 4.25 | 4.49 | 4.79 | 5.69 | 6.08 | 6.46 | 10.06 | 10.06 | 0 | 0 | 0 | 0 | 4.61 | 6.08 | 7.34 | 8.26 | 8.26 | 8.26 | 8.99 | 8.99 | 10.22 | 160000 | 3600 | 464 | Ireland | County Laois | 2 | IE-LS
275 | Carrick-on-Shannon | 0 | 22.4 | 60.6 | 104.12 | 24.93 | 212.05 | 1.99 | 106.5578 | 2.09 | 2.44 | 2.8 | 3.14 | 3.6 | 3.93 | 4.4 | 4.81 | 5.9 | 8.51 | 0 | 0 | 69.29 | 121.48 | 155.36 | 187.04 | 192.87 | 201.89 | 212.05 | 212.05 | 212.05 | 212.05 | 212.05 | 1990000 | 21400 | 275 | Ireland | County Leitrim | 1 | IE-LM
155 | Manorhamilton | 0 | 7.59 | 10.3 | 5.16 | 0 | 23.05 | 0.42 | 54.881 | 4.75 | 5.17 | 6.07 | 6.84 | 8.15 | 8.79 | 10.45 | 10.45 | 13.58 | 15.07 | 0 | 0 | 0 | 0 | 2.23 | 3.87 | 8.13 | 10.78 | 12.6 | 12.6 | 15.37 | 19.57 | 20.75 | 420000 | 9200 | 155 | Ireland | County Leitrim | 2 | IE-LM
98 | Kinlough | 0 | 8.65 | 7.09 | 3.09 | 0 | 18.83 | 0.39 | 48.2821 | 5.25 | 5.81 | 6.53 | 6.53 | 8.44 | 8.44 | 12.67 | 12.67 | 19.06 | 19.06 | 0 | 0 | 0 | 0 | 0 | 3.09 | 5.42 | 8.5 | 9.14 | 9.14 | 9.14 | 12.27 | 16.01 | 390000 | 9200 | 98 | Ireland | County Leitrim | 3 | IE-LM
179 | Dromahair | 0 | 8.76 | 4.03 | 0 | 0 | 12.79 | 0.32 | 39.9688 | 9.5 | 11.55 | 12.77 | 12.77 | 12.77 | 12.77 | 20.24 | 20.24 | 20.24 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85 | 2.42 | 2.99 | 2.99 | 320000 | 4200 | 179 | Ireland | County Leitrim | 3 | IE-LM
262 | Ballinamore | 0 | 7.66 | 5.08 | 0 | 0 | 12.74 | 0.3 | 42.4667 | 8.5 | 9.15 | 10.74 | 11.9 | 11.9 | 11.9 | 17.63 | 17.63 | 24.13 | 24.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75 | 2.69 | 4.39 | 4.39 | 7.8 | 300000 | 5400 | 262 | Ireland | County Leitrim | 3 | IE-LM
307 | Dromod | 0 | 5.35 | 6.41 | 0 | 0 | 11.76 | 0.27 | 43.5556 | 8.5 | 8.5 | 9.53 | 9.53 | 10.77 | 11.95 | 13.89 | 13.89 | 13.89 | 21.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97 | 3.36 | 6.84 | 8.03 | 8.03 | 270000 | 5800 | 307 | Ireland | County Leitrim | 3 | IE-LM
294 | Mohill | 0 | 5.37 | 2.54 | 8.26 | 0 | 16.17 | 0.26 | 62.1923 | 0 | 4.75 | 4.75 | 5.08 | 5.36 | 5.7 | 7.18 | 8.9 | 8.9 | 14.24 | 0 | 0 | 0 | 0 | 1.87 | 8.26 | 10.8 | 11.28 | 12.48 | 12.48 | 12.48 | 15.08 | 16.17 | 260000 | 5200 | 294 | Ireland | County Leitrim | 2 | IE-LM
496 | Cappavilla | 5.2 | 58.9 | 153.95 | 33.78 | 17.42 | 269.25 | 5.03 | 53.5288 | 1.97 | 3.38 | 4.18 | 5.53 | 6.31 | 7.08 | 7.97 | 9.03 | 11.01 | 19.29 | 0 | 22.96 | 39.51 | 51.21 | 87.43 | 106.48 | 132.45 | 182.45 | 182.45 | 203.97 | 232.74 | 255.52 | 269.25 | 5030000 | 33000 | 496 | Ireland | County Limerick | 2 | IE-LK
519 | Newcastle West | 0.7 | 24.79 | 56.96 | 64.03 | 0 | 146.47 | 2 | 73.235 | 3.08 | 3.52 | 3.96 | 4.33 | 4.95 | 5.47 | 5.98 | 6.81 | 8.99 | 13.71 | 0 | 0 | 2.64 | 37.21 | 71.58 | 97.75 | 113.22 | 120.33 | 131.73 | 131.73 | 139.97 | 146.47 | 146.47 | 1999999.99 | 21400 | 519 | Ireland | County Limerick | 2 | IE-LK
538 | Charleville | 0 | 19.29 | 43.8 | 20.17 | 9.43 | 92.68 | 1.3 | 71.2923 | 0 | 2.96 | 3.96 | 3.96 | 5.4 | 6.1 | 6.51 | 7.59 | 9.7 | 12.22 | 9.43 | 9.43 | 17.55 | 24.54 | 24.54 | 41.23 | 65.13 | 71.17 | 71.17 | 80.98 | 80.98 | 88.34 | 92.68 | 1300000 | 19400 | 538 | Ireland | County Limerick | 2 | IE-LK
522 | Abbeyfeale | 0.32 | 16.08 | 12.37 | 5.27 | 0 | 34.05 | 0.78 | 43.6538 | 5.75 | 6.56 | 7.3 | 7.75 | 9.64 | 9.64 | 13.24 | 13.24 | 20.53 | 20.53 | 0 | 0 | 0 | 0 | 0 | 1.22 | 5.27 | 10.71 | 14.79 | 16.77 | 16.77 | 21.91 | 21.91 | 780000 | 13200 | 522 | Ireland | County Limerick | 3 | IE-LK
488 | Castleconnell | 0 | 13.04 | 18 | 0 | 0 | 31.04 | 0.69 | 44.9855 | 7.5 | 9.81 | 9.81 | 13.96 | 13.96 | 13.96 | 18.52 | 18.52 | 23.65 | 23.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.84 | 0.84 | 5.92 | 5.92 | 12.02 | 20.47 | 690000 | 10400 | 488 | Ireland | County Limerick | 3 | IE-LK
535 | Kilmallock | 0 | 14.09 | 10.43 | 0 | 0 | 24.51 | 0.59 | 41.5424 | 9.5 | 10.39 | 11.84 | 13.52 | 13.52 | 13.52 | 18 | 18 | 18 | 24.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.66 | 7.02 | 9.65 | 15.83 | 590000 | 9600 | 535 | Ireland | County Limerick | 3 | IE-LK
514 | Rathkeale | 0 | 9.88 | 7.55 | 3.87 | 0 | 21.3 | 0.45 | 47.3333 | 6.5 | 6.5 | 7.23 | 7.71 | 9.1 | 9.53 | 9.53 | 13.89 | 13.89 | 20.65 | 0 | 0 | 0 | 0 | 0 | 0 | 1.35 | 8.69 | 8.69 | 10.88 | 10.88 | 15.15 | 15.15 | 450000 | 7800 | 514 | Ireland | County Limerick | 3 | IE-LK
515 | Caherconlish | 0 | 8.81 | 11.72 | 0 | 0 | 20.54 | 0.44 | 46.6818 | 7.99 | 8.82 | 10.4 | 10.4 | 13.28 | 16.43 | 16.43 | 16.43 | 23.37 | 23.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.71 | 3.76 | 4.79 | 5.51 | 8.87 | 12.13 | 440000 | 8200 | 515 | Ireland | County Limerick | 3 | IE-LK
484 | Cappavilla | 0 | 6.89 | 8.95 | 1.38 | 0 | 17.22 | 0.38 | 45.3158 | 4.75 | 7.17 | 7.17 | 9.86 | 9.86 | 12.1 | 14.4 | 14.4 | 20.28 | 20.28 | 0 | 0 | 0 | 0 | 1.38 | 1.38 | 1.38 | 2.81 | 2.81 | 6.72 | 6.72 | 11.28 | 11.28 | 380000 | 7200 | 484 | Ireland | County Limerick | 3 | IE-LK
509 | Adare | 0 | 8.21 | 6.4 | 0 | 0 | 14.61 | 0.37 | 39.4865 | 0 | 9.5 | 10.03 | 10.03 | 12.45 | 16.41 | 16.41 | 22.14 | 22.14 | 22.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.63 | 4.08 | 5.86 | 8.56 | 370000 | 6800 | 509 | Ireland | County Limerick | 3 | IE-LK
505 | Murroe | 0 | 6.46 | 10.54 | 0 | 0 | 17 | 0.35 | 48.5714 | 6.5 | 7.14 | 7.77 | 7.98 | 9.04 | 10.35 | 10.35 | 14.21 | 14.21 | 18.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96 | 5.62 | 7.49 | 8.06 | 9.45 | 12.82 | 15.59 | 350000 | 5800 | 505 | Ireland | County Limerick | 3 | IE-LK
518 | Croom, County Limerick | 0 | 7.38 | 7.57 | 0 | 0 | 14.95 | 0.35 | 42.7143 | 9.5 | 11.01 | 11.91 | 11.91 | 15.09 | 15.09 | 18.76 | 18.76 | 23.13 | 23.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94 | 3.12 | 3.12 | 10.36 | 350000 | 4400 | 518 | Ireland | County Limerick | 3 | IE-LK
529 | Hospital, County Limerick | 0.16 | 9.46 | 2.27 | 0 | 0 | 11.89 | 0.33 | 36.0303 | 11 | 14.3 | 14.3 | 14.3 | 14.3 | 21.08 | 21.08 | 27.5 | 27.5 | 27.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85 | 2.27 | 2.27 | 330000 | 4600 | 529 | Ireland | County Limerick | 3 | IE-LK
491 | Foynes | 0 | 4.81 | 7.59 | 2.11 | 0 | 14.5 | 0.28 | 51.7857 | 0 | 3.75 | 3.75 | 3.75 | 3.75 | 7.93 | 8.55 | 9.35 | 10.62 | 14.02 | 0 | 0 | 0 | 2.11 | 2.11 | 2.11 | 2.11 | 7.73 | 10.17 | 11.01 | 11.99 | 13.55 | 14.5 | 280000 | 8000 | 491 | Ireland | County Limerick | 2 | IE-LK
525 | Bruff | 0 | 5.42 | 5.29 | 0 | 0 | 10.71 | 0.27 | 39.6667 | 0 | 11 | 11 | 14.5 | 14.5 | 14.5 | 19.13 | 22.96 | 22.96 | 22.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.85 | 3.69 | 6.61 | 270000 | 5000 | 525 | Ireland | County Limerick | 3 | IE-LK
495 | Cappavilla | 0 | 0 | 0.55 | 0 | 9.92 | 10.48 | 0.03 | 349.3333 | 0 | 0 | 0 | 0 | 0 | 1.6 | 1.6 | 1.6 | 1.6 | 1.76 | 0 | 9.92 | 10.47 | 10.47 | 10.47 | 10.47 | 10.47 | 10.47 | 10.47 | 10.47 | 10.47 | 10.47 | 10.47 | 30000 | 800 | 495 | Ireland | County Limerick | 1 | IE-LK
497 | Cappavilla | 0 | 0.35 | 1.71 | 4.71 | 9.89 | 16.66 | 0.07 | 238 | 0 | 0 | 0 | 0 | 1.3 | 1.3 | 1.3 | 1.82 | 2.13 | 2.93 | 0 | 12.77 | 16.31 | 16.66 | 16.66 | 16.66 | 16.66 | 16.66 | 16.66 | 16.66 | 16.66 | 16.66 | 16.66 | 70000 | 1200 | 497 | Ireland | County Limerick | 1 | IE-LK
502 | Ahane | 0 | 1.78 | 5.37 | 6.05 | 12.91 | 26.11 | 0.18 | 145.0556 | 0 | 0 | 0 | 1.6 | 1.72 | 1.9 | 1.9 | 2.66 | 2.66 | 4.6 | 0 | 15.51 | 19.92 | 24.33 | 25.38 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 180000 | 3200 | 502 | Ireland | County Limerick | 1 | IE-LK
331 | Longford | 0.79 | 29.45 | 70.59 | 232.36 | 31.15 | 364.34 | 3.12 | 116.7756 | 1.85 | 2.25 | 2.7 | 2.7 | 3.18 | 3.43 | 3.68 | 3.97 | 4.92 | 6.85 | 0 | 12.49 | 107.62 | 269.18 | 327.69 | 347 | 357.21 | 357.21 | 364.34 | 364.34 | 364.34 | 364.34 | 364.34 | 3120000 | 32200 | 331 | Ireland | County Longford | 1 | IE-LD
343 | Edgeworthstown | 0.16 | 8.31 | 20.08 | 23.15 | 0 | 51.69 | 0.68 | 76.0147 | 2.4 | 3.29 | 3.29 | 4.37 | 4.73 | 5.37 | 5.93 | 6.57 | 8.39 | 11.51 | 0 | 0 | 5.67 | 9.7 | 24.2 | 34.95 | 39.2 | 41.59 | 44.49 | 44.49 | 49.36 | 51.69 | 51.69 | 680000 | 9200 | 343 | Ireland | County Longford | 1 | IE-LD
335 | Lanesborough–Ballyleague | 0 | 13.87 | 6.67 | 8.98 | 0 | 29.52 | 0.58 | 50.8966 | 4.25 | 4.48 | 5.5 | 6.59 | 8.67 | 8.67 | 12.52 | 12.52 | 12.52 | 21.09 | 0 | 0 | 0 | 0 | 3.83 | 8.98 | 11.93 | 13.36 | 14.54 | 14.54 | 14.54 | 19.03 | 19.03 | 580000 | 10600 | 335 | Ireland | County Longford | 2 | IE-LD
351 | Ballymahon | 0.13 | 11.54 | 12.75 | 6.51 | 0 | 30.93 | 0.56 | 55.2321 | 0 | 5.02 | 5.62 | 5.94 | 5.94 | 7.83 | 8.44 | 10.86 | 10.86 | 16.43 | 0 | 0 | 0 | 0 | 3.74 | 9.7 | 9.7 | 18.56 | 19.73 | 19.73 | 23.11 | 23.11 | 28.57 | 560000 | 8400 | 351 | Ireland | County Longford | 2 | IE-LD
332 | Granard | 0.18 | 7.7 | 7.09 | 5.03 | 0 | 20 | 0.37 | 54.0541 | 0 | 5.09 | 5.69 | 6.92 | 7.35 | 9.48 | 9.48 | 13.58 | 13.58 | 18.26 | 0 | 0 | 0 | 0 | 2.37 | 5.04 | 7.85 | 8.77 | 10.55 | 11.59 | 11.59 | 15.75 | 19.14 | 370000 | 6400 | 332 | Ireland | County Longford | 2 | IE-LD
320 | Drumlish | 0 | 8.93 | 4.01 | 0 | 0 | 12.94 | 0.31 | 41.7419 | 6.5 | 7.58 | 9.29 | 10.7 | 10.7 | 16.62 | 16.62 | 16.62 | 24.21 | 24.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96 | 2.09 | 2.7 | 3.38 | 4.49 | 4.49 | 7.66 | 310000 | 5000 | 320 | Ireland | County Longford | 3 | IE-LD
324 | Newtownforbes | 0 | 7.03 | 4.29 | 0 | 0 | 11.32 | 0.29 | 39.0345 | 6.5 | 10.99 | 10.99 | 10.99 | 20.64 | 20.64 | 20.64 | 20.64 | 30.08 | 30.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98 | 0.98 | 0.98 | 0.98 | 1.61 | 1.61 | 1.61 | 290000 | 4000 | 324 | Ireland | County Longford | 3 | IE-LD
314 | Dundalk | 4.27 | 99.73 | 341.96 | 611.8 | 390.89 | 1448.64 | 12.02 | 120.5191 | 1.18 | 1.45 | 1.84 | 2.2 | 2.63 | 2.85 | 3.26 | 3.89 | 4.64 | 7.62 | 9.88 | 444.38 | 790.87 | 1135.07 | 1319.18 | 1387.91 | 1431.57 | 1448.64 | 1448.64 | 1448.64 | 1448.64 | 1448.64 | 1448.64 | 12019999.98 | 78400 | 314 | Ireland | County Louth | 1 | IE-LH
341 | Ardee | 1.79 | 22.89 | 36.77 | 82.78 | 22.72 | 166.96 | 1.91 | 87.4136 | 1.93 | 2.62 | 3.21 | 3.58 | 3.85 | 4.14 | 4.74 | 5.38 | 6.02 | 11.1 | 0 | 12.86 | 29.87 | 73.45 | 119.77 | 141.47 | 143.06 | 152.23 | 152.23 | 162.07 | 166.96 | 166.96 | 166.96 | 1909999.99 | 17600 | 341 | Ireland | County Louth | 1 | IE-LH
350 | Clogherhead | 0 | 9.79 | 21.37 | 0 | 0 | 31.16 | 0.63 | 49.4603 | 6.97 | 7.92 | 8.64 | 9.2 | 9.87 | 11.77 | 11.77 | 15.59 | 15.59 | 19.91 | 0 | 0 | 0 | 0 | 0 | 0 | 1.88 | 4.96 | 10.41 | 12.6 | 16.44 | 16.44 | 28.09 | 630000 | 5400 | 350 | Ireland | County Louth | 3 | IE-LH
353 | Termonfeckin | 0 | 13.84 | 11.52 | 0 | 0 | 25.36 | 0.58 | 43.7241 | 8.39 | 10.67 | 10.67 | 13.83 | 17.42 | 17.42 | 17.42 | 17.42 | 27.34 | 27.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.76 | 3 | 3.86 | 4.64 | 8.15 | 12.01 | 580000 | 9800 | 353 | Ireland | County Louth | 3 | IE-LH
346 | Dunleer | 0 | 9.87 | 17.19 | 0 | 7.01 | 34.07 | 0.53 | 64.283 | 0 | 0 | 2.28 | 4.01 | 4.62 | 6.46 | 7.91 | 7.91 | 10.68 | 15.2 | 0 | 7.01 | 10.34 | 11.19 | 15.25 | 17.67 | 20.05 | 22.94 | 22.94 | 22.94 | 27.38 | 27.38 | 34.07 | 530000 | 6800 | 346 | Ireland | County Louth | 2 | IE-LH
337 | Castlebellingham | 0 | 7.97 | 9.06 | 0 | 0 | 17.02 | 0.38 | 44.7895 | 6.5 | 7.13 | 7.68 | 9.82 | 11.44 | 14.14 | 14.14 | 14.14 | 22.63 | 22.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98 | 3.49 | 3.49 | 5.83 | 7.99 | 9.97 | 9.97 | 380000 | 7000 | 337 | Ireland | County Louth | 3 | IE-LH
354 | Tullyallen | 0 | 6.74 | 12.71 | 0 | 0 | 19.45 | 0.38 | 51.1842 | 0 | 5.75 | 6.11 | 6.83 | 7.24 | 8.23 | 8.49 | 10.87 | 10.87 | 17.02 | 0 | 0 | 0 | 0 | 0 | 2.12 | 7.44 | 8.77 | 12.01 | 12.01 | 14.03 | 14.03 | 17.79 | 380000 | 5600 | 354 | Ireland | County Louth | 2 | IE-LH
334 | Dromiskin | 0 | 5.64 | 8.41 | 0 | 0 | 14.05 | 0.29 | 48.4483 | 0 | 0 | 7.5 | 8.53 | 9.34 | 10.94 | 13.53 | 13.53 | 20.49 | 20.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.35 | 5.18 | 5.92 | 7.27 | 8.9 | 8.9 | 289999.99 | 6400 | 334 | Ireland | County Louth | 3 | IE-LH
330 | Tallanstown | 0 | 7.79 | 2.65 | 0 | 0 | 10.44 | 0.28 | 37.2857 | 11 | 11 | 16.15 | 18.53 | 18.53 | 18.53 | 18.53 | 30.18 | 30.18 | 30.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 3.62 | 280000 | 4000 | 330 | Ireland | County Louth | 3 | IE-LH
325 | Louth | 0 | 3.55 | 3.33 | 3.41 | 0 | 10.3 | 0.18 | 57.2222 | 0 | 5.25 | 5.25 | 5.53 | 5.99 | 6.41 | 8.8 | 9.92 | 9.92 | 16.73 | 0 | 0 | 0 | 0 | 0 | 4.45 | 5.35 | 5.35 | 6.75 | 7.25 | 7.25 | 7.25 | 9.37 | 180000 | 3800 | 325 | Ireland | County Louth | 2 | IE-LH
255 | Castlebar | 6.24 | 30.61 | 137.41 | 215.13 | 116.83 | 506.22 | 4.81 | 105.2432 | 1.42 | 1.71 | 2.02 | 2.49 | 2.73 | 3.27 | 3.62 | 4.35 | 4.99 | 9.07 | 0 | 116.1 | 254.99 | 334.81 | 451.22 | 467.17 | 496.22 | 503.95 | 506.17 | 506.22 | 506.22 | 506.22 | 506.22 | 4810000 | 21000 | 255 | Ireland | County Mayo | 1 | IE-MO
166 | Ballina, County Mayo | 0.81 | 60.33 | 74.88 | 91.1 | 18.88 | 246 | 3.55 | 69.2958 | 2.07 | 3.02 | 3.36 | 4.11 | 4.7 | 5.4 | 6.4 | 7 | 9.57 | 13.19 | 0 | 21.76 | 39.38 | 80.44 | 119.03 | 141.89 | 176.67 | 176.67 | 176.67 | 206.16 | 206.16 | 233.99 | 246 | 3550000.01 | 45200 | 166 | Ireland | County Mayo | 2 | IE-MO
259 | Westport | 0.18 | 34.61 | 42.17 | 18.36 | 17.4 | 112.71 | 1.81 | 62.2707 | 1.1 | 1.72 | 2.85 | 3.89 | 5.13 | 6.15 | 7.41 | 10.17 | 10.17 | 14.98 | 0 | 19.71 | 31.75 | 42.47 | 46.67 | 63.65 | 68.43 | 74.65 | 74.65 | 74.65 | 88.56 | 105.6 | 112.72 | 1810000 | 26400 | 259 | Ireland | County Mayo | 2 | IE-MO
298 | Claremorris | 0.25 | 26.22 | 23.97 | 14.42 | 0 | 64.86 | 1.26 | 51.4762 | 5.2 | 5.76 | 6.53 | 6.9 | 8.18 | 9.31 | 9.31 | 12.78 | 12.78 | 18.67 | 0 | 0 | 0 | 0 | 3.83 | 9.32 | 20.63 | 29.72 | 32.65 | 36.1 | 36.1 | 46.35 | 59.13 | 1260000 | 17000 | 298 | Ireland | County Mayo | 2 | IE-MO
311 | Ballinrobe | 0 | 16.31 | 21.5 | 38.25 | 4.97 | 81.03 | 1.03 | 78.6699 | 1.6 | 2.88 | 3.64 | 3.79 | 4.39 | 5.36 | 5.36 | 6.72 | 8.87 | 11.66 | 0 | 4.97 | 15.27 | 25.43 | 32.7 | 45.94 | 62.22 | 66.06 | 72.18 | 72.18 | 79.28 | 81.03 | 81.03 | 1030000 | 15600 | 311 | Ireland | County Mayo | 1 | IE-MO
299 | Ballyhaunis | 0 | 11.04 | 25.66 | 8.36 | 0 | 45.07 | 0.75 | 60.0933 | 5.25 | 5.86 | 5.86 | 7.1 | 7.1 | 7.84 | 8.78 | 9.79 | 11.37 | 14.95 | 0 | 0 | 0 | 0 | 0 | 5.78 | 13.72 | 23.93 | 30.38 | 34.13 | 38.07 | 43.52 | 45.07 | 750000 | 15000 | 299 | Ireland | County Mayo | 2 | IE-MO
247 | Charlestown, County Mayo | 0 | 12.43 | 3.09 | 0 | 0 | 15.52 | 0.46 | 33.7391 | 11.88 | 13.32 | 13.32 | 19.73 | 19.73 | 19.73 | 19.73 | 19.73 | 31.63 | 31.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.38 | 2.56 | 5.67 | 460000 | 8400 | 247 | Ireland | County Mayo | 3 | IE-MO
245 | Swinford | 0 | 10.93 | 4.05 | 6.99 | 0 | 21.97 | 0.45 | 48.8222 | 0 | 5.25 | 5.25 | 5.8 | 7.16 | 8.08 | 11.71 | 11.71 | 11.71 | 19.24 | 0 | 0 | 0 | 0 | 0 | 6.99 | 9.88 | 10.52 | 11.5 | 11.5 | 14.64 | 14.64 | 19.95 | 450000 | 8800 | 245 | Ireland | County Mayo | 3 | IE-MO
88 | Belmullet | 0 | 7.7 | 11.88 | 7.18 | 0 | 26.76 | 0.43 | 62.2326 | 4.75 | 4.75 | 5.95 | 5.95 | 6.77 | 6.99 | 8.4 | 10.96 | 10.96 | 15.62 | 0 | 0 | 0 | 0 | 1.88 | 5.92 | 14.45 | 16.07 | 17.99 | 17.99 | 21.28 | 21.28 | 26.76 | 430000 | 7800 | 88 | Ireland | County Mayo | 2 | IE-MO
267 | Kiltimagh | 0 | 11.93 | 2.38 | 0 | 0 | 14.3 | 0.43 | 33.2558 | 8.5 | 11.64 | 11.64 | 18.62 | 18.62 | 18.62 | 18.62 | 18.62 | 31.36 | 31.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97 | 1.81 | 2.38 | 2.38 | 4.97 | 430000 | 8600 | 267 | Ireland | County Mayo | 3 | IE-MO
260 | Pontoon, County Mayo | 0 | 5.24 | 12.09 | 0 | 0 | 17.33 | 0.35 | 49.5143 | 8.5 | 8.5 | 9.13 | 9.94 | 10.87 | 12.13 | 12.13 | 15.56 | 15.56 | 19.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 6.66 | 8.16 | 9.91 | 15.99 | 350000 | 3400 | 260 | Ireland | County Mayo | 3 | IE-MO
165 | Crossmolina | 0 | 9.09 | 1.9 | 0 | 0 | 10.99 | 0.34 | 32.3235 | 11 | 15.7 | 15.7 | 20.24 | 20.24 | 20.24 | 20.24 | 30.61 | 30.61 | 30.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.62 | 0.62 | 1.9 | 340000 | 9000 | 165 | Ireland | County Mayo | 3 | IE-MO
225 | Foxford | 0 | 8.34 | 2.8 | 1.75 | 0 | 12.89 | 0.32 | 40.2812 | 0 | 4.75 | 4.75 | 8.16 | 8.16 | 14.03 | 14.03 | 14.03 | 23.42 | 23.42 | 0 | 0 | 0 | 0 | 1.75 | 1.75 | 4.02 | 4.02 | 4.55 | 4.55 | 4.55 | 6.98 | 6.98 | 320000 | 7000 | 225 | Ireland | County Mayo | 3 | IE-MO
270 | Balla, County Mayo | 0 | 7.27 | 2.16 | 1.28 | 0 | 10.71 | 0.3 | 35.7 | 0 | 11.36 | 11.36 | 11.36 | 19.2 | 19.2 | 19.2 | 28.98 | 28.98 | 28.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.28 | 1.28 | 1.83 | 1.83 | 4.31 | 300000 | 6200 | 270 | Ireland | County Mayo | 3 | IE-MO
356 | Drogheda | 3.63 | 124.15 | 361.01 | 233.04 | 34.13 | 755.97 | 10.14 | 74.5533 | 2.18 | 2.91 | 3.66 | 3.95 | 4.51 | 5.03 | 5.56 | 6.75 | 7.29 | 12.61 | 0 | 42.63 | 130.26 | 254.42 | 326.72 | 466.82 | 603.95 | 634.53 | 686.01 | 686.01 | 734.1 | 755.97 | 755.97 | 10139999.99 | 63600 | 356 | Ireland | County Meath | 2 | IE-MH
359 | Navan | 0.98 | 90.49 | 191.31 | 327.24 | 408.5 | 1018.52 | 7.95 | 128.1157 | 0.99 | 1.28 | 1.47 | 1.83 | 2.06 | 2.42 | 2.82 | 3.27 | 4.18 | 8 | 72.7 | 406.28 | 694.34 | 883.84 | 921.61 | 964.4 | 998.97 | 1018.4 | 1018.52 | 1018.52 | 1018.52 | 1018.52 | 1018.52 | 7950000 | 58200 | 359 | Ireland | County Meath | 1 | IE-MH
386 | Ashbourne, County Meath | 1.95 | 32.3 | 112.04 | 74.91 | 108.76 | 329.95 | 3.15 | 104.746 | 0.7 | 1.22 | 1.62 | 2.06 | 2.61 | 3.01 | 3.69 | 4.09 | 5.28 | 8.72 | 14.3 | 116.92 | 179.41 | 224.4 | 285.73 | 303.55 | 312.47 | 324.11 | 329.95 | 329.95 | 329.95 | 329.95 | 329.95 | 3150000 | 17600 | 386 | Ireland | County Meath | 1 | IE-MH
362 | Laytown | 0.35 | 42.92 | 102.82 | 10.56 | 3.42 | 160.06 | 2.81 | 56.9609 | 4.21 | 5.24 | 5.24 | 6.65 | 7.31 | 7.93 | 8.6 | 9.28 | 10.98 | 19.19 | 0 | 0 | 0 | 11.9 | 17.23 | 28.85 | 61.03 | 95.66 | 107.22 | 115.56 | 129.59 | 147.97 | 160.06 | 2810000.01 | 30800 | 362 | Ireland | County Meath | 2 | IE-MH
374 | Trim, County Meath | 0.03 | 34.45 | 74.36 | 79.13 | 15.12 | 203.1 | 2.57 | 79.0272 | 2.68 | 3.31 | 3.65 | 4.23 | 4.87 | 5.43 | 6.17 | 6.69 | 9.07 | 13.74 | 0 | 0 | 15.12 | 52.06 | 101.13 | 132.47 | 151.44 | 163.81 | 163.81 | 179.52 | 196.83 | 203.1 | 203.1 | 2570000 | 27000 | 374 | Ireland | County Meath | 1 | IE-MH
388 | Ratoath | 1.01 | 35.45 | 84.15 | 18.65 | 3.04 | 142.31 | 2.52 | 56.4722 | 3.89 | 4.41 | 5.76 | 6.37 | 7.03 | 7.78 | 8.37 | 9.17 | 11.41 | 18.58 | 0 | 0 | 3.04 | 13.76 | 20.11 | 42.38 | 54.52 | 85.2 | 93.94 | 102.49 | 119.38 | 134.67 | 142.31 | 2520000 | 15200 | 388 | Ireland | County Meath | 2 | IE-MH
407 | Dunboyne | 0.29 | 27.59 | 53.06 | 17.43 | 17.16 | 115.54 | 1.68 | 68.7738 | 1.77 | 2.45 | 3.43 | 4.19 | 4.75 | 5.44 | 6.33 | 7.46 | 8.66 | 16.16 | 0 | 13.53 | 23.2 | 32.82 | 52.5 | 71.89 | 85.96 | 90.07 | 96.68 | 96.68 | 96.68 | 108.73 | 115.54 | 1680000 | 16800 | 407 | Ireland | County Meath | 2 | IE-MH
366 | Duleek | 0 | 23.35 | 33.76 | 18 | 4.05 | 79.17 | 1.25 | 63.336 | 2.8 | 3.56 | 4.3 | 5.08 | 5.85 | 7.09 | 8.03 | 11.15 | 11.15 | 15.01 | 0 | 0 | 4.05 | 12.7 | 25.63 | 37.5 | 44.02 | 46.56 | 50.92 | 50.92 | 62.41 | 62.41 | 72.04 | 1250000 | 16200 | 366 | Ireland | County Meath | 2 | IE-MH
383 | Dunshaughlin | 0.37 | 18.62 | 30.24 | 13.16 | 4.15 | 66.54 | 1.07 | 62.1869 | 2.8 | 4.06 | 4.69 | 5.84 | 6.5 | 7.37 | 8.89 | 8.89 | 11.15 | 15.49 | 0 | 0 | 6.78 | 9.18 | 16.47 | 25.99 | 31.71 | 41.41 | 46.13 | 46.13 | 53.66 | 53.66 | 66.54 | 1070000 | 9800 | 383 | Ireland | County Meath | 2 | IE-MH
349 | Kells | 0 | 11.15 | 20.56 | 4.45 | 32.54 | 68.69 | 0.71 | 96.7465 | 0 | 0 | 2 | 2 | 2.2 | 2.61 | 3.23 | 4.02 | 5 | 6.97 | 0 | 0 | 43.1 | 46.35 | 57.05 | 62.11 | 65.63 | 65.63 | 65.63 | 65.63 | 68.69 | 68.69 | 68.69 | 710000 | 13800 | 349 | Ireland | County Meath | 1 | IE-MH
375 | Stamullen | 0 | 9.79 | 30.58 | 1.33 | 0 | 41.71 | 0.71 | 58.7465 | 4.71 | 5.37 | 5.37 | 5.94 | 6.65 | 7.03 | 7.82 | 8.41 | 10.67 | 13.35 | 0 | 0 | 0 | 0 | 2.46 | 13.65 | 20.67 | 28.03 | 29.76 | 29.76 | 34.45 | 37.92 | 41.71 | 710000 | 9800 | 375 | Ireland | County Meath | 2 | IE-MH
395 | Enfield | 0.15 | 7.9 | 19.72 | 32.54 | 10.76 | 71.07 | 0.68 | 104.5147 | 2 | 2.45 | 2.45 | 2.87 | 3.23 | 3.58 | 4.09 | 4.59 | 5.5 | 8.46 | 0 | 0 | 25.36 | 39.38 | 58.17 | 62.88 | 66 | 66 | 70.25 | 71.07 | 71.07 | 71.07 | 71.07 | 680000 | 5200 | 395 | Ireland | County Meath | 1 | IE-MH
85 | Kells | 0 | 3.51 | 31.17 | 14.73 | 0 | 49.41 | 0.56 | 88.2321 | 0 | 6.5 | 6.89 | 6.89 | 7.66 | 7.66 | 8.29 | 8.57 | 9.16 | 11.31 | 0 | 0 | 0 | 0 | 0 | 0 | 11.55 | 22.18 | 37.67 | 45.08 | 48.5 | 49.41 | 49.41 | 560000 | 5800 | 85 | Ireland | County Meath | 1 | IE-MH
360 | Athboy | 0 | 12.37 | 6.22 | 7.41 | 0 | 26 | 0.51 | 50.9804 | 3.25 | 3.25 | 4.09 | 4.73 | 5.02 | 6.91 | 8.95 | 8.95 | 14.33 | 21.62 | 0 | 0 | 0 | 6.15 | 10.13 | 10.8 | 14.88 | 15.95 | 17.24 | 17.24 | 17.24 | 20.85 | 20.85 | 510000 | 12800 | 360 | Ireland | County Meath | 2 | IE-MH
372 | Kentstown | 0 | 7.37 | 10.45 | 0 | 0 | 17.82 | 0.4 | 44.55 | 8.5 | 9.79 | 9.79 | 13.42 | 13.42 | 13.42 | 18.78 | 18.78 | 23.71 | 23.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.79 | 3.41 | 3.41 | 6.11 | 11.37 | 400000 | 7000 | 372 | Ireland | County Meath | 3 | IE-MH
355 | Slane | 0 | 8.61 | 7.85 | 0 | 0 | 16.46 | 0.38 | 43.3158 | 9.5 | 13.17 | 13.17 | 14.93 | 14.93 | 19.36 | 19.36 | 19.36 | 19.36 | 27.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 1.77 | 5.16 | 9.2 | 380000 | 6000 | 355 | Ireland | County Meath | 3 | IE-MH
342 | Oldcastle | 0 | 7.39 | 6.15 | 9.84 | 0 | 23.37 | 0.35 | 66.7714 | 0 | 4.25 | 4.25 | 4.49 | 4.91 | 5.32 | 6.95 | 6.95 | 9.53 | 13.14 | 0 | 0 | 0 | 0 | 10.88 | 14.35 | 16.28 | 16.28 | 16.28 | 18.99 | 18.99 | 21.54 | 23.37 | 350000 | 7600 | 342 | Ireland | County Meath | 2 | IE-MH
384 | Summerhill | 0 | 8.28 | 2.89 | 0 | 8.14 | 19.3 | 0.29 | 66.5517 | 0 | 0 | 2 | 2 | 2.84 | 5.52 | 5.52 | 5.52 | 11.32 | 14.19 | 0 | 0 | 9.08 | 9.08 | 9.08 | 11.02 | 11.02 | 11.02 | 11.02 | 11.02 | 15.69 | 17.44 | 17.44 | 290000 | 3800 | 384 | Ireland | County Meath | 2 | IE-MH
348 | Baile Órthaí | 0 | 1.15 | 4.94 | 9.23 | 20.24 | 35.56 | 0.19 | 187.1579 | 0 | 0 | 0 | 0.7 | 0.94 | 1.33 | 1.85 | 2.35 | 3.03 | 4.61 | 16.81 | 24.14 | 31.24 | 34.41 | 35.07 | 35.56 | 35.56 | 35.56 | 35.56 | 35.56 | 35.56 | 35.56 | 35.56 | 190000 | 2800 | 348 | Ireland | County Meath | 1 | IE-MH
376 | Ballivor | 0 | 1.89 | 5.31 | 0 | 6.76 | 13.96 | 0.13 | 107.3846 | 0 | 0 | 0 | 0 | 1.3 | 1.81 | 2.86 | 3.65 | 4.64 | 7.11 | 0 | 7.94 | 9.74 | 10.89 | 12.03 | 12.87 | 13.4 | 13.74 | 13.96 | 13.96 | 13.96 | 13.96 | 13.96 | 130000 | 2800 | 376 | Ireland | County Meath | 1 | IE-MH
361 | Domhnach Phádraig | 0 | 3.08 | 13.75 | 14.56 | 0 | 31.39 | 0.34 | 92.3235 | 4.75 | 5.07 | 5.07 | 5.72 | 5.72 | 6.37 | 6.72 | 7.14 | 7.69 | 10.66 | 0 | 0 | 0 | 0 | 2.07 | 10.67 | 20.18 | 26.34 | 26.34 | 26.34 | 31.39 | 31.39 | 31.39 | 340000 | 7600 | 361 | Ireland | County Meath | 1 | IE-MH
368 | Dunderry | 0 | 0.66 | 0 | 2.92 | 10.08 | 13.65 | 0.04 | 341.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0.9 | 2.89 | 10.08 | 13 | 13.39 | 13.39 | 13.65 | 13.65 | 13.65 | 13.65 | 13.65 | 13.65 | 13.65 | 13.65 | 13.65 | 40000 | 1000 | 368 | Ireland | County Meath | 1 | IE-MH
239 | Monaghan | 0.42 | 48.79 | 70.72 | 67.85 | 24.38 | 212.16 | 2.88 | 73.6667 | 1.87 | 2.42 | 3.11 | 3.52 | 4.48 | 5.08 | 6.07 | 7.12 | 9.18 | 14.93 | 0 | 21.04 | 51.83 | 86.7 | 100.75 | 140.36 | 154.75 | 161.52 | 161.52 | 182.52 | 182.52 | 211.89 | 212.16 | 2880000 | 34000 | 239 | Ireland | County Monaghan | 2 | IE-MN
315 | Carrickmacross | 0.24 | 31.4 | 50.98 | 35.12 | 4.83 | 122.57 | 1.83 | 66.9781 | 2.66 | 3.99 | 4.22 | 5.45 | 5.99 | 6.41 | 7.37 | 8.28 | 10.9 | 16.76 | 0 | 4.83 | 9.93 | 22.82 | 26.2 | 59.19 | 74.97 | 80.86 | 88.46 | 88.46 | 104.9 | 116.57 | 122.57 | 1830000 | 21600 | 315 | Ireland | County Monaghan | 2 | IE-MN
283 | Castleblayney | 0.49 | 11.06 | 37.81 | 110.51 | 18.38 | 178.26 | 1.47 | 121.2653 | 1.94 | 2.56 | 2.96 | 3.21 | 3.58 | 3.92 | 3.92 | 4.7 | 5.18 | 7.24 | 0 | 15.31 | 52.19 | 105.11 | 152.85 | 169.71 | 169.71 | 178.26 | 178.26 | 178.26 | 178.26 | 178.26 | 178.26 | 1470000 | 12800 | 283 | Ireland | County Monaghan | 1 | IE-MN
253 | Clones | 0.18 | 11.73 | 16.58 | 19.46 | 14.25 | 62.2 | 0.76 | 81.8421 | 1.6 | 1.95 | 2.77 | 3.18 | 3.68 | 4.02 | 5.28 | 6.36 | 7.81 | 13.74 | 0 | 7.98 | 20.81 | 28.34 | 37.69 | 47.42 | 49.19 | 53.33 | 53.33 | 53.33 | 59.5 | 62.2 | 62.2 | 760000 | 10200 | 253 | Ireland | County Monaghan | 1 | IE-MN
273 | Ballybay | 0 | 10.89 | 11.84 | 2.75 | 0 | 25.49 | 0.56 | 45.5179 | 6.5 | 7.4 | 8.63 | 9.34 | 12.34 | 12.34 | 14.96 | 14.96 | 21.99 | 21.99 | 0 | 0 | 0 | 0 | 0 | 0 | 2.75 | 3.82 | 6.84 | 8.17 | 8.17 | 15.78 | 15.78 | 560000 | 9000 | 273 | Ireland | County Monaghan | 3 | IE-MN
210 | Emyvale | 0 | 4.67 | 7.63 | 0 | 0 | 12.3 | 0.25 | 49.2 | 9.5 | 10.52 | 10.52 | 11.85 | 11.85 | 14.03 | 14.03 | 16.37 | 20.46 | 20.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68 | 4.57 | 7.08 | 9 | 250000 | 4400 | 210 | Ireland | County Monaghan | 3 | IE-MN
400 | Tullamore | 0.98 | 62.75 | 94.86 | 272.86 | 108.31 | 539.76 | 5 | 107.952 | 1.54 | 1.79 | 2.18 | 2.43 | 2.64 | 3.06 | 3.29 | 4.15 | 5.04 | 9.27 | 0 | 116.94 | 285.42 | 411.13 | 465.14 | 475.68 | 504.54 | 527.15 | 527.15 | 539.76 | 539.76 | 539.76 | 539.76 | 5000000 | 53200 | 400 | Ireland | County Offaly | 1 | IE-OY
430 | Birr | 1.11 | 24.74 | 66.02 | 43.01 | 5.21 | 140.09 | 2.03 | 69.0099 | 2.16 | 3.85 | 4.75 | 4.75 | 5.71 | 6.4 | 6.92 | 7.91 | 9.65 | 14.96 | 0 | 5.21 | 7.88 | 21.68 | 36.41 | 56.13 | 89.48 | 109.19 | 112.45 | 123 | 123 | 140.08 | 140.09 | 2030000 | 16800 | 430 | Ireland | County Offaly | 2 | IE-OY
438 | Portarlington, County Laois | 0 | 15.31 | 38.5 | 52.39 | 0 | 106.19 | 1.27 | 83.6142 | 2.69 | 2.69 | 3 | 3.36 | 3.61 | 4.27 | 4.27 | 5.62 | 6.3 | 11.48 | 0 | 0 | 10.1 | 54.2 | 74.38 | 84.83 | 90.8 | 96.14 | 96.14 | 102.27 | 105.78 | 106.19 | 106.19 | 1270000 | 18000 | 438 | Ireland | County Offaly | 1 | IE-OY
405 | Edenderry | 0 | 13.3 | 23.04 | 44.6 | 0 | 80.94 | 0.94 | 86.1064 | 2.4 | 2.78 | 3.12 | 3.12 | 3.52 | 3.89 | 4.45 | 5.25 | 5.93 | 8.97 | 0 | 0 | 14.79 | 49.24 | 58.35 | 68.55 | 68.55 | 73.46 | 77.64 | 77.64 | 80.94 | 80.94 | 80.94 | 940000 | 16200 | 405 | Ireland | County Offaly | 1 | IE-OY
389 | Clara | 0 | 18.82 | 15.05 | 2.33 | 0 | 36.2 | 0.76 | 47.6316 | 4.31 | 5.51 | 6.69 | 7.87 | 10.12 | 10.12 | 15.7 | 15.7 | 21.71 | 21.71 | 0 | 0 | 0 | 2.33 | 3.47 | 5.55 | 9.19 | 11.72 | 11.72 | 11.72 | 15.08 | 15.08 | 24.13 | 760000 | 13800 | 389 | Ireland | County Offaly | 3 | IE-OY
415 | Banagher | 0 | 7.71 | 15.75 | 16.4 | 0 | 39.86 | 0.57 | 69.9298 | 2.4 | 3.18 | 3.41 | 4.07 | 4.81 | 6.25 | 6.94 | 8.6 | 10.97 | 13.62 | 0 | 0 | 3 | 12.17 | 18.06 | 21.43 | 25.43 | 25.43 | 29.93 | 29.93 | 34.98 | 38.49 | 39.86 | 570000 | 9600 | 415 | Ireland | County Offaly | 2 | IE-OY
424 | Kilcormac | 0 | 9.72 | 5.96 | 1.64 | 0 | 17.32 | 0.39 | 44.4103 | 5.75 | 7.47 | 8.56 | 9.63 | 11.11 | 11.11 | 16.27 | 16.27 | 21.82 | 21.82 | 0 | 0 | 0 | 0 | 0 | 1.64 | 1.64 | 3.04 | 4.39 | 5.79 | 7.03 | 7.03 | 11.19 | 390000 | 5600 | 424 | Ireland | County Offaly | 3 | IE-OY
394 | Ferbane | 0 | 8.23 | 5.82 | 3.5 | 0 | 17.55 | 0.35 | 50.1429 | 0 | 5.69 | 5.69 | 7.01 | 8.17 | 9.58 | 9.58 | 13.98 | 13.98 | 20.38 | 0 | 0 | 0 | 0 | 1.95 | 3.5 | 3.5 | 5.35 | 7.56 | 8.82 | 8.82 | 12.34 | 12.34 | 350000 | 5600 | 394 | Ireland | County Offaly | 2 | IE-OY
416 | Mucklagh, County Offaly | 0 | 7.49 | 3.81 | 0 | 0 | 11.3 | 0.29 | 38.9655 | 0 | 9.5 | 11.66 | 11.66 | 18.01 | 18.01 | 18.01 | 26.07 | 26.07 | 26.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.06 | 2.76 | 2.76 | 5.27 | 290000 | 5800 | 416 | Ireland | County Offaly | 3 | IE-OY
434 | Crinkill | 0 | 5.21 | 6.28 | 0 | 0 | 11.49 | 0.23 | 49.9565 | 7.5 | 7.97 | 8.49 | 9.07 | 11.16 | 11.16 | 11.16 | 16.34 | 20.06 | 20.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3.02 | 3.94 | 5.13 | 5.13 | 8.21 | 230000 | 4600 | 434 | Ireland | County Offaly | 3 | IE-OY
454 | Shinrone | 0 | 4.27 | 2.51 | 3.83 | 0 | 10.61 | 0.19 | 55.8421 | 0 | 0 | 3.75 | 4.19 | 5.33 | 7.56 | 9.74 | 9.74 | 16.92 | 16.92 | 0 | 0 | 0 | 2.13 | 3.83 | 4.88 | 4.88 | 6.34 | 6.34 | 7.25 | 7.25 | 7.25 | 9.5 | 190000 | 4000 | 454 | Ireland | County Offaly | 2 | IE-OY
385 | Kilbeggan | 0 | 3.73 | 3.16 | 5.92 | 0 | 12.81 | 0.17 | 75.3529 | 0 | 3.25 | 3.58 | 3.58 | 4 | 4.72 | 5.28 | 5.28 | 9.98 | 12.76 | 0 | 0 | 0 | 5.92 | 7.52 | 8.52 | 8.52 | 8.52 | 8.52 | 11.19 | 11.19 | 12.33 | 12.81 | 170000 | 4000 | 385 | Ireland | County Offaly | 1 | IE-OY
369 | Athlone | 5.34 | 79.81 | 210.67 | 427.02 | 61.68 | 784.51 | 8.25 | 95.0921 | 1.9 | 2.24 | 2.72 | 3.2 | 3.66 | 3.85 | 4.53 | 5.02 | 6.19 | 10.24 | 0 | 58.15 | 240.23 | 424.87 | 581.64 | 670.52 | 700.73 | 739.14 | 766.69 | 783.87 | 784.51 | 784.51 | 784.51 | 8250000 | 59200 | 369 | Ireland | County Roscommon | 1 | IE-RN
338 | Roscommon | 0.99 | 38.63 | 46.47 | 91.42 | 9.91 | 187.42 | 2.46 | 76.187 | 1.94 | 2.51 | 3.56 | 3.89 | 4.26 | 4.85 | 5.65 | 6.55 | 8.51 | 14.71 | 0 | 15.71 | 24.93 | 66.67 | 107.8 | 135.84 | 142.47 | 142.47 | 159.4 | 159.4 | 179.1 | 187.42 | 187.42 | 2460000 | 25400 | 338 | Ireland | County Roscommon | 1 | IE-RN
268 | Ballaghaderreen | 0.08 | 17.66 | 18.84 | 4.61 | 3.38 | 44.57 | 0.83 | 53.6988 | 2.4 | 3.93 | 5.38 | 6.18 | 6.18 | 7.76 | 8.54 | 10.46 | 10.46 | 21.89 | 0 | 0 | 3.38 | 6.75 | 6.75 | 11.35 | 15.28 | 25.65 | 28.23 | 28.23 | 31.96 | 31.96 | 40.54 | 830000 | 16400 | 268 | Ireland | County Roscommon | 2 | IE-RN
308 | Castlerea | 0 | 18.54 | 12.66 | 1.35 | 0 | 32.54 | 0.77 | 42.2597 | 7.5 | 8.11 | 9.57 | 10.33 | 12.1 | 12.1 | 16.28 | 16.28 | 16.28 | 22.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.35 | 6.7 | 9.53 | 11.09 | 14.41 | 21.32 | 770000 | 12800 | 308 | Ireland | County Roscommon | 3 | IE-RN
264 | Boyle | 0 | 12.93 | 16.72 | 11.74 | 0 | 41.39 | 0.75 | 55.1867 | 3.25 | 4.72 | 5.69 | 6.22 | 6.45 | 7.65 | 8.68 | 10.66 | 10.66 | 16.41 | 0 | 0 | 0 | 2.13 | 5.16 | 11.41 | 21.6 | 24.3 | 26.98 | 26.98 | 30.7 | 30.7 | 38.19 | 750000 | 14600 | 264 | Ireland | County Roscommon | 2 | IE-RN
316 | Strokestown | 0 | 9.35 | 1.53 | 2.71 | 0 | 13.58 | 0.33 | 41.1515 | 0 | 7.5 | 8.02 | 9.92 | 9.92 | 15.23 | 15.23 | 15.23 | 15.23 | 25.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.71 | 4.24 | 4.72 | 4.72 | 4.72 | 7.3 | 330000 | 5400 | 316 | Ireland | County Roscommon | 3 | IE-RN
336 | Castlecoote | 0 | 5.19 | 4.65 | 4.8 | 0 | 14.64 | 0.25 | 58.56 | 0 | 3.75 | 3.75 | 3.98 | 5.45 | 5.97 | 8.02 | 10.24 | 10.24 | 16.57 | 0 | 0 | 0 | 4.79 | 5.87 | 7.5 | 7.5 | 8.84 | 9.44 | 9.44 | 10.87 | 10.87 | 14.64 | 250000 | 4000 | 336 | Ireland | County Roscommon | 2 | IE-RN
146 | Sligo | 1.79 | 73.35 | 155.88 | 325.57 | 146.26 | 702.86 | 6.58 | 106.8176 | 1.27 | 1.99 | 2.24 | 2.48 | 2.9 | 3.26 | 3.61 | 4.15 | 5.25 | 9.25 | 0 | 132.22 | 343.57 | 508.45 | 602.87 | 621.2 | 656.07 | 656.07 | 691.39 | 702.86 | 702.86 | 702.86 | 702.86 | 6580000 | 56200 | 146 | Ireland | County Sligo | 1 | IE-SO
220 | Tubbercurry | 0 | 10.48 | 21.97 | 20.67 | 0 | 53.12 | 0.74 | 71.7838 | 2.8 | 3.6 | 4.35 | 4.35 | 4.35 | 6.17 | 6.65 | 7.45 | 8.93 | 12.79 | 0 | 0 | 2.6 | 9.42 | 14.49 | 27.39 | 38.71 | 41.01 | 44.76 | 44.76 | 44.76 | 51.13 | 53.12 | 740000 | 13800 | 220 | Ireland | County Sligo | 2 | IE-SO
186 | Collooney | 0 | 10.53 | 20.02 | 21.54 | 16.2 | 68.29 | 0.71 | 96.1831 | 1.6 | 1.86 | 2.1 | 2.54 | 3.1 | 3.38 | 4.26 | 5.35 | 6.03 | 10.03 | 0 | 16.2 | 30.36 | 36.5 | 50.86 | 53.93 | 56.99 | 61.74 | 61.74 | 61.74 | 68.29 | 68.29 | 68.29 | 710000 | 9800 | 186 | Ireland | County Sligo | 1 | IE-SO
219 | Ballymote | 0 | 12.5 | 13.46 | 5.6 | 3.49 | 35.05 | 0.64 | 54.7656 | 2 | 3.18 | 4.77 | 5.75 | 5.75 | 7.53 | 9.88 | 9.88 | 9.88 | 18.07 | 0 | 0 | 3.49 | 5.09 | 9.09 | 12.32 | 17.7 | 20.56 | 21.98 | 24.41 | 24.41 | 24.41 | 33.53 | 640000 | 9800 | 219 | Ireland | County Sligo | 2 | IE-SO
144 | Strandhill | 0 | 12.41 | 11.2 | 1.52 | 0 | 25.13 | 0.54 | 46.537 | 4.75 | 7.56 | 9.49 | 9.49 | 12.06 | 12.06 | 12.06 | 17.41 | 22.08 | 22.08 | 0 | 0 | 0 | 0 | 1.52 | 1.52 | 3.12 | 4.55 | 6.58 | 7.32 | 7.32 | 10.49 | 17.88 | 540000 | 7200 | 144 | Ireland | County Sligo | 3 | IE-SO
172 | Ballysadare | 0.05 | 8.69 | 16.05 | 0 | 0 | 24.79 | 0.51 | 48.6078 | 6.5 | 6.5 | 8.14 | 8.66 | 9.68 | 10.86 | 10.86 | 14.58 | 14.58 | 24.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96 | 0.96 | 8.65 | 11.81 | 13.76 | 18.67 | 22.44 | 510000 | 6200 | 172 | Ireland | County Sligo | 3 | IE-SO
321 | Grange, County Sligo | 0 | 7.05 | 10.84 | 3.59 | 0 | 21.49 | 0.43 | 49.9767 | 0 | 5.83 | 8.3 | 9.52 | 9.52 | 12.48 | 12.48 | 16.03 | 16.03 | 20.17 | 0 | 0 | 0 | 0 | 2.18 | 3.59 | 3.59 | 5.49 | 6.28 | 7.68 | 7.68 | 11.79 | 16.47 | 429999.99 | 7200 | 321 | Ireland | County Sligo | 3 | IE-SO
581 | Rathcormack | 0 | 7.98 | 14.02 | 0 | 0 | 22 | 0.43 | 51.1628 | 5.75 | 6.23 | 7.14 | 7.14 | 8.52 | 8.91 | 10.17 | 10.17 | 13.67 | 17.22 | 0 | 0 | 0 | 0 | 0 | 1.05 | 4.54 | 6.04 | 11.64 | 11.64 | 13.51 | 17.69 | 20.44 | 430000 | 5600 | 581 | Ireland | County Sligo | 2 | IE-SO
184 | Coolaney | 0 | 10.36 | 4.26 | 0 | 0 | 14.62 | 0.36 | 40.6111 | 13.15 | 13.15 | 15.86 | 15.86 | 15.86 | 21.46 | 21.46 | 21.46 | 21.46 | 29.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.64 | 1.39 | 3.16 | 360000 | 5400 | 184 | Ireland | County Sligo | 3 | IE-SO
135 | Enniscrone | 0 | 8.58 | 3.67 | 0 | 0 | 12.25 | 0.34 | 36.0294 | 7.5 | 7.5 | 10.54 | 10.54 | 17.63 | 17.63 | 17.63 | 17.63 | 29.24 | 29.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.17 | 1.17 | 1.17 | 2.62 | 2.62 | 5.13 | 340000 | 7600 | 135 | Ireland | County Sligo | 3 | IE-SO
109 | Grange, County Sligo | 0 | 5.02 | 3.72 | 2.58 | 0 | 11.32 | 0.21 | 53.9048 | 0 | 0 | 3.75 | 3.75 | 8.77 | 10.55 | 10.55 | 15.55 | 15.55 | 20.04 | 0 | 0 | 0 | 2.58 | 2.58 | 2.58 | 2.58 | 2.58 | 4.66 | 4.66 | 5.78 | 5.78 | 8.84 | 210000 | 4400 | 109 | Ireland | County Sligo | 2 | IE-SO
557 | Clonmel | 2.04 | 59.43 | 105.03 | 181.27 | 19.36 | 367.13 | 4.52 | 81.2235 | 2.23 | 3 | 3.32 | 3.7 | 4.24 | 4.64 | 5.19 | 5.79 | 6.52 | 11.96 | 0 | 0 | 65.86 | 121.14 | 234.02 | 287.63 | 310.42 | 334.97 | 334.97 | 356.45 | 367.06 | 367.13 | 367.13 | 4520000 | 39400 | 557 | Ireland | County Tipperary | 1 | IE-TA
465 | Nenagh | 1.07 | 45.1 | 70.99 | 172.54 | 20.64 | 310.34 | 3.58 | 86.6872 | 1.86 | 2.5 | 2.96 | 3.33 | 3.65 | 4.13 | 4.56 | 5.07 | 5.8 | 10.41 | 0 | 20.64 | 72.3 | 161.9 | 227.38 | 265.4 | 265.4 | 289.6 | 303.99 | 303.99 | 310.34 | 310.34 | 310.34 | 3580000 | 28000 | 465 | Ireland | County Tipperary | 1 | IE-TA
516 | Thurles | 0.94 | 28.11 | 87.2 | 110.64 | 6.3 | 233.19 | 2.75 | 84.7964 | 2.9 | 3.89 | 3.89 | 4.4 | 4.75 | 5.2 | 5.53 | 5.98 | 6.95 | 10.61 | 0 | 0 | 16.86 | 46.06 | 99.36 | 181.52 | 205.93 | 205.93 | 218.92 | 228.75 | 233.19 | 233.19 | 233.19 | 2750000 | 23600 | 516 | Ireland | County Tipperary | 1 | IE-TA
463 | Roscrea | 1 | 34.52 | 74.94 | 36.76 | 0 | 147.22 | 2.25 | 65.4311 | 3.78 | 4.78 | 4.78 | 5.58 | 6.15 | 6.6 | 7.21 | 7.88 | 9.81 | 15.81 | 0 | 0 | 2.34 | 11.7 | 26.37 | 49.19 | 94.89 | 109.27 | 109.27 | 123.1 | 123.1 | 142.62 | 147.22 | 2250000 | 19600 | 463 | Ireland | County Tipperary | 2 | IE-TA
533 | Tipperary | 0.18 | 20.05 | 53.88 | 57.4 | 6.8 | 138.31 | 1.62 | 85.3765 | 1.61 | 2.7 | 3.3 | 3.82 | 4.38 | 4.38 | 5.32 | 5.84 | 6.82 | 11.53 | 0 | 9.5 | 24.26 | 53.97 | 84.41 | 106.84 | 120.3 | 126.83 | 126.83 | 133.89 | 138.31 | 138.31 | 138.31 | 1620000 | 19400 | 533 | Ireland | County Tipperary | 1 | IE-TA
534 | Cashel | 0.67 | 16.75 | 50.83 | 41.97 | 3.07 | 113.29 | 1.45 | 78.131 | 2.96 | 3.9 | 4.32 | 4.32 | 5.19 | 5.55 | 6.02 | 6.89 | 7.55 | 12.94 | 0 | 0 | 8.45 | 21.33 | 30.22 | 59.52 | 88.8 | 95.42 | 102.47 | 102.47 | 109.96 | 113.29 | 113.29 | 1450000 | 13600 | 534 | Ireland | County Tipperary | 1 | IE-TA
494 | Templemore | 0 | 11.55 | 28.19 | 12.01 | 0 | 51.75 | 0.79 | 65.5063 | 4.56 | 5.02 | 5.44 | 6.17 | 6.17 | 7.02 | 7.67 | 8.92 | 10.57 | 13.82 | 0 | 0 | 0 | 0 | 6.7 | 13.21 | 25.95 | 35.14 | 40.97 | 40.97 | 45.66 | 51.75 | 51.75 | 790000 | 11200 | 494 | Ireland | County Tipperary | 2 | IE-TA
493 | Newport | 0 | 13.47 | 15.83 | 1.26 | 0 | 30.57 | 0.63 | 48.5238 | 6.08 | 7.15 | 8.38 | 8.99 | 10.66 | 10.66 | 10.66 | 15.83 | 15.83 | 19.97 | 0 | 0 | 0 | 0 | 0 | 1.26 | 2.28 | 4.07 | 11.19 | 13.34 | 15.02 | 15.02 | 28.33 | 630000 | 7200 | 493 | Ireland | County Tipperary | 3 | IE-TA
552 | Cahir | 0 | 5.75 | 12.71 | 9.25 | 0 | 27.71 | 0.4 | 69.275 | 5.53 | 5.53 | 6.17 | 6.17 | 6.74 | 6.74 | 7.5 | 8.11 | 10.95 | 13.02 | 0 | 0 | 0 | 0 | 0 | 2.49 | 12.83 | 19.72 | 20.67 | 20.67 | 24.85 | 26.76 | 27.71 | 400000 | 7000 | 552 | Ireland | County Tipperary | 2 | IE-TA
448 | Borrisokane | 0 | 9.03 | 4.52 | 0 | 0 | 13.55 | 0.35 | 38.7143 | 13 | 13 | 16.35 | 16.35 | 16.35 | 16.35 | 21.48 | 21.48 | 26.57 | 26.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57 | 1.15 | 3.48 | 350000 | 5400 | 448 | Ireland | County Tipperary | 3 | IE-TA
500 | Borrisoleigh | 0 | 7.05 | 3.68 | 6.05 | 3.91 | 20.69 | 0.33 | 62.697 | 0 | 2 | 2 | 2.47 | 3.36 | 4.18 | 5.64 | 7.8 | 7.8 | 15.09 | 0 | 0 | 8.46 | 9.96 | 12.45 | 13.64 | 13.64 | 15.35 | 15.35 | 15.35 | 15.35 | 15.35 | 20.69 | 330000 | 6400 | 500 | Ireland | County Tipperary | 2 | IE-TA
544 | Fethard | 0 | 4.36 | 11.45 | 1.65 | 0 | 17.46 | 0.29 | 60.2069 | 3.75 | 4.53 | 5.48 | 5.98 | 6.23 | 7.04 | 8.21 | 10.71 | 13.86 | 13.86 | 0 | 0 | 0 | 1.65 | 2.7 | 6.96 | 7.71 | 10.81 | 11.87 | 11.87 | 13.95 | 15.63 | 15.63 | 290000 | 5200 | 544 | Ireland | County Tipperary | 2 | IE-TA
590 | Tramore | 1.8 | 67.86 | 95.23 | 21.83 | 0 | 186.72 | 3.69 | 50.6016 | 4.36 | 4.91 | 6.84 | 7.37 | 8.41 | 8.85 | 10.21 | 10.21 | 13.87 | 20.89 | 0 | 0 | 0 | 11.23 | 20.25 | 20.25 | 55.26 | 80.88 | 96.15 | 96.15 | 112.97 | 150.09 | 185.41 | 3690000 | 25800 | 590 | Ireland | County Waterford | 2 | IE-WD
591 | Dungarvan | 0.09 | 12 | 21.91 | 140.55 | 25.02 | 199.57 | 1.45 | 137.6345 | 1.71 | 2.06 | 2.33 | 2.62 | 2.62 | 3.14 | 3.33 | 3.66 | 4.08 | 6.78 | 0 | 15.23 | 99.92 | 163.94 | 192.01 | 196.5 | 199.57 | 199.57 | 199.57 | 199.57 | 199.57 | 199.57 | 199.57 | 1450000 | 13800 | 591 | Ireland | County Waterford | 1 | IE-WD
577 | Waterford | 0.3 | 19.2 | 34.25 | 21.68 | 11.08 | 86.52 | 1.23 | 70.3415 | 1.3 | 2.18 | 2.95 | 3.74 | 4.21 | 4.72 | 5.38 | 6.65 | 8.46 | 15.67 | 0 | 11.08 | 23.91 | 34.57 | 48.53 | 62.22 | 65.99 | 65.99 | 73.2 | 73.2 | 80.5 | 80.5 | 86.52 | 1230000 | 19800 | 577 | Ireland | County Waterford | 2 | IE-WD
566 | Carrick-on-Suir | 0.27 | 8.98 | 23.8 | 38.29 | 0 | 71.34 | 0.8 | 89.175 | 2.8 | 3.52 | 3.52 | 3.95 | 3.95 | 4.34 | 4.7 | 5.33 | 6.51 | 10.86 | 0 | 0 | 2.52 | 25.26 | 51.88 | 60.26 | 63.3 | 65.66 | 68.92 | 68.92 | 71.34 | 71.34 | 71.34 | 800000 | 14200 | 566 | Ireland | County Waterford | 1 | IE-WD
597 | Dunmore East | 0.11 | 16.28 | 14.05 | 1.29 | 0 | 31.73 | 0.67 | 47.3582 | 6.94 | 7.83 | 8.65 | 10.08 | 12.13 | 12.13 | 12.13 | 16.2 | 16.2 | 25.18 | 0 | 0 | 0 | 0 | 0 | 0 | 2.31 | 5.34 | 8.3 | 10.3 | 11.52 | 15.56 | 22.76 | 670000 | 10400 | 597 | Ireland | County Waterford | 3 | IE-WD
573 | Portlaw | 0 | 7.34 | 17.23 | 1.49 | 0 | 26.07 | 0.49 | 53.2041 | 4.75 | 6.57 | 8.05 | 9.4 | 10.27 | 11.55 | 11.55 | 11.55 | 15.91 | 18.47 | 0 | 0 | 0 | 0 | 1.49 | 3.51 | 5.05 | 5.05 | 7.57 | 10.4 | 14.77 | 14.77 | 24.45 | 490000 | 6600 | 573 | Ireland | County Waterford | 2 | IE-WD
482 | Ballinacourty | 0 | 6.63 | 4.41 | 0 | 0 | 11.04 | 0.26 | 42.4615 | 8.5 | 8.95 | 11.73 | 11.73 | 17.45 | 17.45 | 17.45 | 17.45 | 27.63 | 27.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 1.5 | 2.78 | 2.78 | 4.89 | 260000 | 4800 | 482 | Ireland | County Waterford | 3 | IE-WD
579 | Lismore | 0 | 6.72 | 3.66 | 0 | 0 | 10.38 | 0.25 | 41.52 | 0 | 6.8 | 7.57 | 9.15 | 10.32 | 13.2 | 13.2 | 13.2 | 21.59 | 28.38 | 0 | 0 | 0 | 0 | 1.05 | 1.05 | 2.05 | 2.51 | 2.51 | 3.54 | 5.2 | 5.96 | 5.96 | 250000 | 5600 | 579 | Ireland | County Waterford | 3 | IE-WD
585 | Passage East | 0 | 5.08 | 4.15 | 1.28 | 0 | 10.52 | 0.23 | 45.7391 | 0 | 5.81 | 5.81 | 9.14 | 10.41 | 12.15 | 12.15 | 12.15 | 21.93 | 21.93 | 0 | 0 | 0 | 0 | 1.28 | 2.02 | 2.02 | 3.17 | 3.7 | 4.14 | 4.83 | 5.49 | 5.49 | 230000 | 5600 | 585 | Ireland | County Waterford | 3 | IE-WD
583 | Carriganore | 0 | 1.18 | 0 | 12.12 | 0 | 13.3 | 0.1 | 133 | 0 | 3.25 | 3.25 | 3.25 | 4.13 | 4.36 | 4.36 | 4.58 | 4.58 | 5.89 | 0 | 0 | 0 | 2.62 | 9.46 | 13.02 | 13.3 | 13.3 | 13.3 | 13.3 | 13.3 | 13.3 | 13.3 | 100000 | 1800 | 583 | Ireland | County Waterford | 1 | IE-WD
589 | Rossduff | 0 | 2.38 | 4.06 | 19.7 | 6.81 | 32.95 | 0.23 | 143.2609 | 0 | 0 | 2.4 | 2.4 | 2.86 | 2.86 | 3.48 | 3.73 | 4.32 | 5.57 | 0 | 0 | 14.78 | 26.51 | 30.57 | 32.95 | 32.95 | 32.95 | 32.95 | 32.95 | 32.95 | 32.95 | 32.95 | 230000 | 3000 | 589 | Ireland | County Waterford | 1 | IE-WD
592 | Garrynageragh | 0 | 6.9 | 4.36 | 1.84 | 0 | 13.1 | 0.27 | 48.5185 | 0 | 3.25 | 4.67 | 5.97 | 7.79 | 10.14 | 10.14 | 18.71 | 18.71 | 28.56 | 0 | 0 | 0 | 2.99 | 3.88 | 5.06 | 5.06 | 6.44 | 6.44 | 6.44 | 7.46 | 7.46 | 10.46 | 270000 | 6000 | 592 | Ireland | County Waterford | 3 | IE-WD
594 | Garrynageragh | 0 | 4.64 | 4.94 | 1.25 | 0 | 10.83 | 0.21 | 51.5714 | 0 | 4.25 | 4.48 | 5.43 | 6.37 | 7.25 | 8.24 | 12.16 | 12.16 | 12.16 | 0 | 0 | 0 | 0 | 3.28 | 3.91 | 5.59 | 6.04 | 6.93 | 6.93 | 7.84 | 8.4 | 8.4 | 210000 | 3400 | 594 | Ireland | County Waterford | 2 | IE-WD
367 | Mullingar | 1.51 | 45.78 | 84.94 | 269.13 | 51.2 | 452.57 | 4.13 | 109.5811 | 1.51 | 1.79 | 2.52 | 2.52 | 2.92 | 3.39 | 3.56 | 4.15 | 5.15 | 8.64 | 10.72 | 47.75 | 182.75 | 348.05 | 394.76 | 407.01 | 427.45 | 444.65 | 452.57 | 452.57 | 452.57 | 452.57 | 452.57 | 4130000 | 48400 | 367 | Ireland | County Westmeath | 1 | IE-WH
382 | Rochfortbridge | 0 | 9.35 | 4.26 | 0 | 0 | 13.61 | 0.32 | 42.5312 | 5.75 | 8.24 | 8.24 | 9.29 | 10.92 | 12.25 | 12.25 | 19.61 | 19.61 | 33.46 | 0 | 0 | 0 | 0 | 0 | 0.89 | 0.89 | 0.89 | 2.64 | 4.26 | 6.59 | 7.27 | 9.9 | 320000 | 6800 | 382 | Ireland | County Westmeath | 3 | IE-WH
358 | Delvin | 0 | 5.06 | 5.33 | 0 | 0 | 10.4 | 0.26 | 40 | 11 | 15.87 | 15.87 | 15.87 | 15.87 | 21.83 | 21.83 | 21.83 | 28.65 | 28.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.56 | 0.56 | 1.84 | 260000 | 6200 | 358 | Ireland | County Westmeath | 3 | IE-WH
347 | Castlepollard | 0 | 5.91 | 4.3 | 0 | 0 | 10.21 | 0.22 | 46.4091 | 0 | 6.5 | 6.81 | 8.77 | 8.77 | 8.77 | 12.41 | 16.95 | 16.95 | 16.95 | 0 | 0 | 0 | 0 | 0 | 0 | 2.39 | 2.39 | 4.07 | 4.07 | 4.07 | 6.72 | 8.04 | 220000 | 5800 | 347 | Ireland | County Westmeath | 3 | IE-WH
380 | Kinnegad | 0 | 2.01 | 2.69 | 8.68 | 0 | 13.38 | 0.15 | 89.2 | 0 | 0 | 3.25 | 3.25 | 3.25 | 3.25 | 3.52 | 4.07 | 5.28 | 7.4 | 0 | 0 | 0 | 9.59 | 11.37 | 11.79 | 11.79 | 12.56 | 12.56 | 12.56 | 13.38 | 13.38 | 13.38 | 150000 | 3600 | 380 | Ireland | County Westmeath | 1 | IE-WH
364 | Coolnahay | 0 | 1.21 | 3.56 | 5.83 | 9.87 | 20.47 | 0.13 | 157.4615 | 0 | 0 | 0 | 0 | 1.6 | 1.6 | 1.97 | 2.77 | 3.45 | 4.78 | 0 | 12.72 | 15.7 | 17.82 | 19.99 | 20.46 | 20.46 | 20.46 | 20.46 | 20.46 | 20.46 | 20.46 | 20.46 | 130000 | 3400 | 364 | Ireland | County Westmeath | 1 | IE-WH
478 | Stonehall | 0 | 0 | 2.64 | 8.46 | 7.95 | 19.05 | 0.09 | 211.6667 | 0 | 0 | 0 | 0 | 1.1 | 1.53 | 1.53 | 2.35 | 2.6 | 3.09 | 0 | 9.94 | 17.45 | 19.05 | 19.05 | 19.05 | 19.05 | 19.05 | 19.05 | 19.05 | 19.05 | 19.05 | 19.05 | 90000 | 2800 | 478 | Ireland | County Westmeath | 1 | IE-WH
582 | Wexford | 2.2 | 57.84 | 144.62 | 364.19 | 91.56 | 660.41 | 6.03 | 109.5207 | 1.85 | 2.22 | 2.41 | 2.64 | 2.8 | 3.16 | 3.42 | 3.94 | 4.85 | 8.22 | 0 | 41.48 | 295.5 | 499.15 | 586.5 | 604.75 | 629.98 | 659.63 | 660.41 | 660.41 | 660.41 | 660.41 | 660.41 | 6030000 | 32000 | 582 | Ireland | County Wexford | 1 | IE-WX
565 | Enniscorthy | 1.68 | 63.52 | 94.56 | 31.01 | 3.83 | 194.61 | 3.59 | 54.2089 | 2.98 | 3.82 | 5.06 | 5.88 | 6.36 | 8.02 | 8.95 | 11.84 | 11.84 | 20.02 | 0 | 0 | 17.52 | 34.13 | 40.85 | 71.11 | 82.19 | 108.97 | 126.56 | 126.56 | 154.36 | 154.36 | 194.54 | 3590000 | 34400 | 565 | Ireland | County Wexford | 2 | IE-WX
542 | Gorey | 0.3 | 41.43 | 86.53 | 92.23 | 25.18 | 245.68 | 3.02 | 81.351 | 1.82 | 2.15 | 2.68 | 3.11 | 3.93 | 4.34 | 4.86 | 5.94 | 7.65 | 10.49 | 0 | 31.09 | 74.55 | 122.13 | 157.77 | 195.56 | 204.54 | 219.13 | 219.13 | 219.13 | 245.68 | 245.68 | 245.68 | 3020000 | 28000 | 542 | Ireland | County Wexford | 1 | IE-WX
568 | New Ross | 0.53 | 38.99 | 38.74 | 164.9 | 20.12 | 263.28 | 2.69 | 97.8736 | 2.3 | 2.57 | 2.83 | 3.32 | 3.55 | 4.01 | 4.37 | 4.75 | 5.39 | 10.61 | 0 | 0 | 58.64 | 137.56 | 214.46 | 223.64 | 240.87 | 240.87 | 255.8 | 255.8 | 263.28 | 263.28 | 263.28 | 2690000 | 26000 | 568 | Ireland | County Wexford | 1 | IE-WX
549 | Riverchapel | 0 | 24.32 | 29.81 | 10.44 | 0 | 64.57 | 1.28 | 50.4453 | 4.87 | 6.05 | 6.79 | 8.28 | 9.01 | 11.34 | 11.34 | 14.92 | 14.92 | 18.76 | 0 | 0 | 0 | 0 | 3.66 | 9.2 | 14.96 | 23.19 | 24.76 | 27.8 | 37.49 | 50.83 | 60.01 | 1279999.99 | 12000 | 549 | Ireland | County Wexford | 2 | IE-WX
598 | Rosslare Harbour | 0 | 4.87 | 17.68 | 53.61 | 0 | 76.15 | 0.68 | 111.9853 | 3.09 | 3.09 | 3.59 | 3.95 | 3.95 | 4.53 | 4.53 | 5.11 | 5.59 | 7.2 | 0 | 0 | 2.67 | 28.02 | 53.61 | 70.7 | 73.77 | 75.03 | 76.16 | 76.16 | 76.16 | 76.16 | 76.16 | 680000 | 8600 | 598 | Ireland | County Wexford | 1 | IE-WX
575 | Castlebridge | 0 | 13.58 | 14.48 | 3.7 | 0 | 31.76 | 0.65 | 48.8615 | 4.25 | 6.1 | 7.3 | 8.33 | 9.64 | 10.5 | 10.5 | 14.95 | 14.95 | 20.48 | 0 | 0 | 0 | 0 | 2.26 | 4.81 | 5.67 | 8.77 | 11.61 | 14.43 | 16.09 | 23.22 | 23.22 | 650000 | 10800 | 575 | Ireland | County Wexford | 3 | IE-WX
593 | Rosslare Harbour | 0 | 13.41 | 8.47 | 7.61 | 0 | 29.48 | 0.62 | 47.5484 | 3.75 | 4.2 | 5.31 | 5.96 | 7.52 | 8.7 | 9.15 | 11.41 | 11.41 | 17.78 | 0 | 0 | 0 | 2.54 | 6.4 | 10.39 | 10.39 | 14.37 | 17.07 | 17.94 | 20.92 | 20.92 | 26.91 | 620000 | 9800 | 593 | Ireland | County Wexford | 3 | IE-WX
541 | Bunclody | 0 | 15.32 | 9.07 | 0 | 0 | 24.39 | 0.6 | 40.65 | 7.5 | 8.19 | 9.49 | 11.35 | 14.21 | 14.21 | 14.21 | 23.99 | 23.99 | 23.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.81 | 5.07 | 7.75 | 9.53 | 12.06 | 12.06 | 600000 | 11800 | 541 | Ireland | County Wexford | 3 | IE-WX
551 | Ferns | 0 | 10.74 | 7.89 | 0 | 0 | 18.64 | 0.44 | 42.3636 | 13 | 14.59 | 14.59 | 16.3 | 16.3 | 16.3 | 20.04 | 20.04 | 20.04 | 26.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.39 | 6.81 | 440000 | 5800 | 551 | Ireland | County Wexford | 3 | IE-WX
586 | Whitechurch | 0 | 5.63 | 4.51 | 0 | 0 | 10.14 | 0.27 | 37.5556 | 11 | 13.22 | 15.56 | 15.56 | 19.64 | 19.64 | 25.11 | 25.11 | 25.11 | 25.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.64 | 1.44 | 4.96 | 270000 | 4600 | 586 | Ireland | County Wexford | 3 | IE-WX
553 | Ballycanew | 0 | 4.72 | 2.57 | 2.88 | 0 | 10.16 | 0.21 | 48.381 | 0 | 6.5 | 7.38 | 7.91 | 8.49 | 10.19 | 10.19 | 10.19 | 10.19 | 21.27 | 0 | 0 | 0 | 0 | 0 | 0 | 1.61 | 3.83 | 4.72 | 5.45 | 5.85 | 5.85 | 5.85 | 210000 | 4200 | 553 | Ireland | County Wexford | 3 | IE-WX
477 | Monmore | 0 | 0.71 | 10.15 | 14.71 | 0 | 25.57 | 0.24 | 106.5417 | 0 | 4.25 | 4.25 | 4.44 | 4.44 | 4.81 | 4.81 | 5.2 | 5.62 | 6.16 | 0 | 0 | 0 | 0 | 14.71 | 23.83 | 25.57 | 25.57 | 25.57 | 25.57 | 25.57 | 25.57 | 25.57 | 240000 | 4600 | 477 | Ireland | County Wexford | 1 | IE-WX
584 | Carrickbyrne | 0 | 0.77 | 1.95 | 8.54 | 3.25 | 14.51 | 0.1 | 145.1 | 0 | 0 | 2.4 | 2.4 | 2.78 | 3.05 | 3.38 | 3.38 | 4.11 | 4.46 | 0 | 0 | 5.88 | 11.79 | 13.74 | 13.74 | 14.51 | 14.51 | 14.51 | 14.51 | 14.51 | 14.51 | 14.51 | 100000 | 2000 | 584 | Ireland | County Wexford | 1 | IE-WX
459 | Bray | 3.9 | 57.77 | 233.84 | 288.86 | 136.67 | 721.04 | 6.97 | 103.4491 | 1.51 | 1.88 | 2.33 | 2.93 | 3.2 | 3.69 | 4.07 | 4.38 | 5.33 | 8.78 | 0 | 108.92 | 278.91 | 419.4 | 614.86 | 666 | 683.08 | 708.4 | 721.04 | 721.04 | 721.04 | 721.04 | 721.04 | 6969999.99 | 29600 | 459 | Ireland | County Wicklow | 1 | IE-WW
471 | Greystones | 0.7 | 66.41 | 140.39 | 55.29 | 13.85 | 276.63 | 4.29 | 64.4825 | 2.95 | 3.36 | 4.08 | 4.66 | 5.65 | 6.16 | 7.33 | 8.05 | 10.33 | 17.21 | 0 | 0 | 25.56 | 63.42 | 93.5 | 132.54 | 177.71 | 187.51 | 201.01 | 201.01 | 232.34 | 259.24 | 276.63 | 4290000 | 41800 | 471 | Ireland | County Wicklow | 2 | IE-WW
504 | Wicklow | 0.87 | 50.99 | 122.22 | 75.46 | 7.49 | 257.04 | 3.81 | 67.4646 | 3.27 | 3.78 | 4.35 | 5.25 | 5.8 | 6.43 | 7.06 | 8.46 | 10.03 | 16.19 | 0 | 0 | 6.82 | 45.13 | 81.95 | 124.07 | 166.89 | 182.44 | 199.77 | 199.77 | 220.72 | 243.68 | 257.04 | 3810000 | 34800 | 504 | Ireland | County Wicklow | 2 | IE-WW
530 | Arklow | 1.24 | 35.58 | 85.18 | 211.39 | 43.22 | 376.62 | 3.58 | 105.2011 | 1.1 | 2.31 | 2.76 | 3.1 | 3.48 | 3.96 | 4.34 | 4.74 | 5.66 | 9.25 | 20.85 | 47.06 | 99.48 | 222.69 | 309.67 | 335.54 | 356.85 | 369.51 | 369.51 | 376.62 | 376.62 | 376.62 | 376.62 | 3580000 | 24400 | 530 | Ireland | County Wicklow | 1 | IE-WW
456 | Blessington | 0.82 | 21.56 | 42.09 | 8.68 | 0 | 73.15 | 1.3 | 56.2692 | 4.75 | 5.11 | 5.66 | 6.55 | 6.93 | 7.8 | 9.36 | 11.33 | 11.33 | 20.58 | 0 | 0 | 0 | 0 | 10.94 | 19.42 | 32.43 | 41.34 | 45.69 | 50.98 | 58.32 | 58.32 | 72.99 | 1300000 | 12400 | 456 | Ireland | County Wicklow | 2 | IE-WW
479 | Kilcoole | 0 | 9.37 | 41.38 | 2.53 | 13.48 | 66.75 | 0.86 | 77.6163 | 0 | 0.9 | 2.16 | 3.14 | 4.55 | 4.55 | 5.88 | 6.52 | 7.58 | 10.55 | 9.83 | 16.01 | 17.14 | 27.14 | 32.87 | 44.95 | 50.67 | 55.83 | 55.83 | 62.4 | 64.82 | 66.75 | 66.75 | 860000 | 9600 | 479 | Ireland | County Wicklow | 1 | IE-WW
499 | Baltinglass | 0 | 18.38 | 11.53 | 1.39 | 0 | 31.3 | 0.72 | 43.4722 | 6.92 | 8.18 | 9.25 | 10.69 | 11.32 | 11.32 | 15.82 | 15.82 | 21.78 | 30.86 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 3.15 | 5.26 | 9.43 | 12.86 | 12.86 | 19.15 | 720000 | 12000 | 499 | Ireland | County Wicklow | 3 | IE-WW
480 | Newtownmountkennedy | 0 | 10.83 | 12.81 | 10.02 | 4.78 | 38.44 | 0.57 | 67.4386 | 0 | 2.56 | 3.33 | 3.33 | 5.19 | 5.49 | 7.41 | 8.64 | 13.86 | 13.86 | 0 | 4.78 | 7.5 | 11.14 | 15.88 | 20.27 | 25.72 | 26.74 | 28.74 | 28.74 | 28.74 | 34.48 | 34.48 | 570000 | 10200 | 480 | Ireland | County Wicklow | 2 | IE-WW
513 | Rathdrum | 0 | 13.76 | 7.88 | 1.74 | 0 | 23.38 | 0.56 | 41.75 | 7.5 | 9.12 | 11.09 | 11.09 | 17.06 | 17.06 | 17.06 | 17.06 | 26.05 | 34.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.74 | 3.18 | 5.43 | 6.61 | 6.61 | 11.58 | 560000 | 11200 | 513 | Ireland | County Wicklow | 3 | IE-WW
521 | Aughrim, County Wicklow | 0 | 8.43 | 13.26 | 1.62 | 0 | 23.3 | 0.47 | 49.5745 | 0 | 8.59 | 9.26 | 11.17 | 11.17 | 13.82 | 13.82 | 16.19 | 16.19 | 21.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.34 | 4.52 | 5.34 | 7.99 | 13.05 | 16.56 | 470000 | 7800 | 521 | Ireland | County Wicklow | 3 | IE-WW
462 | Enniskerry | 0 | 12.29 | 4.79 | 0 | 0 | 17.09 | 0.46 | 37.1522 | 10.18 | 14.14 | 14.14 | 18.94 | 18.94 | 18.94 | 30.36 | 30.36 | 30.36 | 30.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68 | 1.74 | 2.9 | 5.2 | 460000.01 | 11000 | 462 | Ireland | County Wicklow | 3 | IE-WW
537 | Carnew | 0 | 8.15 | 5.65 | 0 | 0 | 13.79 | 0.37 | 37.2703 | 0 | 8.5 | 9.75 | 9.75 | 14.26 | 14.26 | 14.26 | 25.66 | 25.66 | 25.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.92 | 3.98 | 3.98 | 5.65 | 5.65 | 370000 | 8000 | 537 | Ireland | County Wicklow | 3 | IE-WW
524 | Tinahely | 0 | 8.86 | 3.02 | 0 | 0 | 11.89 | 0.35 | 33.9714 | 13.97 | 13.97 | 13.97 | 22.19 | 22.19 | 29.2 | 29.2 | 29.2 | 29.2 | 29.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99 | 0.99 | 350000 | 7800 | 524 | Ireland | County Wicklow | 3 | IE-WW
483 | Roundwood | 0 | 5.26 | 6.03 | 0 | 0 | 11.3 | 0.26 | 43.4615 | 0 | 8.5 | 8.95 | 10.9 | 10.9 | 10.9 | 16.93 | 16.93 | 22.08 | 22.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.02 | 3.56 | 4.22 | 4.22 | 7.38 | 260000 | 5000 | 483 | Ireland | County Wicklow | 3 | IE-WW
473 | Dunlavin | 0 | 5.32 | 5.53 | 0 | 0 | 10.85 | 0.25 | 43.4 | 9.5 | 9.5 | 10.66 | 11.25 | 11.25 | 15.94 | 15.94 | 23.14 | 23.14 | 23.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.71 | 3.61 | 3.61 | 5.48 | 250000 | 4400 | 473 | Ireland | County Wicklow | 3 | IE-WW
466 | Kilmacanogue | 0 | 4.41 | 6.57 | 2.65 | 0 | 13.63 | 0.24 | 56.7917 | 0 | 3.75 | 3.75 | 5.98 | 6.98 | 7.6 | 9.69 | 12.36 | 12.36 | 17.87 | 0 | 0 | 0 | 2.65 | 2.65 | 5 | 6.24 | 6.96 | 6.96 | 8.71 | 8.71 | 10.55 | 13.63 | 240000 | 3800 | 466 | Ireland | County Wicklow | 2 | IE-WW
503 | Ashford | 0 | 3.27 | 7.01 | 0 | 0 | 10.28 | 0.2 | 51.4 | 0 | 4.75 | 6.1 | 6.59 | 7.35 | 7.35 | 11.97 | 11.97 | 17.75 | 17.75 | 0 | 0 | 0 | 0 | 1.2 | 2.18 | 3.85 | 4.36 | 4.36 | 4.36 | 7.01 | 7.01 | 8.83 | 199999.99 | 3800 | 503 | Ireland | County Wicklow | 2 | IE-WW
531 | Shillelagh | 0 | 2.8 | 0.65 | 3.99 | 5.52 | 12.95 | 0.13 | 99.6154 | 0 | 0 | 0 | 0 | 1.6 | 1.6 | 1.6 | 4.12 | 4.12 | 8.99 | 0 | 5.52 | 5.52 | 9.5 | 10.15 | 10.15 | 10.15 | 10.15 | 11.74 | 11.74 | 11.74 | 11.74 | 12.95 | 130000 | 3000 | 531 | Ireland | County Wicklow | 1 | IE-WW
421 | Dublin | 143.13 | 1650.48 | 7096.38 | 10230.39 | 1869.86 | 20990.24 | 223.29 | 94.0044 | 1.83 | 2.2 | 2.43 | 2.7 | 3.13 | 3.44 | 3.86 | 4.12 | 4.95 | 8.5 | 107.66 | 1000.05 | 8890.5 | 14674.02 | 18668.11 | 19551.66 | 20660.97 | 20921.55 | 20990.24 | 20990.24 | 20990.24 | 20990.24 | 20990.24 | 223289999.88 | 535800 | 421 | Ireland |  | 0 | IE-D
599 | Cork | 28.96 | 427.46 | 1164.17 | 2258.14 | 712.47 | 4591.21 | 45.84 | 100.1573 | 1.44 | 2 | 2.24 | 2.5 | 2.94 | 3.29 | 3.71 | 3.97 | 5.01 | 8.86 | 10.07 | 824.74 | 2277.75 | 3440.29 | 4092.18 | 4371.21 | 4371.21 | 4574.62 | 4591.22 | 4591.22 | 4591.22 | 4591.22 | 4591.22 | 45840000 | 158800 | 599 | Ireland |  | 0 | IE-CO
492 | Limerick | 12.79 | 176.71 | 711 | 1178.75 | 258.14 | 2337.38 | 22.95 | 101.8466 | 1.85 | 2.14 | 2.55 | 2.77 | 3.23 | 3.45 | 3.98 | 4.29 | 5.16 | 8.19 | 0 | 172.23 | 839.74 | 1598.48 | 1991.83 | 2172.65 | 2253.82 | 2336.26 | 2337.38 | 2337.38 | 2337.38 | 2337.38 | 2337.38 | 22950000 | 95200 | 492 | Ireland |  | 0 | IE-LK
363 | Galway | 8.41 | 136.11 | 560.27 | 1439.43 | 438.29 | 2582.51 | 21 | 122.9767 | 1.39 | 1.66 | 2.17 | 2.44 | 2.64 | 3.09 | 3.49 | 3.78 | 4.41 | 6.92 | 10.62 | 528.28 | 1322.1 | 1984.75 | 2447.09 | 2508.47 | 2582.51 | 2582.51 | 2582.51 | 2582.51 | 2582.51 | 2582.51 | 2582.51 | 21000000 | 98200 | 363 | Ireland |  | 0 | IE-G
578 | Waterford | 3.27 | 82.48 | 243.66 | 778.08 | 279.05 | 1386.54 | 10.8 | 128.3833 | 1.29 | 1.63 | 2.05 | 2.25 | 2.45 | 2.64 | 3.04 | 3.3 | 3.81 | 6.33 | 9.6 | 165.58 | 842.46 | 1194.74 | 1317.43 | 1376.8 | 1386.54 | 1386.54 | 1386.54 | 1386.54 | 1386.54 | 1386.54 | 1386.54 | 10800000 | 53600 | 578 | Ireland |  | 0 | IE-WD

## 40 Comp. hp, airsource 10 MW
Technology |  | Heat pump, air source - heat pump - electricity - large
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 10 | 10 | 10 | 10 | 10 | 5 | 20 | 5 | 20
| Heat efficiency (net, annual average) [] | 380% | 380% | 385% | 390% | 390% | 360% | 400% | 360% | 410% | [A, A1, B, D] | [1, 14, 15]
| Heat efficiency (net, name plate) [] | 350% | 350% | 355% | 360% | 360% | 330% | 370% | 330% | 380% | [A, A1, B, C] | [1, 14, 15]
| Auxiliary Electricity consumption (share of heat gen.) [] | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | E | [1, 14, 15]
| Forced outage [] | 0% | 0% | 0% | 0% | 0% | 0% | 5% | 0% | 5% |  | [1, 14, 15]
| Planned outage [weeks per year] | 1 | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | [1, 14, 15]
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 | 15 | 40 | 15 | 40 |  | [1, 9, 10, 14, 15]
| Construction time [years] | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.5 | 1 | 0.4 | 1 | [F, G] | [9, 14, 15]
| Space requirement [1000 m2/MW_h] | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 1 | 0.4 | 1 | Q | [15, 18]
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 5% | 5% | 5% | 5% | 5% | 5% | 100% | 5% | 100% | H | [1, 9, 14, 15]
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 100% | 10% | 100% | H | [1, 9, 14, 15]
| Minimum load (of full load) [] | 25% | 25% | 25% | 25% | 25% | 10% | 50% | 10% | 50% | [H, J] | [1, 9, 14, 15]
| Warm start-up time [hours] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.2 | H | [9, 14, 15]
| Cold start-up time [hours] | 1 | 1 | 1 | 1 | 1 | 0.2 | 1 | 0.2 | 1 | [H, I] | [9, 14, 15]
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 0.86 | 0.86 | 0.76 | 0.76 | 0.76 | 0.67 | 1.14 | 0.67 | 1.14 | [A, K, L, P, Q] | [1, 14, 15]
| Nominal investment (equipment) [2015-MEUR/MW_h] | 0.68 | 0.68 | 0.61 | 0.61 | 0.61 | 0.53 | 0.91 | 0.53 | 0.91 | A | [1, 14, 15]
| Nominal investment (grid connection) [2015-MEUR/MW_e] | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.01 | 0.11 | 0.01 | 0.11 | K | [1, 14, 15]
| Nominal investment (installation) [2015-MEUR/MW_h] | 0.15 | 0.15 | 0.14 | 0.14 | 0.14 | 0.12 | 0.11 | 0.12 | 0.11 | A | [1, 14, 15]
| Variable O&M (*total) [2015-EUR/MWh_h] | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1 | 2.69 | 1 | 2.69 |  | [1, 14, 15]
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [E, N] | [1, 14, 15]
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.5 | 2.69 | 1.5 | 2.69 | M | [1, 14, 15]
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 2000 | 2000 | 2000 | 2000 | 2000 | 1000 | 3000 | 1000 | 5000 | M | [1, 14, 15]
| Startup cost [2015-EUR/MW_h/startup] | 10 | 10 | 10 | 10 | 10 | 5 | 20 | 2 | 20 | O | 15
Notes:
A. Actual development within COP optimization and reduced investment cost depends on the development in fuel and electricity prices.
A1. Performance data regarding ambient air and industrial waste heat are based on typical supply temperatures of decentral district heating systems with an annual average return/forward temperature of 35 °C / 70 °C (it varies over the year). It is assumed that the heat pumps only cover 85 % of the annual heat demand, meaning that the heat pumps co-produce with peak load units during the coldest periods. This mean that the forward temperature of the heat pump can be kept at around 70 °C during the coldest periods or even lowered.
B. Includes energy consumption for defrosting and auxiliary electricity consumption.
C. Total efficiency, net (%), name plate is at an ambient temperature of -1 °C. District heating temperatures are 35 °C return and 70 °C forward.
D. Annual average at 85 % heat production of total demand utilizing coproduction at peak demands with reduced output temperatur from heat pump. DH temperatures are 35 °C return and 70 °C forward.
E. Auxiliary electricity consumption is included in the Total efficiency. Electricity for fans constitute appr. 0.3 %. Cost for electricity is therefore not accounted for in variable O&M
F. Does not include tendering and regulatory approvals.
G. The development within construction time will depend on future production figures and standardization of plants.
H. The regulation ablility will depend on the future markets for regulation services.
I. Cold start of time is starting a heat pump where stand by heating has not been applied
J. Operation at part load will usually increase COP but also variable O&M costs
K. It is assumed that heat pumps is connected with limited access like electrical boilers. Upper values regarding uncertainty assume that installations must pay for full access
L. Land is usually owned by the company
M. O&M regard the heat pump it self including auxiliary equipment, building etc. for the heat pump. The costs does not include O&M for the entire district heating network, peak load or back up units, administration regarding end users etc.
N. All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M
O. 1/4 MWh-heat per MW is lost during startup
P. At district heating temperatures of 40-80 °C, the specific investment is expected to increase by 5 % as compontents must be rated for higher pressure levels
Q. Including land for air coolers
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Støchkel, Paaske, Clausen, 2017, see https://ens.dk/sites/ens.dk/files/Varme/drejebog_for_store_varmepumper.pdf
2. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Sørensen, Paaske, Jacobsen, Hofmeister, 2013
3. Absorption chillers and heat pumps, Keith E. Herold, Reinhard Radermacher and Sanford A. Klein, 1996
4. Scandinavian Energy Group, 2015, Conversation
5. Advansor, 2015, Conversation
6. Hybrid Energi, 2015, Conversation
7. Innoterm, 2015, Conversation
8. Cronborg, 2015, Conversation
9. Johnson Controls, 2019, Conversation
10. Teknologisk Institut, 2015, 2019, Conversation
11. Energinet.dk, 2015, Conversation
12. IEA 2012, Energy Technology Perspectives, 2012
13. Store varmepumper i fjernvarmen - driftserfaringer, Flørning, Carøe, Nielsen, Støchkel, 2019
14. IES/Victor DST, 2019, Conversation
15. PlanEnergi, 2019, practical experience from installed plants
16. DMI, 2019
17. Danfoss, 2019, Conversation
18. Varmeværket Bjerringbro, Vejen Varmeværk, Skjern Papirfabrik, Høje Taastrup Fjernvarme, Rødkærsbro Kraftvarmeværk, Kalundborg Forsyning, Rye Kraftvarmeværk, Broager Fjernvarmeselskab, Sig Varmeværk, Fensmark Fjernvarme, Slagslunde Fjernvarme, Farum Fjernvarme, FFV Energi & Miljø, Karup Varmeværk, Støvring Kraftvarmeværk, Skagen Varmeværk, Strandby Varmeværk

## 41 Electric boiler, large
Technology |  | Electric boiler - boiler - electricity - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2030 | 2030 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 5 | 5 | 5 | 5 | 1 | 25 |  |  | 1 | 25
| Heat efficiency (net, name plate) [] | 98% | 99% | 99% | 99% | 98% | 99% |  |  | 99% | 99%
| Heat efficiency (net, annual average) [] | 98% | 99% | 99% | 99% | 98% | 99% |  |  | 99% | 99%
| Auxiliary Electricity consumption (share of heat gen.) [] | 0.5% | 0.5% | 0.5% | 0.5% | 0.1% | 0.5% |  |  | 0.1% | 0.5%
| Forced outage [] | 1% | 1% | 1% | 1% | 0.5% | 1% |  |  | 0.5% | 1%
| Planned outage [weeks per year] | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  | 0.2 | 0.2
| Technical lifetime [years] | 20 | 20 | 20 | 20 | 20 | 20 |  |  | 20 | 20
| Construction time [years] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 |  |  | 0.5 | 1
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 100% | 100% | 100% | 100% | 100% | 100% |  |  | 100% | 100%
| Secondary regulation (of full load, per minute) [] | 100% | 100% | 100% | 100% | 100% | 100% |  |  | 100% | 100%
Minimum load (of full load) [] | bar: ctrl to upper; lower to upper
| Warm start-up time [hours] | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 |  |  | 0.01 | 0.01
| Cold start-up time [hours] | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 |  |  | 0.08 | 0.08
Environment
SO2 [g/GJ_i]
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 0.07 | 0.07 | 0.06 | 0.06 | 0.02 | 0.17 |  |  | 0.02 | 0.17
| Nominal investment (equipment) [2015-MEUR/MW_h] | 0.06 | 0.06 | 0.05 | 0.05 | 0.02 | 0.14 |  |  | 0.02 | 0.14
| Nominal investment (installation) [2015-MEUR/MW_h] | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0.03 |  |  | 0 | 0.03
| Variable O&M (*total) [2015-EUR/MWh_h] | 0.8 | 0.9 | 1 | 1 | 0.5 | 0.9 |  |  | 0.5 | 1
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 0.3 | 0.3 | 0.5 | 0.6 | 0.1 | 0.3 |  |  | 0.1 | 0.6
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 0.5 | 0.5 | 0.5 | 0.4 | 0.4 | 0.5 |  |  | 0.3 | 0.5
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 1100 | 1070 | 1020 | 920 | 1000 | 1100 |  |  | 900 | 1000
Technology-specific data
| Startup cost [2015-EUR/MW_h/startup] | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Notes:
A. The investment and O&M costs are assessed in relation to an approx. operation in 500 hours/year.
B. The installation at low voltage necessitates a transformer substation & expansion of the distribution board. Costs for these are included in the stated equipment costs.
C. Electrode boilers at medium-high voltage are directly connected to the distribution grid. Costs for the distribution board are included in the equipment costs.
D. The installation costs include costs for electrical integration & grid connection fees.
E. The forced outage of electric boilers is very limited and typically well below 1 %. The planned outage is typically limited to 1 day/year.
F. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Tjæreborg Industri, 2016
2. Parat, unknown date, Brochure High Voltage Electrode Boiler, available at http://parat.no/media/201154/Electrode-Boiler-web.pdf

## 44 Natural Gas DH Only
Technology |  | Gas boiler - boiler - natural gas - medium
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | lower: 0.5; upper: 10; lower: 0.5; upper: 10
| Heat efficiency (net, annual average) [] | 103% | 103% | 104% | 104% | 93% | 105% | 94% | 106% | B | [1, 3]
| Heat efficiency (net, name plate) [] | 105% | 105% | 106% | 106% | 95% | 107% | 96% | 108% | A | [1, 2, 3]
| Auxiliary Electricity consumption (share of heat gen.) [] | 0.15% | 0.14% | 0.12% | 0.1% | 0.13% | 0.2% | 0.08% | 0.15% | L | 1
| Forced outage [] | 1% | 1% | 1% | 1% | 0.08% | 2% | 0.08% | 2% |  | 3
| Planned outage [weeks per year] | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.6 | 0.3 | 0.6 | F | 3
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 |  | 25 |  | K | 3
| Construction time [years] | 0.5 | 0.5 | 0.5 | 0.5 | 0.2 | 0.7 | 0.2 | 0.7 | F | 9
| Space requirement [1000 m2/MW_h] | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0.01 | E | 2
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: note
Secondary regulation (of full load, per minute) [] | bar: note
| Minimum load (of full load) [] | 15% | 15% | 15% | 15% | 10% | 20% | 10% | 20% |  | 9
| Warm start-up time [hours] | 0.1 | 0.1 | 0.1 | 0.1 | 0.08 | 0.15 | 0.08 | 0.15 | D | 9
| Cold start-up time [hours] | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.5 | 0.3 | 0.5 | D | 9
Environment
| SO2 [g/GJ_i] | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0.3 | 0 | 0.3 | H | 1
| NOX [g/GJ_i] | 10 | 9 | 7 | 6 | 8 | 60 | 5 | 30 |  | [1, 2]
| CH4 [g/GJ_i] | 3 | 3 | 2 | 2 | 2 | 6 | 2 | 6 |  | [1, 2]
| N2O [g/GJ_i] | 1 | 1 | 1 | 1 |  |  |  |  | I | 7
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 0.06 | 0.06 | 0.05 | 0.05 | 0.04 | 0.25 | 0.04 | 0.25 | J | [2, 3]
| Nominal investment (equipment) [2015-MEUR/MW_h] | 0.04 | 0.04 | 0.03 | 0.03 | 0.03 | 0.15 | 0.03 | 0.15 |  | [2, 3]
| Nominal investment (installation) [2015-MEUR/MW_h] | 0.02 | 0.02 | 0.02 | 0.02 | 0.01 | 0.1 | 0.01 | 0.1 |  | [2, 3]
| Variable O&M (*total) [2015-EUR/MWh_h] | 1.1 | 1.1 | 1 | 1 | 0.6 | 2.1 | 0.6 | 2.2
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | L
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 1 | 1 | 0.9 | 0.9 | 0.5 | 2 | 0.5 | 2 |  | [8, 9]
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 2000 | 1950 | 1900 | 1700 | 1000 | 2500 | 1000 | 2500 | F
Notes:
A. Includes a condensing economizer, without economizer the efficiency will be up to some 93-97 %, LHV reference
B. Includes a condensing economizer, without economizer the efficiency will be up to some 92-95 %, LHV reference
C. Not Relevant for heat-only technologies
D. Boilers with low water content (e.g. watertube instaed of shell tube 3-5 pass boilers) are used start up time from cold is shorter
E. Boilers in the low power range approx. 0.010 and boilersin the higher power range 0.003
F. DGC Estimate
G. Ultra Low NOx burners can reach a level of 5 g/GJ
H. Fuel dependent , not tecchnology dependent
I. No data available
J. The average numbers are for a 2- 3 MW boiler installation
K. Technical lifetime often exceeds 25 years
L. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. DGC efficiency and emission test reports from district heating boilers, 2014
2. Burner and boiler manufacturer informations, 2015
3. Danish District Heating Association, data from a 2012 survey for the report
7. National Environmental Research Institute, Denmark 2009
8. Elsam/Elkraft update "Teknologidata for el- og varmeproduktionsanlæg", 1997
9. DGC calculations, estimates

## 45.2.a Geothermal DH, 1200m, A
Technology |  | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 22.66 | 22.47 | 22.3 | 22.12 | 21.95 | 38.56 | 8.56 | 38.56 | 8.56 | [I, A] | [1, 2]
| Heat efficiency (net, annual average) [] | 165.1% | 166% | 166.9% | 167.8% | 168.7% | 172.3% | 164.4% | 179.4% | 170.9% | AG
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.076% | 2.093% | 2.11% | 2.127% | 2.143% | 0.8237% | 3.701% | 0.8237% | 3.701% | B | [2, 3, 4]
| Forced outage [] | 2% | 2% | 2% | 2% | 2% | 1% | 3% | 1% | 3% |  | 5
| Planned outage [weeks per year] | 2 | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 |  | 5
| Technical lifetime [years] | 25 | 25 | 30 | 30 | 30 | 25 | 30 | 25 | 35 |  | 5
| Construction time [years] | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 5 | 3 | 5 |  | 5
| Space requirement [1000 m2/MW_h] | 5 | 5 | 5 | 5 | 5 | 3 | 7 | 3 | 7 | D | 5
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: note
Secondary regulation (of full load, per minute) [] | bar: note
| Minimum load (of full load) [] | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | H | [2, 5]
Warm start-up time [hours]
| Cold start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 3
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 1.26 | 1.23 | 1.19 | 1.15 | 1.12 | 0.74 | 1.88 | 0.69 | 1.74 | [C, K] | [2, 4, 7]
| Nominal investment (equipment) [2015-MEUR/MW_h] | 0.77 | 0.75 | 0.73 | 0.71 | 0.68 | 0.43 | 1.16 | 0.39 | 1.05 |  | [2, 4]
| Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | 0.23 | 0.22 | 0.22 | 0.21 | 0.2 | 0.16 | 0.33 | 0.16 | 0.33 | [J, K]
| Nominal investment (installation) [2015-MEUR/MW_h] | 0.26 | 0.25 | 0.24 | 0.24 | 0.23 | 0.15 | 0.4 | 0.13 | 0.36 |  | [2, 4]
| Variable O&M (*total) [2015-EUR/MWh_h] | 2.08 | 2.11 | 2.14 | 2.13 | 2.11 | 2.07 | 2.07 | 2.03 | 2.03 | FJ | 2
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 2.08 | 2.11 | 2.14 | 2.13 | 2.11 | 2.07 | 2.07 | 2.03 | 2.03 | F
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 11100 | 10800 | 10500 | 10100 | 9800 | 10800 | 10800 | 9800 | 9800 | [E, J] | [1, 3, 2]
Technology-specific data
| Number of injection wells | 4 | 4 | 4 | 4 | 4 | 3 | 2 | 3 | 2 | [L, N] | 1
| Number of production wells | 2 | 2 | 2 | 2 | 2 | 3 | 1 | 3 | 1 | [L, N] | 1
| Heat pump SCOP (net, annual average) [] | 171% | 172% | 173% | 174% | 175% | 172% | 172% | 175% | 175% | [A, N]
| Heat generation from heat pumps [MW_h] | 13.25 | 13.07 | 12.89 | 12.71 | 12.54 | 22.06 | 4.89 | 21.17 | 4.69 | A | 1
| Heat generation from geothermal ressource [MW_h] | 9.41 | 9.41 | 9.41 | 9.41 | 9.41 | 15.88 | 3.52 | 15.88 | 3.52 | [I, A, L, N] | 1
| Depth of geothermal well [m] | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 |  | 1
Notes:
A. No part of the geothermal heat is transferred directly to DH water. 100% heat source for the heat pump. Heat pump according to Ch. 40.
B. The total electricity demand for submerged pumps / reinjection pumps etc. This will vary according to reservoir properties. Lower / upper case considers variations.
C. Includes CAPEX for the heat pump. Does not include project development costs e.g. initial screening, seismic survey, and geological model, estimated to 1,5-3 MEUR/site (based on 1;4 and Ref. [10]). A well cost of 1800 EUR/m is assumed.
D. This will vary with the design. Requirements are usually higher during construction phase. In case of vertical injection wells a horizontal offset in the range of 1-2 km for the injection wells is necessary
E. Replacement of submersible pump(s), approx. once every five years, operation staff. Heat pump fixed O&M included, as per see datasheets in Chapter 40 Heat pumps.
F. Include maintenance of filters and wells (chemical treatment)
G. Total efficiency is calculated as heat output divided by energy input. Energy input is input to heat pump and auxiliary electricity to pumps etc.
H. A geothermal plant is intended for continuous operation. Electric heat pumps may provide some of regulation though, e.g. in connection with a heat storage.
I. Uncertainty does not consider the risk of not finding a suitable reservoir.
J. Including heat pump nominal investment and O&M costs - re.datasheets in chapter 40 Heat pumps
K. The base for the specific investment is the heat generation capacity for one unit including heat pumps.
L. Lower / upper cases considers variations in the plant size in terms of numbers of wells.
M. Auxiliary electricity consumption is included in the total efficiency. Can be calculated separately based on the figure above.
N. Temperature of geothermal heat is 44/17 (°C source/return). Temperature of DH water is 80/40 (°C source/return)
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. PlanEnergi, GEUS, 2019
2. Data collected from European energy projects
3. Thisted District Heating, Personal Communication
4. Energy Technology Data Catalogue, June 2019
5. European Technology platform on Renewable Heating and Cooling, 2014, Geothermal Technology Roadmap
6. Technology Catalogue, Ch. 40 (2020)
7. Input from APMH March 2020 (drilling costs variations with depth)

## 45.3.a Geoth. DH, 1200m, E (LT)
Technology |  | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 10.93 | 10.9 | 10.86 | 10.8 | 10.77 | 18.45 | 4.1 | 18.45 | 4.1 | [I, A] | [1, 2]
| Heat efficiency (net, annual average) [] | 548.1% | 556.1% | 564% | 579.6% | 587.3% | 651.7% | 467.8% | 704.3% | 494.3% | AG
| Auxiliary Electricity consumption (share of heat gen.) [] | 4.304% | 4.318% | 4.331% | 4.356% | 4.368% | 1.721% | 7.749% | 1.721% | 7.749% | B | [2, 3, 4]
| Forced outage [] | 2% | 2% | 2% | 2% | 2% | 1% | 3% | 1% | 3% |  | 5
| Planned outage [weeks per year] | 2 | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 |  | 5
| Technical lifetime [years] | 25 | 25 | 30 | 30 | 30 | 25 | 30 | 25 | 35 |  | 5
| Construction time [years] | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 5 | 3 | 5 |  | 5
| Space requirement [1000 m2/MW_h] | 5 | 5 | 5 | 5 | 5 | 3 | 7 | 3 | 7 | D | 5
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: note
Secondary regulation (of full load, per minute) [] | bar: note
| Minimum load (of full load) [] | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | H | [2, 5]
Warm start-up time [hours]
| Cold start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 3
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 2.7 | 2.64 | 2.49 | 2.43 | 2.37 | 1.6 | 4.04 | 1.48 | 3.74 | [C, K] | [2, 4, 7]
| Nominal investment (equipment) [2015-MEUR/MW_h] | 1.6 | 1.56 | 1.51 | 1.46 | 1.42 | 0.89 | 2.41 | 0.81 | 2.2 |  | [2, 4]
| Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | 0.56 | 0.56 | 0.48 | 0.48 | 0.48 | 0.4 | 0.8 | 0.39 | 0.79 | [J, K]
| Nominal investment (installation) [2015-MEUR/MW_h] | 0.53 | 0.52 | 0.5 | 0.49 | 0.47 | 0.31 | 0.83 | 0.28 | 0.75 |  | [2, 4]
| Variable O&M (*total) [2015-EUR/MWh_h] | 5.46 | 5.45 | 5.78 | 5.86 | 5.51 | 4.93 | 5.77 | 5.43 | 6.18 | FJ | 2
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 5.46 | 5.45 | 5.78 | 5.86 | 5.51 | 4.93 | 5.77 | 5.43 | 6.18 | F
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 23200 | 22500 | 21800 | 21100 | 20500 | 22500 | 22500 | 20500 | 20500 | [E, J] | [1, 3, 2]
Technology-specific data
| Number of injection wells | 4 | 4 | 4 | 4 | 4 | 3 | 2 | 3 | 2 | [L, N] | 1
| Number of production wells | 2 | 2 | 2 | 2 | 2 | 3 | 1 | 3 | 1 | [L, N] | 1
| Heat pump SCOP (net, annual average) [] | 603% | 614.8% | 626.6% | 650.3% | 662.1% | 614.8% | 614.8% | 662.1% | 662.1% | [A, N]
| Heat generation from heat pumps [MW_h] | 1.52 | 1.49 | 1.46 | 1.39 | 1.36 | 2.51 | 0.56 | 2.3 | 0.51 | A | 1
| Heat generation from geothermal ressource [MW_h] | 9.41 | 9.41 | 9.41 | 9.41 | 9.41 | 15.88 | 3.53 | 15.88 | 3.53 | [I, A, L, N] | 1
| Depth of geothermal well [m] | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 |  | 1
Notes:
A. Part of the geothermal heat is transferred directly to DH water. In combination with an electric heat pump, 19% of geothermal heat can be exchanged directly, leaving 79 as heat source for the heat pump. Heat pump COP calculated according to [15] with Lorentz efficiency 0,5. Improved COP as per Ch. 40.
B. The total electricity demand for submerged pumps / reinjection pumps etc. This will vary according to reservoir properties. Lower / upper case considers variations.
C. Includes CAPEX for the heat pump. Does not include project development costs e.g. initial screening, seismic survey, and geological model, estimated to 1,5-3 MEUR/site (based on 1;4 and Ref. [10]). A well cost of 1900 EUR/m is assumed.
D. This will vary with the design. Requirements are usually higher during construction phase. In case of vertical injection wells a horizontal offset in the range of 1-2 km for the injection wells is necessary
E. Replacement of submersible pump(s), approx. once every five years, operation staff. Heat pump fixed O&M included, as per see datasheets in Chapter 40 Heat pumps.
F. Include maintenance of filters and wells (chemical treatment)
G. Total efficiency is calculated as heat output divided by energy input. Energy input is input to heat pump and auxiliary electricity to pumps etc.
H. A geothermal plant is intended for continuous operation. Electric heat pumps may provide some of regulation though, e.g. in connection with a heat storage
I. Uncertainty does not consider the risk of not finding a suitable reservoir.
J. Including heat pump nominal investment and O&M costs - re.datasheets in chapter 40 Heat pumps
K. The base for the specific investment is the heat generation capacity for one unit including heat pumps.
L. Lower / upper cases considers variations in the plant size in terms of numbers of wells.
M. Auxiliary electricity consumption is included in the total efficiency. Can be calculated separately based on the figure above.
N. Temperature of geothermal heat is 44/17 (°C source/return). Temperature of DH water is 70/35 (°C source/return)
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. PlanEnergi, GEUS, 2019
2. Data collected from European energy projects
3. Thisted District Heating, Personal Communication
4. Energy Technology Data Catalogue, June 2019
5. European Technology platform on Renewable Heating and Cooling, 2014, Geothermal Technology Roadmap
6. Technology Catalogue, Ch. 40 (2020)
7. Input from APMH March 2020 (drilling costs variations with depth)

## 46 Solar District Heating
Technology |  | Solar DH - renewable heat - solar - medium
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Heat efficiency (net, annual average) [] | 43% | 45% | 48% | 49.95% | 42% | 49% | 46% | 54% | P
| Auxiliary Electricity consumption (share of heat gen.) [] | 0.3% | 0.3% | 0.3% | 0.3% | 0.2% | 0.4% | 0.2% | 0.4%
| Forced outage [] | 0.5% | 0.5% | 0.5% | 0.5% | 0% | 1% | 0% | 1% | K
| Technical lifetime [years] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | I | 17
| Construction time [years] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
| Space requirement [1000 m2/MWh_h/y] | 6.7 | 6.3 | 6 | 5.7 | 6 | 6.7 | 5.5 | 6 | J
Regulation ability
Primary regulation (of full load, per 30 seconds) []
Secondary regulation (of full load, per minute) []
Minimum load (of full load) [] | bar: note
Warm start-up time [hours]
Cold start-up time [hours]
Environment
| SO2 [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NOX [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CH4 [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| N2O [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 0.31 | 0.31 | 0.3 | 0.28 | 0.29 | 0.32 | 0.26 | 0.31 | [C, E, H, N, S] | [16, 18]
| Nominal investment (equipment) [2015-MEUR/MW_h] | 0.23 | 0.23 | 0.22 | 0.21 | 0.22 | 0.23 | 0.19 | 0.22 | O
| Nominal investment (installation) [2015-MEUR/MW_h] | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.03 | 0.04 | O
| Nominal investment (diurnal heat storage) [2015-MEUR/MW_h] | 0.04 | 0.04 | 0.04 | 0.04 | 0.03 | 0.05 | 0.03 | 0.05 | [D, M]
| Variable O&M (*total) [2015-EUR/MWh_h] | 0.19 | 0.21 | 0.3 | 0.35 | 0.14 | 0.28 | 0.23 | 0.47
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 0.19 | 0.21 | 0.3 | 0.35 | 0.14 | 0.28 | 0.23 | 0.47 | R
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 57.86 | 60.81 | 56.81 | 59.71 | 56.68 | 64.29 | 54.78 | 56.81 | B
Technology-specific data
| Nominal investment (diurnal heat storage) [2015-EUR/MWh_h/y] | 60 | 57 | 54 | 52 | 41 | 75 | 37 | 68 | [D, M]
| Nominal investment (total solar system excl diurnal heat storage) [2015-EUR/MWh_h/y] | 428.89 | 395.39 | 362.11 | 325.4 | 371.04 | 422.22 | 292.08 | 362.11 | [C, H, N]
| Nominal investment (total solar system excl diurnal heat storage, per collector area) [2015-EUR/m2] | 193 | 187 | 180 | 170 | 184 | 190 | 160 | 180 | [G, H, N] | 16
| Fixed O&M (*total, per annual output) [2015-EUR/MWh_h/y] | 0.09 | 0.09 | 0.08 | 0.08 | 0.08 | 0.1 | 0.07 | 0.08 | B
| Fixed O&M (*total, per collector area) [2015-EUR/m2/y] | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | B
| Typical plant size (collector area) [m2] | 10000 | 13000 | 21000 | 55000 | 10000 | 20000 | 10000 | 100000 | L
| Collector input [MWh_i/m2/y] | 1.05 | 1.05 | 1.05 | 1.05 | 1.01 | 1.08 | 1.01 | 1.08 | Q
| Collector output [MWh_h/m2/y] | 0.45 | 0.47 | 0.5 | 0.52 | 0.45 | 0.5 | 0.5 | 0.55 | A | 4
Notes:
A. The yield is weather dependent and very site-specific, depending much on the temperatures of the district heating network. The quoted yield the average measured output from 40 Danish solar heating plants for 2015.
B. Estimate is 0,2 EUR/MWh heat output in 2015, excluding electricity consumption.
C. Applying the formula 250,000 EUR + 167 EUR/m2 solar panel collector for plants <50.000m2, cf. figures from Note G.
D. Including a diurnal storage is mandatory, 0.2 m3/m2 being a typical average storage size. This figure can vary, dependent on the local conditions and desired solar fraction.
E. Can be combined with seasonal storage, cf. corresponding chapter.
F. Solar thermal plants can be regulated by varying the flow of the heat transfer fluid. The regulation ability is limited by the available heat demand in the heat sink (incl. available storage capacity) and solar radiation.
G. 2015-Prices of different plant sizes (Ref. 1): {"5000":{"Price pr. m2 [eur\/m2]":216.0,"Total price [M-eur]":1.08},"10000":{"Price pr. m2 [eur\/m2]":193.33,"Total price [M-eur]":1.93},"20000":{"Price pr. m2 [eur\/m2]":180.0,"Total price [M-eur]":3.6},"50000":{"Price pr. m2 [eur\/m2]":174.67,"Total price [M-eur]":8.73},"100000":{"Price pr. m2 [eur\/m2]":170.0,"Total price [M-eur]":17.0}}
H. Prices include leveling of ground, laying of district heating pipelines in the ground inkl. 50 m of transmission pipeline to the district heating plant, heat exchanger connected to solar panel field and installed with collection tank and expansion with flanges to secondary side, control and electricity works, design and project management, start-up regulation and documentation.
I. The lifetime is minimum 25-30 years, proven in actual plants still in operation. Critical component is the teflon foil, not the material itself, but the application method. The pipes have been improved, designed for the relatively large number of temperature variations, compared to normal district heating pipelines. The fluid is well managed.
J. Space requirement is approximately 3 m2 for each m2 gross collector area. No development of this parameter is expected, since the main reason is to avoid the shadow effect. Minor optimization of the sides of the panels may be obtained, increasing the ratio of aperture/gross area. Other types of solar collectors such as vacuum and CSP (concentrated solar power) may have lower space requirement.
K. The forced outage is very small, therefore in practice close to 0 %. The modular construction makes it possible to maintain sections of the panels. Outage of critical components such as the heat exchanger is very limited.
L. The average plant size increases, but with large variations since both small plants and increasingly larger plants are installed. A 5 % annual increase of the average size is assumed. The plant size is rather dependent on the heat demand in the district heating grid, it is connected to. The collector area is, cf. international standards, stated as gross area.
M. Estimate of cost of tank storage (diurnal storage) is 135 EUR/m3. The required size of the storage differs, but a typical size is 0.1-0.3 m3 storage for each m2 of solar panels, hence a 10,000 m2 solar thermal plant requires 1-3,000 m3 of diurnal storage.
N. Considering a reduction in prices for 2015-2020 / 2020-2030 / 2030-2050 of 0.6 / 0.4 / 0.3 % p.a.
O. The division of cost elements is site- and plant specific. An indicative distribution of costs are; Solar collectors and piping (48%), heat exchanger, pumps etc. (8%), accumulation tank (11%), transmission pipeline (13%), building (2%), control, operation and startup (5%), land purchase, ground works (7%), design, permits, unforeseen (6%). Total for equipment is 85% and for installation is 15% (design, permits, unforeseen, ground works, control and start up), but including accumulation tank and a transmission pipeline.
P. Please refer to www.solvarmedata.dk for display of efficiencies of Danish solar district heating plants. Chose a plant, select "Production and efficiency" and a chart will display the efficiency - typically varying between 20 and 50%.
Q. The solar radiation on the horizontal surface.
R. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
S. The cost per output power is converted from cost per collector area via formula: Power/Area = 0.7 kWth/m2. Note this is an approximation, original figures are stated per area or MWh
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
4. Solar Heating plants in Denmark, Simon Furbo, Bengt Perers and Federico Bava, Department of Civil Engineering, Technical University of Denmark. The projected outputs for 2020, 2030 and 2050 are not from this reference.
16. Arcon-Sunmark, personal communication. The projected costs are not from this reference, but estimated based on two components; the lower specific costs of larger plants in 2015 and increased competition among suppliers and more efficient production of solar panels.
17. "Life expectancy of solar collectors in solar district heating systems", Department of Civil Engineering, Technical University of Denmark, 2009.
18. "Recommendation1: Converting solar thermal collector area into installed capacity (m2 to kWth) ", Solar Heaing and Cooling programme, IEA , 2004.

## 45.2.b Geothermal DH, 2000m, A
Technology |  | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 17.58 | 17.51 | 17.44 | 17.37 | 17.3 | 29.84 | 6.62 | 29.84 | 6.62 | [I, A] | [1, 2]
| Heat efficiency (net, annual average) [] | 292.9% | 295.3% | 297.7% | 300.1% | 302.6% | 316.9% | 274.8% | 329.5% | 284.2% | AG
| Auxiliary Electricity consumption (share of heat gen.) [] | 4.857% | 4.877% | 4.898% | 4.918% | 4.937% | 2.761% | 6.903% | 2.761% | 6.903% | B | [2, 3, 4]
| Forced outage [] | 2% | 2% | 2% | 2% | 2% | 1% | 3% | 1% | 3% |  | 5
| Planned outage [weeks per year] | 2 | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 |  | 5
| Technical lifetime [years] | 25 | 25 | 30 | 30 | 30 | 25 | 30 | 25 | 35 |  | 5
| Construction time [years] | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 5 | 3 | 5 |  | 5
| Space requirement [1000 m2/MW_h] | 5 | 5 | 5 | 5 | 5 | 3 | 7 | 3 | 7 | D | 5
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: note
Secondary regulation (of full load, per minute) [] | bar: note
| Minimum load (of full load) [] | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | H | [2, 5]
Warm start-up time [hours]
| Cold start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 3
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 2.09 | 2.03 | 1.97 | 1.91 | 1.85 | 1.26 | 2.87 | 1.14 | 2.6 | [C, K] | [2, 4, 7]
| Nominal investment (equipment) [2015-MEUR/MW_h] | 1.48 | 1.44 | 1.39 | 1.35 | 1.31 | 0.82 | 2.11 | 0.74 | 1.91 |  | [2, 4]
| Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | 0.12 | 0.12 | 0.11 | 0.11 | 0.11 | 0.16 | 0.04 | 0.14 | 0.03 | [J, K]
| Nominal investment (installation) [2015-MEUR/MW_h] | 0.49 | 0.48 | 0.46 | 0.45 | 0.44 | 0.28 | 0.72 | 0.26 | 0.66 |  | [2, 4]
| Variable O&M (*total) [2015-EUR/MWh_h] | 2.99 | 2.96 | 2.92 | 2.86 | 2.8 | 2.93 | 2.93 | 2.74 | 2.74 | FJ | 2
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 2.99 | 2.96 | 2.92 | 2.86 | 2.8 | 2.93 | 2.93 | 2.74 | 2.74 | F
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 17300 | 16800 | 16300 | 15800 | 15300 | 16800 | 16800 | 15300 | 15300 | [E, J] | [1, 3, 2]
Technology-specific data
| Number of injection wells | 4 | 4 | 4 | 4 | 4 | 3 | 2 | 3 | 2 | [L, N] | 1
| Number of production wells | 2 | 2 | 2 | 2 | 2 | 3 | 1 | 3 | 1 | [L, N] | 1
| Heat pump SCOP (net, annual average) [] | 171% | 172% | 173% | 174% | 175% | 172% | 172% | 175% | 175% | [A, N]
| Heat generation from heat pumps [MW_h] | 5.39 | 5.32 | 5.25 | 5.18 | 5.11 | 9.01 | 2 | 8.65 | 1.92 | A | 1
| Heat generation from geothermal ressource [MW_h] | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 20.6 | 4.57 | 20.6 | 4.57 | [I, A, L, N] | 1
| Depth of geothermal well [m] | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 |  | 1
Notes:
A. Part of the geothermal heat is transferred directly to DH water. In combination with an electric heat pump, 68% of geothermal heat can be exchanged directly, leaving 32 as heat source for the heat pump. Heat pump according to Ch. 40.
B. The total electricity demand for submerged pumps / reinjection pumps etc. This will vary according to reservoir properties. Lower / upper case considers variations.
C. Includes CAPEX for the heat pump. Does not include project development costs e.g. initial screening, seismic survey, and geological model, estimated to 1,5-3 MEUR/site (based on 1;4 and Ref. [10]). A well cost of 1900 EUR/m is assumed.
D. This will vary with the design. Requirements are usually higher during construction phase. In case of vertical injection wells a horizontal offset in the range of 1-2 km for the injection wells is necessary
E. Replacement of submersible pump(s), approx. once every five years, operation staff. Heat pump fixed O&M included, as per see datasheets in Chapter 40 Heat pumps.
F. Include maintenance of filters and wells (chemical treatment)
G. Total efficiency is calculated as heat output divided by energy input. Energy input is input to heat pump and auxiliary electricity to pumps etc.
H. A geothermal plant is intended for continuous operation. Electric heat pumps may provide some of regulation though, e.g. in connection with a heat storage.
I. Uncertainty does not consider the risk of not finding a suitable reservoir.
J. Including heat pump nominal investment and O&M costs - re.datasheets in chapter 40 Heat pumps
K. The base for the specific investment is the heat generation capacity for one unit including heat pumps.
L. Lower / upper cases considers variations in the plant size in terms of numbers of wells.
M. Auxiliary electricity consumption is included in the total efficiency. Can be calculated separately based on the figure above.
N. Temperature of geothermal heat is 68/33 (°C source/return). Temperature of DH water is 80/40 (°C source/return)
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. PlanEnergi, GEUS, 2019
2. Data collected from European energy projects
3. Thisted District Heating, Personal Communication
4. Energy Technology Data Catalogue, June 2019
5. European Technology platform on Renewable Heating and Cooling, 2014, Geothermal Technology Roadmap
6. Technology Catalogue, Ch. 40 (2020)
7. Input from APMH March 2020 (drilling costs variations with depth)

## 45.1.b Geothermal DH, 2000m, E
Technology |  | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 13.14 | 13.11 | 13.09 | 13.05 | 13.03 | 22.18 | 4.93 | 22.18 | 4.93 | [I, A] | [1, 2]
| Heat efficiency (net, annual average) [] | 844.4% | 855.3% | 866.1% | 887% | 897.2% | 1124% | 650.4% | 1208% | 677.4% | AG
| Auxiliary Electricity consumption (share of heat gen.) [] | 6.501% | 6.513% | 6.523% | 6.543% | 6.553% | 3.712% | 9.27% | 3.712% | 9.27% | B | [2, 3, 4]
| Forced outage [] | 2% | 2% | 2% | 2% | 2% | 1% | 3% | 1% | 3% |  | 5
| Planned outage [weeks per year] | 2 | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 |  | 5
| Technical lifetime [years] | 25 | 25 | 30 | 30 | 30 | 25 | 30 | 25 | 35 |  | 5
| Construction time [years] | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 5 | 3 | 5 |  | 5
| Space requirement [1000 m2/MW_h] | 5 | 5 | 5 | 5 | 5 | 3 | 7 | 3 | 7 | D | 5
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: note
Secondary regulation (of full load, per minute) [] | bar: note
| Minimum load (of full load) [] | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | H | [2, 5]
Warm start-up time [hours]
| Cold start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 3
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 2.88 | 2.8 | 2.69 | 2.61 | 2.53 | 1.7 | 4.14 | 1.56 | 3.79 | [C, K] | [2, 4, 7]
| Nominal investment (equipment) [2015-MEUR/MW_h] | 1.98 | 1.92 | 1.86 | 1.81 | 1.75 | 1.14 | 2.83 | 1.03 | 2.57 |  | [2, 4]
| Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | 0.24 | 0.24 | 0.21 | 0.21 | 0.2 | 0.17 | 0.34 | 0.17 | 0.34 | [J, K]
| Nominal investment (installation) [2015-MEUR/MW_h] | 0.66 | 0.64 | 0.62 | 0.6 | 0.58 | 0.39 | 0.97 | 0.36 | 0.88 |  | [2, 4]
| Variable O&M (*total) [2015-EUR/MWh_h] | 4.59 | 4.52 | 4.59 | 4.56 | 4.34 | 4.29 | 4.65 | 4.31 | 4.62 | FJ | 2
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 4.59 | 4.52 | 4.59 | 4.56 | 4.34 | 4.29 | 4.65 | 4.31 | 4.62 | F
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 23900 | 23200 | 22500 | 21800 | 21100 | 23200 | 23200 | 21100 | 21100 | [E, J] | [1, 3, 2]
Technology-specific data
| Number of injection wells | 4 | 4 | 4 | 4 | 4 | 3 | 2 | 3 | 2 | L | 1
| Number of production wells | 2 | 2 | 2 | 2 | 2 | 3 | 1 | 3 | 1 | [L, N] | 1
| Heat pump SCOP (net, annual average) [] | 505% | 514.9% | 524.8% | 544.6% | 554.5% | 514.9% | 514.9% | 554.5% | 554.5% | [A, N]
| Heat generation from heat pumps [MW_h] | 0.95 | 0.92 | 0.9 | 0.86 | 0.84 | 1.56 | 0.35 | 1.43 | 0.32 | A | 1
| Heat generation from geothermal ressource [MW_h] | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 20.58 | 4.57 | 20.58 | 4.57 | [I, A, L, N] | 1
| Depth of geothermal well [m] | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 |  | 1
Notes:
A. Part of the geothermal heat is transferred directly to DH water. In combination with an electric heat pump, 68% of geothermal heat can be exchanged directly, leaving 32 as heat source for the heat pump. Heat pump COP calculated according to [15] with Lorentz efficiency 0,5. Improved COP as per Ch. 40.
B. The total electricity demand for submerged pumps / reinjection pumps etc. This will vary according to reservoir properties. Lower / upper case considers variations.
C. Includes CAPEX for the heat pump. Does not include project development costs e.g. initial screening, seismic survey, and geological model, estimated to 1,5-3 MEUR/site (based on 1;4 and Ref. [10]). A well cost of 2000 EUR/m is assumed.
D. This will vary with the design. Requirements are usually higher during construction phase. In case of vertical injection wells a horizontal offset in the range of 1-2 km for the injection wells is necessary
E. Replacement of submersible pump(s), approx. once every five years, operation staff. Heat pump fixed O&M included, as per see datasheets in Chapter 40 Heat pumps.
F. Include maintenance of filters and wells (chemical treatment)
G. Total efficiency is calculated as heat output divided by energy input. Energy input is input to heat pump and auxiliary electricity to pumps etc.
H. A geothermal plant is intended for continuous operation. Electric heat pumps may provide some of regulation though, e.g. in connection with a heat storage.
I. Uncertainty does not consider the risk of not finding a suitable reservoir.
J. Including heat pump nominal investment and O&M costs - re.datasheets in chapter 40 Heat pumps
K. The base for the specific investment is the heat generation capacity for one unit including heat pumps.
L. Lower / upper cases considers variations in the plant size in terms of numbers of wells.
M. Auxiliary electricity consumption is included in the total efficiency. Can be calculated separately based on the figure above.
N. Temperature of geothermal heat is 68/33 (°C source/return). Temperature of DH water is 80/40 (°C source/return)
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. PlanEnergi, GEUS, 2019
2. Data collected from European energy projects
3. Thisted District Heating, Personal Communication
4. Energy Technology Data Catalogue, June 2019
5. European Technology platform on Renewable Heating and Cooling, 2014, Geothermal Technology Roadmap
6. Technology Catalogue, Ch. 40 (2020)
7. Input from APMH March 2020 (drilling costs variations with depth)

## 45.1.a Geothermal DH, 1200m, E
Technology |  | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 11.42 | 11.37 | 11.33 | 11.24 | 11.2 | 19.28 | 4.28 | 19.28 | 4.28 | [I, A] | [1, 2]
| Heat efficiency (net, annual average) [] | 460.3% | 467.2% | 474% | 487.6% | 494.2% | 530.9% | 405.9% | 575.5% | 431.6% | AG
| Auxiliary Electricity consumption (share of heat gen.) [] | 4.121% | 4.138% | 4.154% | 4.185% | 4.199% | 1.647% | 7.423% | 1.647% | 7.423% | B | [2, 3, 4]
| Forced outage [] | 2% | 2% | 2% | 2% | 2% | 1% | 3% | 1% | 3% |  | 5
| Planned outage [weeks per year] | 2 | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 |  | 5
| Technical lifetime [years] | 25 | 25 | 30 | 30 | 30 | 25 | 30 | 25 | 35 |  | 5
| Construction time [years] | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 5 | 3 | 5 |  | 5
| Space requirement [1000 m2/MW_h] | 5 | 5 | 5 | 5 | 5 | 3 | 7 | 3 | 7 | D | 5
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: note
Secondary regulation (of full load, per minute) [] | bar: note
| Minimum load (of full load) [] | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | H | [2, 5]
Warm start-up time [hours]
| Cold start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 3
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 2.71 | 2.65 | 2.5 | 2.44 | 2.38 | 1.63 | 4.06 | 1.52 | 3.76 | [C, K] | [2, 4, 7]
| Nominal investment (equipment) [2015-MEUR/MW_h] | 1.54 | 1.49 | 1.45 | 1.4 | 1.36 | 0.86 | 2.31 | 0.78 | 2.1 |  | [2, 4]
| Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | 0.67 | 0.67 | 0.57 | 0.57 | 0.57 | 0.47 | 0.95 | 0.47 | 0.93 | [J, K]
| Nominal investment (installation) [2015-MEUR/MW_h] | 0.51 | 0.5 | 0.48 | 0.47 | 0.45 | 0.3 | 0.79 | 0.27 | 0.72 |  | [2, 4]
| Variable O&M (*total) [2015-EUR/MWh_h] | 5.7 | 5.71 | 6.13 | 6.25 | 5.86 | 5.09 | 6.09 | 5.75 | 6.64 | FJ | 2
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 5.7 | 5.71 | 6.13 | 6.25 | 5.86 | 5.09 | 6.09 | 5.75 | 6.64 | F
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 22600 | 21900 | 21300 | 20600 | 19900 | 21900 | 21900 | 19900 | 19900 | [E, J] | [1, 3, 2]
Technology-specific data
| Number of injection wells | 4 | 4 | 4 | 4 | 4 | 3 | 2 | 3 | 2 | L | 1
| Number of production wells | 2 | 2 | 2 | 2 | 2 | 3 | 1 | 3 | 1 | [L, N] | 1
| Heat pump SCOP (net, annual average) [] | 568% | 579.1% | 590.3% | 612.5% | 623.7% | 579.1% | 579.1% | 623.7% | 623.7% | [A, N]
| Heat generation from heat pumps [MW_h] | 2.01 | 1.96 | 1.92 | 1.84 | 1.8 | 3.31 | 0.74 | 3.03 | 0.67 | A | 1
| Heat generation from geothermal ressource [MW_h] | 9.41 | 9.41 | 9.41 | 9.41 | 9.41 | 15.88 | 3.53 | 15.88 | 3.53 | [I, A, L, N] | 1
| Depth of geothermal well [m] | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 |  | 1
Notes:
A. No part of the geothermal heat is transferred directly to DH water, all is used as source for the heat pump Heat pump COP calculated according to [15] with Lorentz efficiency 0,5. Improved COP as per Ch. 40.
B. The total electricity demand for submerged pumps / reinjection pumps etc. This will vary according to reservoir properties. Lower / upper case considers variations.
C. Includes CAPEX for the heat pump. Does not include project development costs e.g. initial screening, seismic survey, and geological model, estimated to 1,5-3 MEUR/site (based on 1;4 and Ref. [10]). A well cost of 1800 EUR/m is assumed.
D. This will vary with the design. Requirements are usually higher during construction phase. In case of vertical injection wells a horizontal offset in the range of 1-2 km for the injection wells is necessary
E. Replacement of submersible pump(s), approx. once every five years, operation staff. Heat pump fixed O&M included, as per see datasheets in Chapter 40 Heat pumps.
F. Include maintenance of filters and wells (chemical treatment)
G. Total efficiency is calculated as heat output divided by energy input. Energy input is input to heat pump and auxiliary electricity to pumps etc.
H. A geothermal plant is intended for continuous operation. Electric heat pumps may provide some of regulation though, e.g. in connection with a heat storage.
I. Uncertainty does not consider the risk of not finding a suitable reservoir.
J. Including heat pump nominal investment and O&M costs - re.datasheets in chapter 40 Heat pumps
K. The base for the specific investment is the heat generation capacity for one unit including heat pumps.
L. Lower / upper cases considers variations in the plant size in terms of numbers of wells.
M. Auxiliary electricity consumption is included in the total efficiency. Can be calculated separately based on the figure above.
N. Temperature of geothermal heat is 44/17 (°C source/return). Temperature of DH water is 80/40 (°C source/return)
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. PlanEnergi, GEUS, 2019
2. Data collected from European energy projects
3. Thisted District Heating, Personal Communication
4. Energy Technology Data Catalogue, June 2019
5. European Technology platform on Renewable Heating and Cooling, 2014, Geothermal Technology Roadmap
6. Technology Catalogue, Ch. 40 (2020)
7. Input from APMH March 2020 (drilling costs variations with depth)

## 40 Absorption heat pump, DH
Technology |  | Absorption heat pump - heat pump - heat - medium
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 12 | 12 | 12 | 12 | 12 | 20 | 12 | 30 | [A, A1] | 13
| Heat efficiency (net, annual average) [] | 170% | 171% | 173% | 175% | 170% | 180% | 170% | 180% | B | 4
Heat efficiency (net, name plate) []
| Auxiliary Electricity consumption (share of heat gen.) [] | 1% | 1% | 1% | 1% | 1% | 3% | 1% | 3% | E | 3
| Forced outage [] | 0% | 0% | 0% | 0% | 0% | 1% | 0% | 1% | C
| Planned outage [weeks per year] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | D
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 15 | 30 | 15 | 30 |  | 3
| Construction time [years] | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.7 | 0.3 | 0.7
| Space requirement [1000 m2/MW_h] | 0.01 | 0.01 | 0 | 0 | 0 | 0.01 | 0 | 0.01
Regulation ability
Primary regulation (of full load, per 30 seconds) []
Secondary regulation (of full load, per minute) []
| Minimum load (of full load) [] | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10%
| Warm start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1
| Cold start-up time [hours] | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 2 | 0.25 | 2
Environment
| SO2 [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NOX [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CH4 [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| N2O [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 0.6 | 0.56 | 0.51 | 0.46 | 0.4 | 0.8 | 0.4 | 0.8 | [A, A1] | 3
| Nominal investment (equipment) [2015-MEUR/MW_h] | 50 | 50 | 50 | 50 | 30 | 70 | 30 | 70 |  | 3
| Nominal investment (installation) [2015-MEUR/MW_h] | 50 | 50 | 50 | 50 | 30 | 70 | 30 | 70 |  | 3
| Variable O&M (*total) [2015-EUR/MWh_h] | 0.9 | 0.98 | 1.25 | 1.43 | 1 | 2.5 | 1.4 | 0.3
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 0.6 | 0.7 | 1 | 1.2 | 0.7 | 2.1 | 1.2 | 0 | E
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 0.3 | 0.28 | 0.25 | 0.23 | 0.3 | 0.4 | 0.2 | 0.3 |  | 3
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 2000 | 2000 | 2000 | 2000 | 1000 | 3000 | 1000 | 3000 |  | 3
Notes:
A. The heat pump itself only represents a small part of the total investment. Depending on size the heat pump typically represents 0.2 MEUR per. MW heating (excluding drive energy).
A1. Capacity is excluding drive energy.
B. The heat is assumed delivered at 80 °C in 2015 and 60 °C in 2050
C. May vary depending on availability of heat source
D. May vary depending on specific type, heat source etc.
E. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
3. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, 2014, see http://www.planenergi.dk/varmepumper/
4. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, 2013
13. Scandinavian Energy Group, 2015

## 40 Comp. hp, excess heat 10 MW
Technology |  | Heat pump, industrial excess heat - heat pump - electricity - large
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 10 | 10 | 10 | 10 | 10 | 5 | 20 | 5 | 20
| Heat efficiency (net, annual average) [] | 510% | 520% | 530% | 540% | 550% | 500% | 530% | 510% | 570% | [A, A1, C, D] | [1, 14, 15]
| Heat efficiency (net, name plate) [] | 500% | 510% | 520% | 530% | 540% | 490% | 520% | 500% | 560% | [A, A1, B, D] | [1, 14, 15]
| Auxiliary Electricity consumption (share of heat gen.) [] | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | D | [1, 14, 15]
| Forced outage [] | 0% | 0% | 0% | 0% | 0% | 0% | 5% | 0% | 5% |  | [1, 14, 15]
| Planned outage [weeks per year] | 1 | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | [1, 14, 15]
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 | 15 | 40 | 15 | 40 |  | [1, 9, 10, 14, 15]
| Construction time [years] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 1 | 0.3 | 1 | [E, F] | [9, 14, 15]
| Space requirement [1000 m2/MW_h] | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.06 | 0.02 | 0.06 |  | [15, 18]
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 5% | 5% | 5% | 5% | 5% | 5% | 50% | 5% | 50% | G | [1, 9, 14, 15]
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 100% | 10% | 100% | G | [1, 9, 14, 15]
| Minimum load (of full load) [] | 25% | 25% | 25% | 25% | 25% | 10% | 50% | 10% | 50% | [G, I] | [1, 9, 14, 15]
| Warm start-up time [hours] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.2 | G | [9, 14, 15]
| Cold start-up time [hours] | 1 | 1 | 1 | 1 | 1 | 0.2 | 1 | 0.2 | 1 | [G, H] | [9, 14, 15]
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 0.67 | 0.67 | 0.57 | 0.57 | 0.57 | 0.48 | 0.95 | 0.48 | 0.95 | [A, J, K, O] | [1, 14, 15]
| Nominal investment (equipment) [2015-MEUR/MW_h] | 0.53 | 0.53 | 0.46 | 0.46 | 0.46 | 0.38 | 0.76 | 0.38 | 0.76 | A | [1, 14, 15]
| Nominal investment (grid connection) [2015-MEUR/MW_e] | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.1 | 0.01 | 0.1 | J | [1, 14, 15]
| Nominal investment (installation) [2015-MEUR/MW_h] | 0.12 | 0.12 | 0.1 | 0.1 | 0.1 | 0.09 | 0.1 | 0.09 | 0.1 | A | [1, 14, 15]
| Variable O&M (*total) [2015-EUR/MWh_h] | 1.69 | 1.69 | 2.01 | 2.09 | 1.69 | 1.19 | 2.19 | 1.69 | 2.67 |  | [1, 14, 15]
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [D, M] | [1, 14, 15]
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 1.69 | 1.69 | 2.01 | 2.09 | 1.69 | 1.19 | 2.19 | 1.69 | 2.67 | L | [1, 14, 15]
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 2000 | 2000 | 2000 | 2000 | 2000 | 1000 | 3000 | 1000 | 5000 | L | [1, 14, 15]
| Startup cost [2015-EUR/MW_h/startup] | 10 | 10 | 10 | 10 | 10 | 5 | 20 | 2 | 20 | N | 15
Notes:
A. Based on cooling water that is cooled from 25 to 15 °C. Actual development within COP optimization and reduced investment cost depends on the development in fuel and electricity prices.
A1. Performance data regarding ambient air and industrial waste heat are based on typical supply temperatures of decentral district heating systems with an annual average return/forward temperature of 35 °C / 70 °C (it varies over the year). It is assumed that the heat pumps only cover 85 % of the annual heat demand, meaning that the heat pumps co-produce with peak load units during the coldest periods. This mean that the forward temperature of the heat pump can be kept at around 70 °C during the coldest periods or even lowered.
B. Total efficiency, net (%), name plate is at district heating temperatures of 35 °C return and 70 °C forward.
C. Annual average at 85 % heat production of total demand utilizing coproduction at peak demands with reduced output temperatur from heat pump. DH temperatures are 35 °C return and 70 °C forward.
D. Auxiliary electricity consumption is included in the Total efficiency. Cost for electricity is therefore not accounted for in variable O&M
E. Does not include tendering and regulatory approvals.
F. The development within construction time will depend on future production figures and standardization of plants.
G. The regulation ability will depend on the future marktes for regulation services.
H. Cold start of time is starting a heat pump where stand by heating has not been applied
I. Operation at part load will usually increase COP but also variable O&M costs
J. It is assumed that heat pumps is connected with limited access like electrical boilers. Upper values regarding uncertainty assume that installations must pay for full access
K. Land is usually owned by the company
L. O&M regard the heat pump it self including auxiliary equipment, building etc. for the heat pump. The costs does not include O&M for the entire district heating network, peak load or back up units, administration regarding end users etc.
M. All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M
N. 1/4 MWh-heat per MW is lost during startup
O. At district heating temperatures of 40-80 °C, the specific investment is expected to increase by 5 % as compontents must be rated for higher pressure levels
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Støchkel, Paaske, Clausen, 2017, see https://ens.dk/sites/ens.dk/files/Varme/drejebog_for_store_varmepumper.pdf
2. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Sørensen, Paaske, Jacobsen, Hofmeister, 2013
3. Absorption chillers and heat pumps, Keith E. Herold, Reinhard Radermacher and Sanford A. Klein, 1996
4. Scandinavian Energy Group, 2015, Conversation
5. Advansor, 2015, Conversation
6. Hybrid Energi, 2015, Conversation
7. Innoterm, 2015, Conversation
8. Cronborg, 2015, Conversation
9. Johnson Controls, 2019, Conversation
10. Teknologisk Institut, 2015, 2019, Conversation
11. Energinet.dk, 2015, Conversation
12. IEA 2012, Energy Technology Perspectives, 2012
13. Store varmepumper i fjernvarmen - driftserfaringer, Flørning, Carøe, Nielsen, Støchkel, 2019
14. IES/Victor DST, 2019, Conversation
15. PlanEnergi, 2019, practical experience from installed plants
16. DMI, 2019
17. Danfoss, 2019, Conversation
18. Varmeværket Bjerringbro, Vejen Varmeværk, Skjern Papirfabrik, Høje Taastrup Fjernvarme, Rødkærsbro Kraftvarmeværk, Kalundborg Forsyning, Rye Kraftvarmeværk, Broager Fjernvarmeselskab, Sig Varmeværk, Fensmark Fjernvarme, Slagslunde Fjernvarme, Farum Fjernvarme, FFV Energi & Miljø, Karup Varmeværk, Støvring Kraftvarmeværk, Skagen Varmeværk, Strandby Varmeværk

## 09a Wood Chips HOP, large
Technology |  | Biomass boiler - boiler - wood chips - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 103.43 | 103.43 | 103.43 | 103.42 | 80.92 | 103.78 | 79.47 | 103.87 | A | 1
| Heat efficiency (net, annual average) [] | 114.9% | 114.9% | 114.9% | 114.9% | 89% | 116% | 88% | 116% | [B, C] | 1
| Heat efficiency (net, name plate) [] | 114.9% | 114.9% | 114.9% | 114.9% | 89% | 116% | 88% | 116% | [B, C] | 1
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.201% | 2.201% | 2.201% | 2.2% | 2.095% | 2.456% | 1.706% | 2.452% | [C, K]
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 2 | 2 | 2 | 2 | 1.7 | 2.3 | 1.5 | 2.5
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 3 | 2 | 3 |  | 1
| Space requirement [1000 m2/MW_h] | 0.05 | 0.05 | 0.05 | 0.05 | 0.04 | 0.06 | 0.04 | 0.06
Regulation ability
Primary regulation (of full load, per 30 seconds) []
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | E | 1
| Minimum load (of full load) [] | 40% | 40% | 40% | 40% | 40% | 40% | 40% | 40% |  | 1
| Warm start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | H | 1
| Cold start-up time [hours] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 97.97% | 97.97% | 97.97% | 97.97% | 94.92% | 98.98% | 97.97% | 98.98% | G | 1
| NOX [g/GJ_i] | 90 | 60 | 40 | 20 | 40 | 60 | 20 | 40 |  | [2, 3]
| CH4 [g/GJ_i] | 3 | 2 | 2 | 1 | 1 | 3 | 0 | 3 |  | 3
| N2O [g/GJ_i] | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 1 |  | 3
| Particles [g/GJ_i] | 2 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 |  | 3
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 0.45 | 0.44 | 0.42 | 0.4 | 0.38 | 0.52 | 0.31 | 0.55 | [F, L]
| Nominal investment (equipment) [2015-MEUR/MW_h] | 0.34 | 0.33 | 0.31 | 0.31 | 0.29 | 0.39 | 0.24 | 0.42 | [F, L]
| Nominal investment (installation) [2015-MEUR/MW_h] | 0.11 | 0.11 | 0.1 | 0.09 | 0.09 | 0.13 | 0.08 | 0.13 | [F, L]
| Variable O&M (*total) [2015-EUR/MWh_h] | 2.57 | 2.7 | 3.41 | 3.76 | 2.32 | 3.67 | 3.27 | 5.26 | M
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 1.39 | 1.52 | 2.22 | 2.57 | 1.5 | 1.98 | 2.55 | 3.41 | M
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 1.18 | 1.18 | 1.18 | 1.18 | 0.82 | 1.7 | 0.72 | 1.86 | M
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 35200 | 34600 | 33300 | 31400 | 29500 | 39900 | 23600 | 39900
Technology-specific data
| Nominal investment (*total) [2015-MEUR/MW_i] | 0.52 | 0.5 | 0.48 | 0.46 | 0.44 | 0.6 | 0.36 | 0.63 | L | 1
| Nominal investment (equipment) [2015-MEUR/MW_i] | 0.39 | 0.38 | 0.36 | 0.36 | 0.33 | 0.45 | 0.27 | 0.48 | L
| Nominal investment (installation) [2015-MEUR/MW_i] | 0.13 | 0.12 | 0.12 | 0.11 | 0.11 | 0.15 | 0.09 | 0.15 | L
| Variable O&M (*total) [2015-EUR/MWh_i] | 2.95 | 3.1 | 3.91 | 4.32 | 2.68 | 3.3 | 3.77 | 4.65 | M
| Fixed O&M (*total) [2015-EUR/MW_i/y] | 40500 | 39700 | 38200 | 36100 | 33900 | 45900 | 27200 | 45800
| Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.02 | 0.01 | 0.02 | L
| Output of recovered condensate [t/MWh_i] | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0.25 | 0 | 0.25 | D
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [D, N]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [D, N]
| Additional heat potential with heat pumps (of thermal input) [] | 1.943% | 1.943% | 1.943% | 1.944% | 1% | 26% | 1% | 28% | D | 1
Notes:
A. The plant is directly producing hot water for District Heating by burning fuel on a grate. Fluid-bed combustion technology may be an alternative. It can be assumed that the data for this does not differ significantly from grate fired boilers. Data in this sheet is applicable for plants in the range of 80-99,9 MW fired capacity (heat input). The system is optimised at DH return temperature 40°C and flow 80°C.
B. Boilers larger than approx. 20 MW fuel input for hot water production are designed-for-purpose products with a high degree of fuel flexibility (type of biomass, humidity etc.)
C. Efficiencies refer to lower heating value. The stated total efficiency does NOT consider auxiliary electricity consumption. It describes the total net amount of heat produced at the plant. This is contrary to CHP where the auxiliary electricity is subtracted from the production to yield the net electricity efficiency. Direct condensation and combustion air humidification are included in all cases except in lower range of 2020 and 2050. The colder the return temperature of the district heating, the higher the total efficiency at direct condensation.
D. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
E. Load control of the heat production is important and units of this size can make rapid load variations.
F. Reference to heat output because of the lack of electricity production
G. Assuming content of sulphur in fuel of 20 g/GJ
H. Warm start is starting with a glowing fuel layer on the grate.
K. Result of model calculation, there are reports of DH plants operating at lower power consumption, down to 1% of heat generation.
L. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
M. Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Electricity consumption is included for DH and associated costlisted separately, in addition. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Revenues from sale of heat are not included. Taxes are not included. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
N. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949
3. Emission factors of 2006: 81 g/GJ NOx, 1.9 g/GJ for SO2, <1 g/GJ for CH4, 0.8 g/GJ for N2O, 10 g/GJ for Particles; cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. - NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.

## 08 WtE CHP, Medium
Technology |  | Waste CHP - back pressure - waste - medium
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 18.61 | 18.61 | 19.03 | 19.69 | 16.91 | 20.24 | 16.91 | 21.66 | [A, B]
| Electrical efficiency (net, annual average) [] | 22.1% | 22.1% | 22.6% | 23.38% | 19% | 25% | 19% | 26% | [A, B, C]
| Electrical efficiency (net, name plate) [] | 23.26% | 23.26% | 23.79% | 24.61% | 21% | 26% | 21% | 28% | [A, B, C]
| Cb coefficient (40°C/80°C) | 0.3 | 0.3 | 0.3 | 0.31 | 0.27 | 0.32 | 0.27 | 0.35 | [A, B]
| Cv coefficient (40°C/80°C) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [A, B]
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.91% | 2.91% | 2.922% | 2.911% | 2.147% | 3.196% | 1.718% | 3.268% | [A, B]
Forced outage [] | bar: ctrl to upper; ref
| Planned outage [weeks per year] | 3 | 2.85 | 2.58 | 2.11 | 2.43 | 3.28 | 1.58 | 2.64 | E | 1
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 3 | 1.5 | 3 |  | 1
| Space requirement [1000 m2/MW_e] | 1.61 | 1.61 | 1.58 | 1.52 | 1.37 | 1.85 | 1.14 | 1.9 |  | 1
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: ctrl to note
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | [F, G]
| Minimum load (of full load) [] | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | [F, G]
| Warm start-up time [hours] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [F, G]
| Cold start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [F, G]
Environment
| SO2 (degree of desulphuring) [] | 99.79% | 99.79% | 99.79% | 99.79% | 98.96% | 99.9% | 99.48% | 99.9% | H | 1
| NOX [g/GJ_i] | 80 | 60 | 40 | 10 | 10 | 60 | 10 | 60 | I | [2, 3, 5]
| CH4 [g/GJ_i] | 0.3 | 0.1 | 0.1 | 0.1 | 0 | 0.1 | 0 | 0.1 |  | 2
| N2O [g/GJ_i] | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | J | 2
| Particles [g/GJ_i] | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | J | 2
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 9.25 | 9.02 | 8.6 | 7.54 | 7.67 | 10.59 | 5.5 | 9.37 | N | 1
| Nominal investment (equipment) [2015-MEUR/MW_e] | 5.62 | 5.48 | 5.31 | 4.66 | 4.66 | 6.52 | 3.34 | 5.78 | N | 1
| Nominal investment (installation) [2015-MEUR/MW_e] | 3.63 | 3.54 | 3.29 | 2.88 | 3.01 | 4.07 | 2.16 | 3.6 | M | 1
| Variable O&M (*total) [2015-EUR/MWh_e] | 25.28 | 25.28 | 24.74 | 23.93 | 21.51 | 29.14 | 17.99 | 29.89 | K | 1
| Fixed O&M (*total) [2015-EUR/MW_e/y] | 298000 | 262000 | 245000 | 209000 | 223000 | 306000 | 154000 | 260000 | L | 1
Technology-specific data
| Heat efficiency (net, annual average) [] | 79.99% | 79.99% | 79.71% | 79.42% | 76% | 85% | 73% | 88% | [A, B, C]
| Heat efficiency (net, name plate) [] | 78.82% | 78.82% | 78.52% | 78.19% | 74% | 84% | 71% | 86% | [A, B]
| Nominal investment (*total) [2015-MEUR/MW_i] | 2.15 | 2.1 | 2.05 | 1.86 | 1.78 | 2.46 | 1.35 | 2.31 | N | 1
| Nominal investment (*total) [2015-MEUR/t_i] | 790 | 770 | 750 | 680 | 660 | 910 | 500 | 850 | N | 1
| Nominal investment (equipment) [2015-MEUR/MW_i] | 1.31 | 1.28 | 1.26 | 1.15 | 1.08 | 1.52 | 0.82 | 1.42 | N | 1
| Nominal investment (installation) [2015-MEUR/MW_i] | 0.84 | 0.82 | 0.78 | 0.71 | 0.7 | 0.95 | 0.53 | 0.88 | M | 1
| Variable O&M (*total) [2015-EUR/MWh_i] | 5.88 | 5.88 | 5.88 | 5.89 | 5 | 6.78 | 4.43 | 7.36 | K | 1
| Fixed O&M (*total) [2015-EUR/MW_i/y] | 69300 | 61000 | 58200 | 51400 | 51900 | 71200 | 37800 | 64000 | L | 1
| Fixed O&M (*total) [2015-EUR/t_i/y] | 25.51 | 22.46 | 21.42 | 18.92 | 19.09 | 26.2 | 13.91 | 23.56 | L | [1, 4]
| Steam reheat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | P
| Output of recovered condensate [t/MWh_i] | 0.11 | 0.11 | 0.11 | 0.12 | 0.1 | 0.14 | 0.1 | 0.14 | [D, K]
| Output of recovered condensate [2015-EUR/t_i] | 17.32 | 17.32 | 17.33 | 17.35 | 14.74 | 19.97 | 13.04 | 21.67 | K | [1, 4]
| Incineration capacity [t_i/h] | 27.16 | 27.16 | 27.16 | 27.16 | 27.16 | 27.16 | 27.16 | 27.16 | [A, B]
| Flue gas condensation | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [D, P]
| Combustion air humidification | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | [D, P]
| Additional heat potential with heat pumps (of thermal input) [] | 4.151% | 4.151% | 4.015% | 3.74% | 1% | 6% | 1% | 6% | [A, B, D]
Notes:
A. Assumed lower heating value 10.6 MJ/kg, waste input 27.2 tph = tonnes per hour (incineration capacity), corresponding to thermal input of 80 MW. Live steam pressure in base case 50 bara, temperature 425 °C of 2015 and 2020, increasing to 440 °C and 450 °C, in 2030 and 2050, restpectively. Efficiencies refer to lower heating value.
B. With flue gas condensation (condensation through heat exchange with DH-water, only) and a back-pressure turbine/condenser system optimised for DH return temperature 40°C and flow 80°C
C. Annual average heat output is higher than nameplate because the total efficiency is constant, and the annual average electricity generation is lower than nameplate electricity output. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
D. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation is included in all cases, and combustion air humidification is included in lower/upper ranges of 2020 and 2050.
E. Focus on availability and ambitions of 2 years' continuous operation is expected to gradually reduce planned outage.
F. Regulation and start-up refer to electricity generation controlled by the turbine operation.The WtE facility would usually be operating at 100% thermal input, and the electricity output is controlled to the desired level by use of turbine by-pass, by which excess steam is used to produce DH-energy. Warm start-up time refers to 2 days down-time of the turbine.
G. The combustion process and boiler may be regulated approx. 1% per minute considering extensive use of inconell (in stead of refractory, which may limit rate of change to 0.5% per minute). Minimum load is typically 70% of thermal input under which limit it may be difficult to comply with the requirement of min. 2 sec residence time of the flue gas at min. 850 °C after the last air injection. Below this limit it may also be a challenge to ensure sufficient superheating of the steam. Warm start-up of the combustion process is typically 8 hours and cold start-up is 8 hours.
H. Assumed low SO2-emission 1 g/GJ in 2015 considering the use of flue gas condensation by wet scrubbing down-stream the flue gas treatment system. Sulphur content in fuel 270 g/GJ.
I. Increased focus on NOx reduction is expected in the future, requiring use of SNCR technology to its utmost potential by 2020 (at 60 g/GJ) and use of the more effective catalytic SCR-technology by 2030. The SCR-technology entails additional investment.
J. N2O is expected to be related primarily to the use of SNCR using urea injection. This is why little N2O is expected when the SCR-deNOx technology is used (indicated by very low NOx-level).
K. Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
L. Fixed O&M include amongst other things the major part of staffing and maintenance, analyses, research and development, accounting, insurances, fees, memberships, office. Not included are finance cost, depreciation and amortisation.
M. Installation includes civils works (including waste bunker) and project cost
N. Assuming LOT-based tendering of electromechanical equipment. EPC contracting is expected at unchanged or slightly higher cost (0-10%), provided only construction is included in the EPC contract.
O. Through a turbine by-pass all the produced steam energy can be used for District Heat production. It can be assumed that all electricity production is converted into heat production in by-pass.
P. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll present work, range of WtE-projects
2. Emission factors of 2006: 102 g/GJ NOx, <8,3 g/GJ for SO2, <0,34 g/GJ for CH4, 1,2 g/GJ for N2O, cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. - NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.
3. Environmental permit of a new WtE-facility includes NOx limit value of 180 mg/Nm³ =100 g/GJ. Operation is expected well below limit value. Cf. Miljøstyrelsen, "Tillæg til miljøgodkendelse, Ny ovnlinje 5 på Nordforbrænding, Juni 2013," http://mst.dk/media/mst/Attachments/Tillgtilmiljgodkendelseovn5Juni2013.pdf
4. Two scenarios for adaptation of the waste incineration capacity in Denmark (in Danish: To scenarier for tilpasning af affaldsforbrændingskapaciteten i Danmark.) EA Energianalyse 2014.
5. Best Available Techniques (BAT), Reference Document for Waste Incineration. Frederik Neuwahl, Gianluca Cusano, Jorge Gómez Benavides, Simon Holbrook, Serge Roudier; Best Available Techniques (BAT) Reference Document for Waste Incineration; EUR 29971 EN; doi:10.2760/761437, DEC 2019 https://eippcb.jrc.ec.europa.eu/reference/BREF/WI/JRC118637_WI_Bref_2019_published.pdf

## 09c Straw, Large, 40 degree
Technology |  | Biomass CHP, 40/80 degree - back pressure - straw - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 41.59 | 41.59 | 41.72 | 41.72 | 39.48 | 54.62 | 40.62 | 55.84 | A
| Electrical efficiency (net, annual average) [] | 29.94% | 29.94% | 30.03% | 30.03% | 26% | 40% | 27% | 41% | [A, H] | 1
| Electrical efficiency (net, name plate) [] | 31.51% | 31.51% | 31.61% | 31.61% | 29% | 42% | 30% | 43% | [A, H] | 1
| Cb coefficient (40°C/80°C) | 0.45 | 0.45 | 0.46 | 0.46 | 0.43 | 0.6 | 0.44 | 0.61
Cv coefficient (40°C/80°C) | bar: ctrl to note
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.838% | 2.838% | 2.84% | 2.84% | 2.091% | 3.137% | 1.729% | 3.298% |  | 1
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 3 | 3 | 3 | 3 | 2.55 | 3.45 | 2.25 | 3.75
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 3 | 3 | 3 | 3 | 2.5 | 3.5 | 2 | 3.5 |  | 1
| Space requirement [1000 m2/MW_e] | 0.24 | 0.24 | 0.24 | 0.24 | 0.2 | 0.28 | 0.18 | 0.3
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: ctrl to upper
| Secondary regulation (of full load, per minute) [] | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | D | 1
| Minimum load (of full load) [] | 40% | 40% | 40% | 40% | 40% | 40% | 40% | 40%
| Warm start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | E | 1
| Cold start-up time [hours] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 95.45% | 96.36% | 99.09% | 99.82% | 90.9% | 99.82% | 95.45% | 99.91% | F | [1, 2]
| NOX [g/GJ_i] | 40 | 30 | 30 | 20 | 20 | 40 | 10 | 30 | F | [1, 2]
| CH4 [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F | [1, 2]
| N2O [g/GJ_i] | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | F | [1, 2]
| Particles [g/GJ_i] | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | F | [1, 2]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 3.46 | 3.38 | 3.21 | 2.91 | 2.86 | 3.97 | 2.35 | 3.99 | [J, K] | 1
| Nominal investment (equipment) [2015-MEUR/MW_e] | 2.14 | 2.09 | 1.98 | 1.8 | 1.73 | 2.45 | 1.43 | 2.46 | [J, K]
| Nominal investment (installation) [2015-MEUR/MW_e] | 1.33 | 1.29 | 1.23 | 1.11 | 1.13 | 1.52 | 0.92 | 1.53 | [J, K]
| Variable O&M (*total) [2015-EUR/MWh_e] | 2.11 | 2.11 | 2.1 | 2.1 | 1.62 | 2.4 | 1.42 | 2.58 | L
| Fixed O&M (*total) [2015-EUR/MW_e/y] | 126000 | 122000 | 115000 | 103000 | 103000 | 142000 | 79000 | 133000 | J
Technology-specific data
| Heat efficiency (net, annual average) [] | 70.93% | 70.93% | 70.83% | 70.83% | 48% | 74% | 47% | 73% | [B, H] | 1
| Heat efficiency (net, name plate) [] | 69.35% | 69.35% | 69.25% | 69.25% | 45% | 72% | 44% | 71% | [B, H] | 1
| Nominal investment (*total) [2015-MEUR/MW_i] | 1.09 | 1.07 | 1.01 | 0.92 | 0.9 | 1.25 | 0.74 | 1.26 | [J, K] | 1
| Nominal investment (equipment) [2015-MEUR/MW_i] | 0.67 | 0.66 | 0.63 | 0.57 | 0.55 | 0.77 | 0.45 | 0.78 | K
| Nominal investment (installation) [2015-MEUR/MW_i] | 0.42 | 0.41 | 0.39 | 0.35 | 0.36 | 0.48 | 0.29 | 0.48 | K
| Variable O&M (*total) [2015-EUR/MWh_i] | 0.66 | 0.66 | 0.66 | 0.66 | 0.51 | 0.76 | 0.45 | 0.82 | L
| Fixed O&M (*total) [2015-EUR/MW_i/y] | 39700 | 38500 | 36300 | 32400 | 32500 | 44600 | 24900 | 41900 | J
| Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | 0.06 | 0.06 | 0.06 | 0.05 | 0.06 | 0.07 | 0.05 | 0.08 | K
| Steam reheat | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | M
| Output of recovered condensate [t/MWh_i] | 0.09 | 0.09 | 0.09 | 0.09 | 0 | 0.09 | 0 | 0.09 | [C, L]
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Additional heat potential with heat pumps (of thermal input) [] | 1.768% | 1.768% | 1.768% | 1.768% | 1% | 15% | 1% | 15% | C | 1
Notes:
A. The boiler in the plant is grate fired producing steam to be used in a subsequent back pressure steam turbine. Though a grate is reasonable flexible with respect to combusting different fuels the fuel feed system will be dependent on the type of fuel used. The system is optimised at DH return temperature 40°C and flow 80°C.
B. Through a turbine by-pass all the produced steam energy can be used for District Heat production.
C. Since straw is relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
D. Secondary regulation normally relates to power production; for this type of plant it may not be of importance since load will normally follow heat consumption.
E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator).
F. For NOx-emissions no lower than 40 g/GJ SNCR is assumed. It is probably necessary to include a tail-end SCR catalyst to fulfill expected BREF requirements, particularly after year 2030. This has slight adverse effect on the electricity efficiency.
G. Warm start is starting with a glowing fuel layer on the grate and a warm deaerator.
H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
M. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949

## Sheet1
Member State | Excess Heat Available (PJ) |  |  |  |  | Excess Heat Available (TWh)
| Total | Power Plants | Existing Waste Incineration | Potential Waste Incineration | Industrial Excess Heat | Total | Power Plants | Existing Waste Incineration | Potential Waste Incineration | Industrial Excess Heat
IE | 113.577 | 94.889 | 2.831 |  | 15.857 | 31.5492 | 26.3581 | 0.78639 | 0 | 4.4047
Power Plants
Year | 2015 | 2020 | 2030
Electricity Demand |  | 31.9 | 36.3
RES-E % |  | 40% | 70%
Power Plant Production % |  | 19.14 | 10.89
Power Plant CHP Elec Eff (%) |  | 50% | 50%
Power Plant CHP Heat Eff (%) |  | 40% | 40%
Power Plant Heat Available (TWh) |  | 15.312 | 8.712
Power Plant Heat Available (TJ) |  | 55123.2 | 31363.2
Power Plant Heat Available (PJ) | 94.889 | 55.1232 | 31.3632
Excess Renewable Electricity via Heat Pump
Year |  | 2020 | 2030
Total Renewable Electricity Production |  | 12.76 | 25.41
Dispatch Down Levels (% of RES-E) |  | 12.7% | 10%
Dispatch Down (TWh) |  | 1.8563 | 2.8233
Heat Pump COP |  | 3 | 3
Excess Heat from Dispatch Down (TWh) |  | 5.5688 | 8.47
Excess Heat from Dispatch Down (TJ) |  | 20047.6701 | 30492
Excess Heat from Dispatch Down (PJ) |  | 20.0477 | 30.492
Waste Incinteration
Year | 2015 | 2020 | 2030 |  |  |  |  | 4th generation DH | Feasible with additional policy | Feasible | Very Feasible |  |  |  | https://data.cso.ie/table/E1005
Elec Capacity (MW) | 18 | 78 | 96.5 |  |  |  | 0 - 20TJ/km2 | 20 - 50 TJ/km2 | 50 - 120 TJ/km2 | 120 - 300 TJ/km2 | > 300 TJ/km2 |  |  |  | Dublin City | Very Feasible
Elec Eff | 25% | 25% | 25% |  |  | TJ heat | 311.654 | 8845.348 | 22461.8079 | 28682.7787 | 8653.6989 |  |  |  | APT | 0.35793
Total Capacity | 72 | 312 | 386 |  |  | % heat demand | 0.2956% | 8.388% | 21.3% | 27.2% | 8.207% |  | 65.1% | COM MAX | ATT | 0.59222
Capacity Factor (%) | 80% | 80% | 80% |  |  | €/GJ |  | 8 | 6 | 3.7 | 1.9 |  |  | 65% | DET | 0.05247
Heat Eff | 70% | 70% | 70% |  |  | € Capital costs (Millions) |  | 1387 | 2642 | 2080 | 322 |  |  |  | COM | 1.4264 | 211.7909
Excess Heat Available (MWh) | 353203.2 | 1530547.2 | 1893561.6 |  |  | 10% continguency |  | 1525.7 | 2906.2 | 2288 | 354.2 |  |  |  | Galway,Dublin,Cork City | Feasible
Excess Heat Available (TWh) | 0.3532 | 1.5305 | 1.8936 | [11 empty] | APT | 0.31967
Excess Heat Available (TJ) | 1271.5315 | 5509.9699 | 6816.8218 |  |  | *Above are upfront capital costs, not annualised | [8 empty] | ATT | 0.60404
Excess Heat Available (PJ) | 1.2715 | 5.51 | 6.8168 | [11 empty] | DET | 0.076291
[6 empty] | SUPPLY CUM BOUND | [5 empty] | 2018 |  |  | COM
Industrial Excess Heat |  |  |  |  | RES | Total Heating in 2018 |  | 101.7 | PJ |  | APT | 4.69 | PJ
Year | 2015 |  | 2030 |  | SRV | Total Heating in 2019 |  | 26.74 | PJ |  | ATT | 37.79 | PJ |  | Galway,Dublin, Fingal, Rathdown,Kildare,Louth,Meath,Limerick,Waterford,Galway | Feasible with additional policy + 4th Generation
Industrial Excess Heat (PJ/year) | 15.857 |  | 15.857 |  |  |  |  | 128.44 | PJ |  | DET | 59.22 | PJ |  | APT | 0.20014
[15 empty] | ATT | 0.54761
[15 empty] | DET | 0.25224
Data Centres | [14 empty] | COM
Year | 2018 | 2020 | 2030 |  | Growth in Data Centres: http://www.eirgridgroup.com/site-files/library/EirGrid/EirGrid-Group-All-Island-Generation-Capacity-Statement-2019-2028.pdf
Elec Capacity - Medium Scenario (MW) | 400 | 700 | 1400
Elec to Heat Ratio (Donna - closer to 75% but kept at 50% in case elec capacity is over estimated) | 50% | 50% | 50%
Excess Heat Available (MW) | 200 | 350 | 700
Operating Hours | 100% | 100% | 100%
Excess Heat Production (MWh) | 1752000 | 3066000 | 6132000
Excess Heat Production (TWh) | 1.752 | 3.066 | 6.132
Excess Heat Production (TJ) | 6307.2 | 11037.6 | 22075.2
Excess Heat Production (PJ) | 6.3072 | 11.0376 | 22.0752
Excess Heat Production (PJ) | 2020 | 2030
Power Plants | 55.1232 | 31.3632
Excess Renewable Electricity via Heat Pump | 20.0477 | 30.492
Waste Incinteration | 5.51 | 6.8168
Industrial Excess Heat | 15.857 | 15.857
Data Centres | 11.0376 | 22.0752
Total | 107.5754 | 106.6042
Note on A21: Author: http://www.eirgridgroup.com/site-files/library/EirGrid/2020-Qtrly-Wind-Dispatch-Down-Report.pdf
Note on C21: Author: http://www.eirgridgroup.com/site-files/library/EirGrid/2020-Qtrly-Wind-Dispatch-Down-Report.pdf
Note on D21: Author: Assuming EirGrid can keep levels at 10% - which will require a lot of work e.g. DS3, interconnection, new grid, etc.
Note on B30: Author: Meath Waste to Energy http://www.epa.ie/licences/lic_edms/090151b28031ebd2.pdf
Note on C30: Author: Dublin = 60 MW https://en.wikipedia.org/wiki/Dublin_Waste-to-Energy_Facility#:~:text=The%20plant%20is%20capable%20of,tonnes%20of%20waste%20per%20year.
Note on D30: Author: Ringiskiddy = 18.5 MW https://www.irishtimes.com/news/environment/ireland-must-not-waste-opportunities-offered-by-cross-border-deal-1.3425695
Note on A48: Author: https://www.codema.ie/images/uploads/docs/HeatNet_NWE_Transition_Roadmap_Report_Final_-_Digital.pdf

## 09a Wood Chips HOP, medium
Technology |  | Biomass boiler - boiler - wood chips - medium
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 51.64 | 51.64 | 51.64 | 51.64 | 40.38 | 51.81 | 39.66 | 51.86 | A | 1
| Heat efficiency (net, annual average) [] | 114.8% | 114.8% | 114.8% | 114.7% | 89% | 116% | 88% | 116% | [B, C] | 1
| Heat efficiency (net, name plate) [] | 114.8% | 114.8% | 114.8% | 114.7% | 89% | 116% | 88% | 116% | [B, C] | 1
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.204% | 2.204% | 2.204% | 2.203% | 2.098% | 2.459% | 1.709% | 2.455% | [C, K]
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 2 | 2 | 2 | 2 | 1.7 | 2.3 | 1.5 | 2.5
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 2 | 2 | 2 | 2 | 1.5 | 2.5 | 1.5 | 2.5 |  | 1
| Space requirement [1000 m2/MW_h] | 0.06 | 0.06 | 0.06 | 0.06 | 0.05 | 0.07 | 0.04 | 0.07
Regulation ability
Primary regulation (of full load, per 30 seconds) []
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | E | 1
| Minimum load (of full load) [] | 40% | 40% | 40% | 40% | 40% | 40% | 40% | 40% |  | 1
| Warm start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | H | 1
| Cold start-up time [hours] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 97.97% | 97.97% | 97.97% | 97.97% | 94.92% | 98.98% | 97.97% | 98.98% | G | 1
| NOX [g/GJ_i] | 90 | 60 | 40 | 30 | 40 | 80 | 20 | 40 | I | 2
| CH4 [g/GJ_i] | 16 | 11 | 8 | 4 | 4 | 16 | 2 | 16 | I | 2
| N2O [g/GJ_i] | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | I | 2
| Particles [g/GJ_i] | 2 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | I | 2
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 0.51 | 0.49 | 0.47 | 0.45 | 0.43 | 0.58 | 0.35 | 0.62 | [F, L]
| Nominal investment (equipment) [2015-MEUR/MW_h] | 0.37 | 0.36 | 0.34 | 0.34 | 0.31 | 0.43 | 0.26 | 0.46 | [F, L]
| Nominal investment (installation) [2015-MEUR/MW_h] | 0.14 | 0.13 | 0.13 | 0.11 | 0.12 | 0.16 | 0.09 | 0.16 | [F, L]
| Variable O&M (*total) [2015-EUR/MWh_h] | 2.57 | 2.7 | 3.41 | 3.76 | 2.33 | 3.68 | 3.27 | 5.27 | M
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 1.39 | 1.52 | 2.23 | 2.58 | 1.5 | 1.98 | 2.55 | 3.41 | M
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 1.18 | 1.18 | 1.18 | 1.18 | 0.82 | 1.7 | 0.72 | 1.86 | M
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 42800 | 42000 | 40500 | 38200 | 35800 | 48500 | 28800 | 48500
Technology-specific data
| Nominal investment (*total) [2015-MEUR/MW_i] | 0.58 | 0.57 | 0.54 | 0.52 | 0.49 | 0.67 | 0.4 | 0.71 | L | 1
| Nominal investment (equipment) [2015-MEUR/MW_i] | 0.42 | 0.41 | 0.39 | 0.39 | 0.36 | 0.49 | 0.3 | 0.53 | L
| Nominal investment (installation) [2015-MEUR/MW_i] | 0.16 | 0.15 | 0.14 | 0.13 | 0.13 | 0.18 | 0.11 | 0.18 | L
| Variable O&M (*total) [2015-EUR/MWh_i] | 2.95 | 3.1 | 3.91 | 4.32 | 2.68 | 3.3 | 3.77 | 4.65 | M
| Fixed O&M (*total) [2015-EUR/MW_i/y] | 49100 | 48200 | 46400 | 43900 | 41100 | 55600 | 33000 | 55700
| Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | 0.02 | 0.02 | 0.02 | 0.01 | 0.01 | 0.02 | 0.01 | 0.02 | L
| Output of recovered condensate [t/MWh_i] | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0.25 | 0 | 0.25 | D
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [D, N]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [D, N]
| Additional heat potential with heat pumps (of thermal input) [] | 1.943% | 1.943% | 1.943% | 1.944% | 1% | 26% | 1% | 28% | D | 1
Notes:
A. The plant is directly producing hot water for District Heating by burning fuel on a grate as the basis assumption. Fluid-bed combustion technology may be an alternative.It can be assumed that the data for this does not differ significantly from grate fired boilers. Data in this sheet is applicable for plants in the range of 30-49,9 MW fired capacity (heat input). The system is optimised at DH return temperature 40°C and flow 80°C.
B. Boilers larger than approx. 20 MW fuel input for hot water production are designed-for-purpose products with a high degree of fuel flexibility (type of biomass, humidity etc.)
C. Efficiencies refer to lower heating value. The stated total efficiency does NOT consider auxiliary electricity consumption. It describes the total net amount of heat produced at the plant. This is contrary to CHP where the auxiliary electricity is subtracted from the production to yield the net electricity efficiency. Direct condensation and combustion air humidification are included in all cases except in lower range of 2020 and 2050. The colder the return temperature of the district heating, the higher the total efficiency at direct condensation.
D. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
E. Load control of the heat production is important and units of this size can make rapid load variations.
F. Reference to heat output because of the lack of electricity production
G. assuming content of sulphur in fuel of 20 g/GJ
H. Warm start is starting with a glowing fuel layer on the grate.
I. Emissions shall comply with the order of the Danish EPA no 1535 of 2019 (Bekendtgørelse om miljøkrav for mellemstore fyringsanlæg), implementing the Medium Combustion Directive, Directive (EU) 2015/2193 of the European Parliament and of the Council of 25 November 2015 on the limitation of emissions of certain pollutants into the air from medium combustion plants.. It is anticipated that for the smaller units the supplier has an SNCR solution to reduce NOx emissions sufficiently. However, to reach NOx-levels below 40 g/GJ SCR is assumed.
K. Result of model calculation, there are reports of DH plants operating at lower power consumption, down to 1% of heat generation.
L. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
M. Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Electricity consumption is included for DH and associated costlisted separately, in addition. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Revenues from sale of heat are not included. Taxes are not included. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
N. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplierand operator information, or pre-project studies.
2. Estimated from emission factors of 2006: 81 g/GJ NOx, 1.9 g/GJ for SO2, <1 g/GJ for CH4, 0.8 g/GJ for N2O, 10 g/GJ for Particles; cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. - NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.