## Cover
TIMES-Ireland Model
Document type: | New Technologies
Sector(s): | Power sector (PWR)
Purpose: | Specify techno-economic data for new generation technologies
Original developer(s): | Xiufeng Yue (UCC, xiufeng.yue@ucc.ie)
James Glynn (UCC, james.glynn@ucc.ie)
Current maintainer(s): | Olexandr Balyk (UCC, olexandr.balyk@ucc.ie)
Part of TIM version: | 1
Model repository: | https://github.com/MaREI-EPMG/TIMES-Ireland-model
Licence: | CC BY-NC-SA 4.0 (unless specified otherwise)
https://creativecommons.org/licenses/by-nc-sa/4.0/

## ELC_EGP
Electricity Generators Database
Source: ETRI 2014 (https://setis.ec.europa.eu/publications/jrc-setis-reports/etri-2014 )
[5 empty] | ~FI_T: MEUR2015 | [31 empty] | ~FI_Process
TechName | *Cost data Source | *Effieiency Data source | *TechDesc | Comm-IN | Comm-OUT | EFF | EFF~2020 | EFF~2030 | EFF~2040 | EFF~2050 | Start | INVCOST~2015 | INVCOST~2020 | INVCOST~2030 | INVCOST~2040 | INVCOST~2050 | FIXOM | FIXOM~2020 | FIXOM~2030 | FIXOM~2040 | FIXOM~2050 | VAROM | VAROM~2020 | VAROM~2030 | VAROM~2040 | VAROM~2050 | LIFE | LIFE~2020 | LIFE~2030 | Cap2Act | AFA | AFA~2020 | AFA~2030 | AFA~2040 | AFA~2050 |  | Sets | TechName | TechDesc | Tact | Tcap | Tslvl | PrimaryCG | Vintage
*Technology Name |  |  | Technology Description | Input Commodity | Output Commodity | Efficiency | [5 empty] | CAPEX REF (€2013/kW) |  |  |  |  | FOM (€2013/kW) |  |  |  |  | VOM (€2013/GJ) |  |  |  |  | Technical life |  |  |  | Max. capacity factor | [5 empty] | *Process Set Membership | Technology Name | Technology Description | Activity Unit | Capacity Unit | TimeSlice Level | Primary CommGrp | Vintage Tracking
P-RNW-WIN-OF02 | ETRI2018 |  | PWR Offshore wind new | PWRWIN | ELCC | 100% |  |  |  |  | 2019 | 3500 | 2870 | 2570 | 2430 | 2330 | 128.39 | 92.16 | 77.4 | 66.64 | 52.44 | [5 empty] | 20 | 25 | 30 | 31.536 | [6 empty] | ELE | P-RNW-WIN-OF02 | PWR Offshore wind new | PJ | GW | DAYNITE |  |  | Offshore wind
P-RNW-SOL-PV01 | ETRI2018 |  | PWR Commercial solar PV system 0.1-2 MW new | PWRSOL | ELCC | 100% |  |  |  |  | 2019 | 1140 | 880 | 670 | 510 | 410 | 27.5 | 22.5 | 20.25 | 19 | 18 | [5 empty] | 25 |  |  | 31.536 | [6 empty] | ELE | P-RNW-SOL-PV01 | PWR Commercial solar PV system 0.1-2 MW new | PJ | GW | DAYNITE |  |  | Commercial solar PV system 0.1-2 MW
P-RNW-SOL-PV02 | ETRI2018 |  | PWR Commercial solar PV >2 MW without tracking new | PWRSOL | ELCC | 100% |  |  |  |  | 2019 | 1020 | 790 | 600 | 450 | 370 | 16.66 | 13.6 | 10.88 | 9.86 | 8.84 | [5 empty] | 25 |  |  | 31.536 | [6 empty] | ELE | P-RNW-SOL-PV02 | PWR Commercial solar PV >2 MW without tracking new | PJ | GW | DAYNITE |  |  | Commercial solar PV >2 MW without tracking
P-RNW-SOL-PV03 | ETRI2018 |  | PWR Commercial solar PV >2 MW with tracking new | PWRSOL | ELCC | 100% |  |  |  |  | 2019 | 1120 | 860 | 650 | 500 | 410 | 21.75 | 16.5 | 13.35 | 11.85 | 10.65 | [5 empty] | 25 |  |  | 31.536 | [6 empty] | ELE | P-RNW-SOL-PV03 | PWR Commercial solar PV >2 MW with tracking new | PJ | GW | DAYNITE |  |  | Commercial solar PV >2 MW with tracking
P-RNW-SOL-CSP04 | ETRI2014 |  | PWR Solar thermal electricity power plants without thermal storage (power/heat=0.38) new | PWRSOL | ELCC | 36% |  |  |  |  | 2019 | 5600 | 4500 | 3800 | 3500 | 3400 | 224 | 180 | 152 | 140 | 136 | 0.448 | 0.36 | 0.304 | 0.28 | 0.272 | 30 |  |  | 31.536 | 42% | [5 empty] | ELE | P-RNW-SOL-CSP04 | PWR Solar thermal electricity power plants without thermal storage (power/heat=0.38) new | PJ | GW | DAYNITE |  |  | Solar thermal electricity power plants without thermal storage (power/heat=0.38)
P-RNW-HYD-DAM01 | ETRI2018 |  | PWR Hydropower dam and reservoir, >100 MW new | PWRHYD | ELCC | 100% |  |  |  |  | 2019 | 3500 | 3500 | 3490 | 3480 | 3470 | 22 | 22 | 22 | 22 | 22 | 0.066 | 0.066 | 0.066 | 0.066 | 0.066 | 60 |  |  | 31.536 | 35% | [5 empty] | ELE | P-RNW-HYD-DAM01 | PWR Hydropower dam and reservoir, >100 MW new | PJ | GW | DAYNITE |  |  | Hydropower dam and reservoir, >100 MW
P-RNW-HYD-DAM02 | ETRI2018 |  | PWR Hydropower dam and reservoir, 10-100 MW new | PWRHYD | ELCC | 100% |  |  |  |  | 2019 | 4000 | 4000 | 3980 | 3970 | 3970 | 49.5 | 50.4 | 50.55 | 50.55 | 50.55 | 0.165 | 0.168 | 0.1685 | 0.1685 | 0.1685 | 60 |  |  | 31.536 | 40% | [5 empty] | ELE | P-RNW-HYD-DAM02 | PWR Hydropower dam and reservoir, 10-100 MW new | PJ | GW | DAYNITE |  |  | Hydropower dam and reservoir, 10-100 MW
P-RNW-HYD-DAM03 | ETRI2018 |  | PWR Hydropower dam and reservoir, <10 MW new | PWRHYD | ELCC | 100% |  |  |  |  | 2019 | 5000 | 5000 | 4980 | 4970 | 4960 | 66 | 67.2 | 67.5 | 67.5 | 67.5 | 0.22 | 0.224 | 0.225 | 0.225 | 0.225 | 60 |  |  | 31.536 | 37% | [5 empty] | ELE | P-RNW-HYD-DAM03 | PWR Hydropower dam and reservoir, <10 MW new | PJ | GW | DAYNITE |  |  | Hydropower dam and reservoir, <10 MW
P-RNW-HYD-ROR04 | ETRI2018 |  | PWR Hydropower run-of-a-river new | PWRHYD | ELCC | 100% |  |  |  |  | 2019 | 3000 | 3000 | 2990 | 2980 | 2970 | 82.5 | 84 | 84.3 | 84.3 | 84.3 | 0.275 | 0.28 | 0.281 | 0.281 | 0.281 | 60 |  |  | 31.536 | 37% | [5 empty] | ELE | P-RNW-HYD-ROR04 | PWR Hydropower run-of-a-river new | PJ | GW | DAYNITE |  |  | Hydropower run-of-a-river
P-RNW-GEO01 | ETRI2018 | ETRI2014 | PWR Flash power plant extracting fluid from hydrothermal system at 2.5 km depth new | PWRGEO | ELCC | 10% | 10% | 10% | 10% | 10% | 2019 | 3540 | 3350 | 3150 | 3020 | 2910 | 77.42 | 79.52 | 80.46 | 80.4 | 79.42 | [5 empty] | 30 |  |  | 31.536 | 95% | [5 empty] | ELE | P-RNW-GEO01 | PWR Flash power plant extracting fluid from hydrothermal system at 2.5 km depth new | PJ | GW | DAYNITE |  |  | Flash power plant extracting fluid from hydrothermal system at 2.5 km depth
P-RNW-GEO02 | ETRI2018 | ETRI2014 | PWR Organic Rankine Cycle hydrothermal system. new | PWRGEO | ELCC | 10% | 10% | 10% | 10% | 10% | 2019 | 6970 | 6600 | 6190 | 5950 | 5720 | 146.37 | 145.2 | 143.52 | 146.75 | 148.77 | [5 empty] | 30 |  |  | 31.536 | 95% | [5 empty] | ELE | P-RNW-GEO02 | PWR Organic Rankine Cycle hydrothermal system. new | PJ | GW | DAYNITE |  |  | Organic Rankine Cycle hydrothermal system.
P-RNW-GEO03 | ETRI2014 | ETRI2014 | PWR Organic Rankine Cycle Enhanced Geothermal System at 5.5 km depth new | PWRGEO | ELCC | 10% | 10% | 10% | 10% | 10% | 2019 | 12600 | 10300 | 9000 | 8600 | 8200 | 226.8 | 185.4 | 171 | 163.4 | 155.8 | [5 empty] | 30 |  |  | 31.536 | 95% | [5 empty] | ELE | P-RNW-GEO03 | PWR Organic Rankine Cycle Enhanced Geothermal System at 5.5 km depth new | PJ | GW | DAYNITE |  |  | Organic Rankine Cycle Enhanced Geothermal System at 5.5 km depth
P-RNW-OCE-WAV01 | ETRI2018 |  | PWR Wave energy new | PWROCE | ELCC | 100% |  |  |  |  | 2019 | 7910 | 6310 | 5320 | 4040 | 3240 | 326.88 | 237.39 | 210.56 | 153.7 | 133.4 | [5 empty] | 20 |  |  | 31.536 | 36% | [5 empty] | ELE | P-RNW-OCE-WAV01 | PWR Wave energy new | PJ | GW | DAYNITE |  |  | Wave energy
P-RNW-OCE-TID02 | ETRI2018 |  | PWR Tidal energy new | PWROCE | ELCC | 100% |  |  |  |  | 2019 | 7840 | 6260 | 5270 | 4000 | 3210 | 363.8 | 158.4 | 117.8 | 90.3 | 93.1 | [5 empty] | 20 |  |  | 31.536 | 36% | [5 empty] | ELE | P-RNW-OCE-TID02 | PWR Tidal energy new | PJ | GW | DAYNITE |  |  | Tidal energy
P-TH-OCGT-GAS01 | ETRI2014 |  | PWR Open-Cycle Gas Turbine conventional new | PWRGAS | ELCC | 38% |  |  |  |  | 2019 | 770 |  |  |  |  | 7.7 | [9 empty] | 30 |  |  | 31.536 | 95% | [5 empty] | ELE | P-TH-OCGT-GAS01 | PWR Open-Cycle Gas Turbine conventional new | PJ | GW | DAYNITE |  |  | Open-Cycle Gas Turbine conventional
P-TH-OCGT-GAS02 | ETRI2014 |  | PWR Open Cycle Gas Turbine advanced new | PWRGAS | ELCC | 40% | 40% | 43% | 44% | 45% | 2019 | 550 | 550 | 550 | 550 | 550 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 0.0605 | 0.0605 | 0.0605 | 0.0605 | 0.0605 | 30 |  |  | 31.536 | 95% | [5 empty] | ELE | P-TH-OCGT-GAS02 | PWR Open Cycle Gas Turbine advanced new | PJ | GW | DAYNITE |  |  | Open Cycle Gas Turbine advanced
P-TH-CCGT-GAS03 | ETRI2014 | ETRI2014 | PWR Combined Cycle Gas Turbine advanced new | PWRGAS | ELCC | 58% | 60% | 62% | 62% | 63% | 2019 | 850 | 850 | 850 | 850 | 850 | 21.25 | 21.25 | 21.25 | 21.25 | 21.25 | 0.017 | 0.017 | 0.017 | 0.017 | 0.017 | 30 |  |  | 31.536 | 90% | [5 empty] | ELE | P-TH-CCGT-GAS03 | PWR Combined Cycle Gas Turbine advanced new | PJ | GW | DAYNITE |  |  | Combined Cycle Gas Turbine advanced
P-TH-SC-COA01 | ETRI2014 | ETRI2014 | PWR Pulverised coal supercritical new | PWRCOA | ELCC | 45% | 46% | 48% | 48% | 48% | 2019 | 1600 | 1600 | 1600 | 1600 | 1600 | 40 | 40 | 40 | 40 | 40 | 0.0576 | 0.0576 | 0.0576 | 0.0576 | 0.0576 | 40 |  |  | 31.536 | 90% | [5 empty] | ELE | P-TH-SC-COA01 | PWR Pulverised coal supercritical new | PJ | GW | DAYNITE |  |  | Pulverised coal supercritical
P-TH-FB-PEA01 | ETRI2014 | ETRI2014 | PWR Pulverised peat supercritical new | PWRPEA | ELCC | 42% | 45% | 47% | 47% | 47% | 2019 | 2000 | 2000 | 2000 | 2000 | 2000 | 50 | 50 | 50 | 50 | 50 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 40 |  |  | 31.536 | 90% | [5 empty] | ELE | P-TH-FB-PEA01 | PWR Pulverised peat supercritical new | PJ | GW | DAYNITE |  |  | Pulverised peat supercritical
P-TH-SC-PEA02 | ETRI2014 | ETRI2014 | PWR Supercritical fluidized bed peat new | PWRPEA | ELCC | 42% | 43% | 45% | 45% | 45% | 2019 | 1900 | 1900 | 1900 | 1900 | 1900 | 38 | 38 | 38 | 38 | 38 | 0.114 | 0.114 | 0.114 | 0.114 | 0.114 | 40 |  |  | 31.536 | 85% | [5 empty] | ELE | P-TH-SC-PEA02 | PWR Supercritical fluidized bed peat new | PJ | GW | DAYNITE |  |  | Supercritical fluidized bed peat
P-TH-IGCC-COA03 | ETRI2014 | ETRI2014 | PWR Integrated Gasification Combined Cycle coal new | PWRCOA | ELCC | 45% | 46% | 46% | 47% | 50% | 2019 | 2500 | 2300 | 2300 | 2300 | 2200 | 62.5 | 57.5 | 57.5 | 57.5 | 55 | 0.125 | 0.115 | 0.115 | 0.115 | 0.11 | 35 |  |  | 31.536 | 90% | [5 empty] | ELE | P-TH-IGCC-COA03 | PWR Integrated Gasification Combined Cycle coal new | PJ | GW | DAYNITE |  |  | Integrated Gasification Combined Cycle coal
P-TH-IGCC-PEA03 | ETRI2014 | ETRI2014 | PWR Integrated Gasification Combined Cycle peat new | PWRPEA | ELCC | 43% | 45% | 46% | 47% | 47% | 2019 | 3100 | 3000 | 3000 | 3000 | 3000 | 93 | 90 | 90 | 90 | 90 | 0.217 | 0.21 | 0.21 | 0.21 | 0.21 | 35 |  |  | 31.536 | 90% | [5 empty] | ELE | P-TH-IGCC-PEA03 | PWR Integrated Gasification Combined Cycle peat new | PJ | GW | DAYNITE |  |  | Integrated Gasification Combined Cycle peat
*P-TH-CCGT-GAS-CCS04 | ETRI2018 | ETRI2014 | PWR CCGT advanced CCS post combustion new | PWRGAS | ELCC | 50% | 52% | 55% | 55% | 55% | 2030 |  |  | 1390 | 1310 | 1280 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 30 |  |  | 31.536 | 90% | [5 empty] | ELE | *P-TH-CCGT-GAS-CCS04 | PWR CCGT advanced CCS post combustion new | PJ | GW | DAYNITE |  |  | CCGT advanced CCS post combustion
*P-TH-SC-COA-CCS04 | ETRI2018 | ETRI2014 | PWR Pulverised coal supercritical CCS post-combustion new | PWRCOA | ELCC | 34% | 35% | 35% | 38% | 38% | 2030 |  |  | 2740 | 2590 | 2570 | 75 | 67.5 | 63.75 | 63.75 | 63.75 | 0.165 | 0.1485 | 0.14025 | 0.14025 | 0.14025 | 40 |  |  | 31.536 | 90% | [5 empty] | ELE | *P-TH-SC-COA-CCS04 | PWR Pulverised coal supercritical CCS post-combustion new | PJ | GW | DAYNITE |  |  | Pulverised coal supercritical CCS post-combustion
*P-TH-FB-PEA-CCS04 | ETRI2014 | ETRI2014 | PWR Fluidised bed peat CCS post combustion new | PWRPEA | ELCC | 31% | 32% | 34% | 34% | 34% | 2030 | 3500 | 3500 | 3500 | 3500 | 3500 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 40 |  |  | 31.536 | 85% | [5 empty] | ELE | *P-TH-FB-PEA-CCS04 | PWR Fluidised bed peat CCS post combustion new | PJ | GW | DAYNITE |  |  | Fluidised bed peat CCS post combustion
*P-TH-SC-COA-CCS05 | ETRI2018 | ETRI2014 | PWR Pulverised coal supercritical CCS oxyfuel new | PWRCOA | ELCC | 36% | 37% | 39% | 40% | 40% | 2030 |  |  | 2690 | 2490 | 2470 | 75 | 67.5 | 63.75 | 63.75 | 63.75 | 0.09 | 0.081 | 0.0765 | 0.0765 | 0.0765 | 40 |  |  | 31.536 | 90% | [5 empty] | ELE | *P-TH-SC-COA-CCS05 | PWR Pulverised coal supercritical CCS oxyfuel new | PJ | GW | DAYNITE |  |  | Pulverised coal supercritical CCS oxyfuel
*P-TH-IGCC-COA-CCS06 | ETRI2018 | ETRI2014 | PWR IGCC coal CCS pre-combustion new | PWRCOA | ELCC | 35% | 37% | 40% | 41% | 44% | 2030 |  |  | 2540 | 2220 | 2180 | 93 | 86.55 | 84.75 | 84.75 | 84.75 | 0.186 | 0.1731 | 0.1695 | 0.1695 | 0.1695 | 35 |  |  | 31.536 | 90% | [5 empty] | ELE | *P-TH-IGCC-COA-CCS06 | PWR IGCC coal CCS pre-combustion new | PJ | GW | DAYNITE |  |  | IGCC coal CCS pre-combustion
*P-TH-IGCC-PEA-CCS05 | ETRI2018 | ETRI2014 | PWR IGCC peat CCS pre combustion new | PWRPEA | ELCC | 35% | 37% | 40% | 41% | 41% | 2030 |  |  | 3870 | 3380 | 3310 | 103.5 | 100.51 | 100.51 | 100.51 | 100.51 | 0.36 | 0.3496 | 0.3496 | 0.3496 | 0.3496 | 35 |  |  | 31.536 | 90% | [5 empty] | ELE | *P-TH-IGCC-PEA-CCS05 | PWR IGCC peat CCS pre combustion new | PJ | GW | DAYNITE |  |  | IGCC peat CCS pre combustion
P-RNW-FB-BIO01 | ETRI2014 | ETRI2014 | PWR Biomass grate furnace steam turbine new | PWRBIO | ELCC | 34% | 35% | 36% | 38% | 38% | 2019 | 2890 | 2620 | 2370 | 2150 | 1950 | 63.58 | 57.64 | 52.14 | 47.3 | 42.9 | 0.10115 | 0.0917 | 0.08295 | 0.07525 | 0.06825 | 25 |  |  | 31.536 | 90% | [5 empty] | ELE | P-RNW-FB-BIO01 | New Power Plant - Biomass grate furnace steam turbine | PJ | GW | DAYNITE |  |  | Biomass grate furnace steam turbine
P-RNW-ST-BIO02 | ETRI2014 | ETRI2014 | PWR Fluidised bed boiler (circulating or bubbling) plus steam turbine new | PWRBIO | ELCC | 35% | 36% | 37% | 38% | 39% | 2019 | 2960 | 2620 | 2330 | 2060 | 1830 | 53.28 | 47.16 | 41.94 | 37.08 | 32.94 | 0.11248 | 0.09956 | 0.08854 | 0.07828 | 0.06954 | 25 |  |  | 31.536 | 90% | [5 empty] | ELE | P-RNW-ST-BIO02 | New Power Plant - Fluidised bed boiler (circulating or bubbling) plus steam turbine | PJ | GW | DAYNITE |  |  | Fluidised bed boiler (circulating or bubbling) plus steam turbine
P-RNW-IGCC-BIO03 | ETRI2014 | ETRI2014 | PWR Biomass IGCC new | PWRBIO | ELCC | 35% | 37% | 43% | 47% | 48% | 2019 | 4810 | 3810 | 3140 | 2840 | 2560 | 105.82 | 83.82 | 69.08 | 62.48 | 56.32 | 0.39442 | 0.31242 | 0.25748 | 0.23288 | 0.20992 | 25 |  |  | 31.536 | 90% | [5 empty] | ELE | P-RNW-IGCC-BIO03 | New Power Plant - Biomass IGCC | PJ | GW | DAYNITE |  |  | Biomass IGCC
P-RNW-AB-BIO04 | ETRI2018 | ETRI2014 | PWR Anaerobic digestion new | PWRBIO | ELCC | 36% | 38% | 40% | 42% | 45% | 2019 | 3100 | 2860 | 2740 | 2630 | 2510 | 159.08 | 130.38 | 113.16 | 103.32 | 94.3 | 0.12028 | 0.09858 | 0.08556 | 0.07812 | 0.0713 | 20 |  |  | 31.536 | 90% | [5 empty] | ELE | P-RNW-AB-BIO04 | New Power Plant - Anaerobic digestion | PJ | GW | DAYNITE |  |  | Anaerobic digestion
P-RNW-ST-MSW04 | ETRI2014 | ETRI2014 | PWR Municipal solid waste incinerator new | PWRMSW | ELCC | 27% | 31% | 34% | 37% | 42% | 2019 | 6080 | 5630 | 5240 | 4870 | 4540 | 182.4 | 168.9 | 157.2 | 146.1 | 136.2 | 0.41952 | 0.38847 | 0.36156 | 0.33603 | 0.31326 | 25 |  |  | 31.536 | 90% | [5 empty] | ELE | P-RNW-ST-MSW04 | New Power Plant - Municipal solid waste incinerator | PJ | GW | DAYNITE |  |  | Municipal solid waste incinerator
Source: UK TIMES (for H2)
|  |  | ~FI_T: MEUR2012 | [31 empty] | ~FI_Process
TechName | *TechDesc | Comm-IN | Comm-OUT | EFF | EFF~2020 | EFF~2030 | EFF~2040 | EFF~2050 | Start | INVCOST | INVCOST~2020 | INVCOST~2030 | INVCOST~2040 | INVCOST~2050 | FIXOM | FIXOM~2020 | FIXOM~2030 | FIXOM~2040 | FIXOM~2050 | VAROM | VAROM~2020 | VAROM~2030 | VAROM~2040 | VAROM~2050 | LIFE | LIFE~2020 | LIFE~2030 | Cap2Act | AFA | AFA~2020 | AFA~2030 | AFA~2040 | AFA~2050 |  | Sets | TechName | TechDesc | Tact | Tcap | Tslvl | PrimaryCG | Vintage
*Technology Name | Technology Description | Input Commodity | Output Commodity | Efficiency | [5 empty] | CAPEX REF (€2012/kW) |  |  |  |  | FOM (€2013/kW) |  |  |  |  | VOM (€2013/GJ) |  |  |  |  | Technical life |  |  |  | Max. capacity factor | [5 empty] | *Process Set Membership | Technology Name | Technology Description | Activity Unit | Capacity Unit | TimeSlice Level | Primary CommGrp | Vintage Tracking
P-TH-OCGT-H2-01 | New Power Plant - Hydrogen Open Cycle Gas Turbine | PWRH2G | ELCC |  | 42.73% |  |  |  | 2030 | 520.8233 | 515.5077 | 509.7536 | 504.712 | [11 empty] | 30 |  |  | 31.536 | 91.2% | [5 empty] | ELE | P-TH-OCGT-H2-01 | New Power Plant - Hydrogen Open Cycle Gas Turbine | PJ | GW | DAYNITE
P-TH-CCGT-H2-02 | New Power Plant - Hydrogen Combined Cycle Gas Turbine | PWRH2G | ELCC |  | 59% |  |  |  | 2030 | 700.2967 | 690.7669 | 680.451 | 671.4124 | [11 empty] | 35 |  |  | 31.536 | 91.2% | [6 empty] | P-TH-CCGT-H2-02 | New Power Plant - Hydrogen Combined Cycle Gas Turbine | PJ | GW | DAYNITE
Note on AQ4: Possible TsLvl ANNUAL (Annual level) SEASON (Seasonal level) WEEKLY (Weekly level) DAYNITE (day and night level)
Note on AS4: Possible Vintage NO (if empty by default mean NO) YES
Note on AL5: Sets declarations are NOT inherited. Possible Process Sets ELE (Thermal Electric Power Plant) CHP (Combined Heat and Power) STGTSS (Pump Storage) PRE (Genric Process/Technology) DMD (Demand Device) IMP (Import) EXP (Export) MIN (Mining Process) RNW (Renewable Technology) HPL (Heating Plant)
Note on AO43: Possible TsLvl ANNUAL (Annual level) SEASON (Seasonal level) WEEKLY (Weekly level) DAYNITE (day and night level)
Note on AQ43: Possible Vintage NO (if empty by default mean NO) YES
Note on AJ44: Sets declarations are NOT inherited. Possible Process Sets ELE (Thermal Electric Power Plant) CHP (Combined Heat and Power) STGTSS (Pump Storage) PRE (Genric Process/Technology) DMD (Demand Device) IMP (Import) EXP (Export) MIN (Mining Process) RNW (Renewable Technology) HPL (Heating Plant)

## IMPEXP
Electricity Interconnector | [5 empty] | ~FI_T: MEUR2014 | [10 empty] | ~FI_Process
Region | TechName | *TechDesc | Comm-IN | Comm-OUT | Year | LimType | NCAP_START | NCAP_TLIFE | PRC_CAPACT | COST~2015 | COST~2020 | COST~2030 | COST~2040 | COST~2050 | CAP_BND | CAP_BND~0 | Sets | Region | TechName | TechDesc | Tact | Tcap | Tslvl | PrimaryCG | Vintage
*Region Name | Technology Name | Technology Description | [7 empty] | Euro/GJ | Euro/GJ | Euro/GJ | Euro/GJ | Euro/GJ | GW | GW | *Process Set Membership | Region Name | Technology Name | Technology Description | Activity Unit | Capacity Unit | TimeSlice level of Process Activity | Primary Commodity Group | Vintage Tracking
IE,National | IMPELC_FR-CI | Import of Electricity - France Celtic Interconnector |  | ELCC | 2026 | FX | 2026 | 100 | 31.536 | 12.7752 | 13.8447 | 20.6996 | 24.1002 | 27.9704 | 0.7 | 5 | IMP | IE,National | IMPELC_FR-CI | Import of Electricity - France Celtic Interconnector | PJ | GW | DAYNITE
IE,National | EXPELC_FR-CI | Export of Electricity - France Celtic Interconnector | ELCC |  | 2026 | FX | 2026 | 100 | 31.536 | 8.9427 | 9.6913 | 14.4898 | 16.8701 | 19.5793 | 0.7 | 5 | EXP | IE,National | EXPELC_FR-CI | Export of Electricity - France Celtic Interconnector | PJ | GW | DAYNITE
IE,National | IMPELC_UK-GL | Import of Electricity - UK Greenlink |  | ELCC | 2024 | FX | 2024 | 100 | 31.536 | 12.7752 | 13.8447 | 20.6996 | 24.1002 | 27.9704 | 0.5 | 5 | IMP | IE,National | IMPELC_UK-GL | Import of Electricity - UK Greenlink | PJ | GW | DAYNITE
IE,National | EXPELC_UK-GL | Export of Electricity - UK Greenlink | ELCC |  | 2024 | FX | 2024 | 100 | 31.536 | 8.9427 | 9.6913 | 14.4898 | 16.8701 | 19.5793 | 0.5 | 5 | EXP | IE,National | EXPELC_UK-GL | Export of Electricity - UK Greenlink | PJ | GW | DAYNITE

## ELC_WIN
|  |  | ~FI_T: MEUR2015 | [30 empty] | ~FI_Process
TechName | *TechDesc | Comm-IN | Comm-OUT | EFF | EFF~2020 | EFF~2030 | EFF~2040 | EFF~2050 | Start | INVCOST | INVCOST~2020 | INVCOST~2030 | INVCOST~2040 | INVCOST~2050 | FIXOM | FIXOM~2020 | FIXOM~2030 | FIXOM~2040 | FIXOM~2050 | VAROM | VAROM~2020 | VAROM~2030 | VAROM~2040 | VAROM~2050 | LIFE | LIFE~2020 | LIFE~2030 | Cap2Act | AFA | AFA~2020 | AFA~2030 | AFA~2040 | AFA~2050 | Sets | TechName | TechDesc | Tact | Tcap | Tslvl | PrimaryCG | Vintage
*Technology Name | Technology Description | Input Commodity | Output Commodity | Efficiency | [5 empty] | CAPEX REF (€2013/kW) |  |  |  |  | FOM (€2013/kW) |  |  |  |  | VOM (€2013/GJ) |  |  |  |  | Technical life |  |  |  | Max. capacity factor |  |  |  |  | *Process Set Membership | Technology Name | Technology Description | Activity Unit | Capacity Unit | TimeSlice Level | Primary CommGrp | Vintage Tracking
P-RNW-WIN-ON01 | New Power Plant - Onshore Wind - Connection Cost Level 01 | PWRWIN | ELCC | 1 |  |  |  |  | 2019 | 1374.5378 | 1314.5378 | 1214.5378 | 1164.5378 | 1134.5378 | 37.8 | 32.4 | 28.6 | 22.8 | 18.7 | [5 empty] | 20 | 22 | 25 | 31.536 | [5 empty] | ELE | P-RNW-WIN-ON01 | New Power Plant - Onshore Wind - Connection Cost Level 01 | PJ | GW | DAYNITE
P-RNW-WIN-ON02 | New Power Plant - Onshore Wind - Connection Cost Level 02 | PWRWIN | ELCC | 1 |  |  |  |  | 2019 | 1413.3292 | 1353.3292 | 1253.3292 | 1203.3292 | 1173.3292 | 37.8 | 32.4 | 28.6 | 22.8 | 18.7 | [5 empty] | 20 | 22 | 25 | 31.536 | [5 empty] | ELE | P-RNW-WIN-ON02 | New Power Plant - Onshore Wind - Connection Cost Level 02 | PJ | GW | DAYNITE
P-RNW-WIN-ON03 | New Power Plant - Onshore Wind - Connection Cost Level 03 | PWRWIN | ELCC | 1 |  |  |  |  | 2019 | 1482.2844 | 1422.2844 | 1322.2844 | 1272.2844 | 1242.2844 | 37.8 | 32.4 | 28.6 | 22.8 | 18.7 | [5 empty] | 20 | 22 | 25 | 31.536 | [5 empty] | ELE | P-RNW-WIN-ON03 | New Power Plant - Onshore Wind - Connection Cost Level 03 | PJ | GW | DAYNITE
P-RNW-WIN-ON04 | New Power Plant - Onshore Wind - Connection Cost Level 04 | PWRWIN | ELCC | 1 |  |  |  |  | 2019 | 1634.767 | 1574.767 | 1474.767 | 1424.767 | 1394.767 | 37.8 | 32.4 | 28.6 | 22.8 | 18.7 | [5 empty] | 20 | 22 | 25 | 31.536 | [5 empty] | ELE | P-RNW-WIN-ON04 | New Power Plant - Onshore Wind - Connection Cost Level 04 | PJ | GW | DAYNITE
P-RNW-WIN-ON05 | New Power Plant - Onshore Wind - Connection Cost Level 05 | PWRWIN | ELCC | 1 |  |  |  |  | 2019 | 1992.4211 | 1932.4211 | 1832.4211 | 1782.4211 | 1752.4211 | 37.8 | 32.4 | 28.6 | 22.8 | 18.7 | [5 empty] | 20 | 22 | 25 | 31.536 | [5 empty] | ELE | P-RNW-WIN-ON05 | New Power Plant - Onshore Wind - Connection Cost Level 05 | PJ | GW | DAYNITE

## WIN_ON_COST
fid | Merged_ID | Parcel | COUNTY - 1 | COUNTY - 2 | Station ID | name | operator | voltage | voltage_pr | voltage_te | Distance | Round Up Distance | Area_km_2_ | Class | Area With Packing Density Applied(km2) | Rationalised Output Per Parcel (MW) | Rationalised Output Per Parcel (MW) | Cost (€) | PS | Cost Per MW | Watt per Euro | [7 empty] | Investment Cost
1 | 1 | CL1-001 | KERRY | KERRY | SS-636 | Garranebane 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 15.861 | 16 | 0.122 | 1 | 0.122 | 3.45 | 3.45 | 1703340 | 1 | 493721.7391 | 2.0254 | Rationalised Output Per Parcel (MW) | Connection Cost Million E/Kw | [5 empty] | 2015 | 2020 | 2030 | 2040 | 2050
2 | 2 | CL1-002 | KERRY | KERRY | SS-636 | Garranebane 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.42 | 6 | 0.263 | 1 | 0.263 | 3.45 | 3.45 | 769410 | 4 | 223017.3913 | 4.484 | 3.45 | 493.7217 | Capacity | Total Connection Cost | Cost Range |  | Connection Cost (Euro/kW) | 1350 | 1290 | 1190 | 1140 | 1110
3 | 3 | CL1-003 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.691 | 12 | 0.133 | 1 | 0.133 | 3.45 | 3.45 | 1492540 | 1 | 432620.2899 | 2.3115 | 3.45 | 223.0174 | 8.1111 | 199028.83 | 0 | 30 | 24.5378 | 1374.5378 | 1314.5378 | 1214.5378 | 1164.5378 | 1134.5378
4 | 4 | CL1-004 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 13.24 | 14 | 0.133 | 1 | 0.133 | 3.45 | 3.45 | 1597940 | 1 | 463171.0145 | 2.159 | 3.45 | 432.6203 | 8.7322 | 338735.64 | 30 | 50 | 38.7913 | 1413.3292 | 1353.3292 | 1253.3292 | 1203.3292 | 1173.3292
5 | 5 | CL1-005 | DONEGAL | DONEGAL | SS-138 | Creeslough 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.962 | 10 | 0.157 | 1 | 0.157 | 3.45 | 3.45 | 1387140 | 1 | 402069.5652 | 2.4871 | 3.45 | 463.171 | 5.7897 | 399230.19 | 50 | 100 | 68.9552 | 1482.2844 | 1422.2844 | 1322.2844 | 1272.2844 | 1242.2844
6 | 6 | CL1-006 | DONEGAL | DONEGAL | SS-119 | Drumlough Hill (1) 38kV Substation | ESB Networks | 38000 | low | 38000 | 10.639 | 11 | 0.093 | 1 | 0.093 | 3.45 | 3.45 | 1439840 | 1 | 417344.9275 | 2.3961 | 3.45 | 402.0696 | 3.9777 | 606529.79 | 100 | 200 | 152.4825 | 1634.767 | 1574.767 | 1474.767 | 1424.767 | 1394.767
7 | 7 | CL1-007 | CLARE | CLARE | SS-708 |  | EirGrid | 110000 | medium | 110000 | 1.526 | 2 | 0.126 | 1 | 0.126 | 3.45 | 3.45 | 1340080 | 11 | 388428.9855 | 2.5745 | 3.45 | 417.3449 | 3.9907 | 1427308.23 | 200 | 1000 | 357.6541 | 1992.4211 | 1932.4211 | 1832.4211 | 1782.4211 | 1752.4211
8 | 8 | CL1-008 | DUBLIN | DUBLIN | SS-014 | Ballyboden 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 6.009 | 7 | 0.28 | 1 | 0.28 | 3.45 | 3.45 | 839680 | 4 | 243385.5072 | 4.1087 | 3.45 | 388.429
9 | 9 | CL1-009 | DUBLIN | DUBLIN | SS-014 | Ballyboden 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 5.282 | 6 | 0.178 | 1 | 0.178 | 3.45 | 3.45 | 769410 | 4 | 223017.3913 | 4.484 | 3.45 | 243.3855
10 | 10 | CL1-010 | WICKLOW | WICKLOW | SS-010 | Fassaroe 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 4.695 | 5 | 0.2 | 1 | 0.2 | 3.45 | 3.45 | 1679970 | 7 | 486947.8261 | 2.0536 | 3.45 | 223.0174
11 | 11 | CL1-011 | WICKLOW | WICKLOW | SS-010 | Fassaroe 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.608 | 6 | 0.116 | 1 | 0.116 | 3.45 | 3.45 | 1732670 | 7 | 502223.1884 | 1.9911 | 3.45 | 486.9478
12 | 12 | CL1-012 | WICKLOW | WICKLOW | SS-597 | Kilmartin 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.924 | 6 | 0.134 | 1 | 0.134 | 3.45 | 3.45 | 769410 | 4 | 223017.3913 | 4.484 | 3.45 | 502.2232
13 | 13 | CL1-013 | CORK | CORK | SS-253 | Ballydehob 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.843 | 9 | 0.139 | 1 | 0.139 | 3.45 | 3.45 | 1334440 | 1 | 386794.2029 | 2.5854 | 3.45 | 223.0174
14 | 14 | CL1-014 | WICKLOW | WICKLOW | SS-037 | Ballybeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 4.542 | 5 | 0.154 | 1 | 0.154 | 3.45 | 3.45 | 1679970 | 7 | 486947.8261 | 2.0536 | 3.45 | 386.7942
15 | 15 | CL1-015 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.995 | 12 | 0.155 | 1 | 0.155 | 3.45 | 3.45 | 1492540 | 1 | 432620.2899 | 2.3115 | 3.45 | 486.9478
16 | 16 | CL1-016 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.179 | 12 | 0.101 | 1 | 0.101 | 3.45 | 3.45 | 1492540 | 1 | 432620.2899 | 2.3115 | 3.45 | 432.6203
17 | 17 | CL1-017 | DONEGAL | DONEGAL | SS-610 | Milford (North) 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.864 | 15 | 0.149 | 1 | 0.149 | 3.45 | 3.45 | 1650640 | 1 | 478446.3768 | 2.0901 | 3.45 | 432.6203
18 | 18 | CL1-018 | DONEGAL | DONEGAL | SS-117 | Crockahenny 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.217 | 3 | 0.259 | 1 | 0.259 | 3.45 | 3.45 | 558600 | 4 | 161913.0435 | 6.1762 | 3.45 | 478.4464
19 | 19 | CL1-019 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.887 | 8 | 0.337 | 1 | 0.337 | 3.45 | 3.45 | 909950 | 4 | 263753.6232 | 3.7914 | 3.45 | 161.913
20 | 20 | CL1-020 | DONEGAL | DONEGAL | SS-123 | Derrybeg 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.548 | 9 | 0.523 | 1 | 0.523 | 3.45 | 3.45 | 1334440 | 1 | 386794.2029 | 2.5854 | 3.45 | 263.7536
21 | 21 | CL1-021 | KERRY | KERRY | SS-636 | Garranebane 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 13.635 | 14 | 0.289 | 1 | 0.289 | 3.45 | 3.45 | 1597940 | 1 | 463171.0145 | 2.159 | 3.45 | 386.7942
22 | 22 | CL1-022 | WICKLOW | WICKLOW | SS-209 | Blessington 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.06 | 8 | 0.325 | 1 | 0.325 | 3.45 | 3.45 | 909950 | 4 | 263753.6232 | 3.7914 | 3.45 | 463.171
23 | 23 | CL1-023 | DONEGAL | DONEGAL | SS-117 | Crockahenny 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.876 | 5 | 0.614 | 1 | 0.4605 | 3.45 | 3.45 | 699140 | 4 | 202649.2754 | 4.9346 | 3.45 | 263.7536
24 | 24 | CL1-024 | DONEGAL | DONEGAL | SS-617 | Mulreavy 110kV Substation | EirGrid | 110000 | 33000 | 110000 | 12.664 | 13 | 0.209 | 1 | 0.209 | 3.45 | 3.45 | 2101570 | 7 | 609150.7246 | 1.6416 | 3.45 | 202.6493
25 | 25 | CL1-025 | CAVAN | CAVAN | SS-110 | Corraclassy 110kV Substation | EirGrid | 110000 |  |  | 10.905 | 11 | 0.786 | 1 | 0.5895 | 3.45 | 3.45 | 1996170 | 7 | 578600 | 1.7283 | 3.45 | 609.1507
26 | 26 | CL1-026 | LOUTH | LOUTH | SS-650 | Ballymascanlan 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.994 | 5 | 0.211 | 1 | 0.211 | 3.45 | 3.45 | 699140 | 4 | 202649.2754 | 4.9346 | 3.45 | 578.6
27 | 27 | CL1-027 | CORK | CORK | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 12.641 | 13 | 0.281 | 1 | 0.281 | 3.45 | 3.45 | 1545240 | 1 | 447895.6522 | 2.2327 | 3.45 | 202.6493
28 | 28 | CL1-028 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 12.848 | 13 | 0.134 | 1 | 0.134 | 3.45 | 3.45 | 1545240 | 1 | 447895.6522 | 2.2327 | 3.45 | 447.8957
29 | 29 | CL1-029 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 12.044 | 13 | 0.17 | 1 | 0.17 | 3.45 | 3.45 | 1545240 | 1 | 447895.6522 | 2.2327 | 3.45 | 447.8957
30 | 30 | CL1-030 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 13.637 | 14 | 0.496 | 1 | 0.496 | 3.45 | 3.45 | 1597940 | 1 | 463171.0145 | 2.159 | 3.45 | 447.8957
31 | 31 | CL1-031 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.786 | 13 | 0.351 | 1 | 0.351 | 3.45 | 3.45 | 1545240 | 1 | 447895.6522 | 2.2327 | 3.45 | 463.171
32 | 32 | CL1-032 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.48 | 15 | 0.438 | 1 | 0.438 | 3.45 | 3.45 | 1650640 | 1 | 478446.3768 | 2.0901 | 3.45 | 447.8957
33 | 33 | CL1-033 | KERRY | KERRY | SS-321 | Milltown 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.713 | 12 | 0.121 | 1 | 0.121 | 3.45 | 3.45 | 1492540 | 1 | 432620.2899 | 2.3115 | 3.45 | 478.4464
34 | 34 | CL1-034 | KERRY | KERRY | SS-387 | Coolcorcoran 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.301 | 12 | 0.237 | 1 | 0.237 | 3.45 | 3.45 | 1492540 | 1 | 432620.2899 | 2.3115 | 3.45 | 432.6203
35 | 35 | CL1-035 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.65 | 16 | 0.262 | 1 | 0.262 | 3.45 | 3.45 | 1703340 | 1 | 493721.7391 | 2.0254 | 3.45 | 432.6203
36 | 36 | CL1-036 | KERRY | KERRY | SS-636 | Garranebane 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.091 | 5 | 0.567 | 1 | 0.567 | 3.45 | 3.45 | 699140 | 4 | 202649.2754 | 4.9346 | 3.45 | 493.7217
37 | 37 | CL1-037 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.79 | 3 | 0.399 | 1 | 0.399 | 3.45 | 3.45 | 558600 | 4 | 161913.0435 | 6.1762 | 3.45 | 202.6493
38 | 38 | CL1-038 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 14.268 | 15 | 0.109 | 1 | 0.109 | 3.45 | 3.45 | 1650640 | 1 | 478446.3768 | 2.0901 | 3.45 | 161.913
39 | 39 | CL1-039 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 9.745 | 10 | 0.123 | 1 | 0.123 | 3.45 | 3.45 | 1387140 | 1 | 402069.5652 | 2.4871 | 3.45 | 478.4464
40 | 40 | CL1-040 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 9.612 | 10 | 0.099 | 1 | 0.099 | 3.45 | 3.45 | 1387140 | 1 | 402069.5652 | 2.4871 | 3.45 | 402.0696
41 | 41 | CL1-041 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 15.118 | 16 | 0.109 | 1 | 0.109 | 3.45 | 3.45 | 1703340 | 1 | 493721.7391 | 2.0254 | 3.45 | 402.0696
42 | 42 | CL1-042 | CORK | CORK | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 1.996 | 2 | 0.14 | 1 | 0.14 | 3.45 | 3.45 | 488330 | 4 | 141544.9275 | 7.0649 | 3.45 | 493.7217
43 | 43 | CL1-043 | CORK | CORK | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 2.393 | 3 | 0.093 | 1 | 0.093 | 3.45 | 3.45 | 558600 | 4 | 161913.0435 | 6.1762 | 3.45 | 141.5449
44 | 44 | CL1-044 | CORK | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.316 | 5 | 0.219 | 1 | 0.219 | 3.45 | 3.45 | 699140 | 4 | 202649.2754 | 4.9346 | 3.45 | 161.913
45 | 45 | CL1-045 | KERRY | KERRY | SS-637 | Kilgarvan 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.375 | 5 | 0.163 | 1 | 0.163 | 3.45 | 3.45 | 699140 | 4 | 202649.2754 | 4.9346 | 3.45 | 202.6493
46 | 46 | CL1-046 | KERRY | KERRY | SS-637 | Kilgarvan 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.589 | 6 | 0.256 | 1 | 0.256 | 3.45 | 3.45 | 769410 | 4 | 223017.3913 | 4.484 | 3.45 | 202.6493
47 | 47 | CL1-047 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.077 | 11 | 0.349 | 1 | 0.349 | 3.45 | 3.45 | 1439840 | 1 | 417344.9275 | 2.3961 | 3.45 | 223.0174
48 | 48 | CL1-048 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.851 | 8 | 0.591 | 1 | 0.591 | 3.45 | 3.45 | 909950 | 4 | 263753.6232 | 3.7914 | 3.45 | 417.3449
49 | 49 | CL1-049 | KERRY | KERRY | SS-140 | Ballyard 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 4.771 | 5 | 0.381 | 1 | 0.381 | 3.45 | 3.45 | 699140 | 4 | 202649.2754 | 4.9346 | 3.45 | 263.7536
50 | 50 | CL1-050 | CLARE | CLARE | SS-595 | Kilkee 38kV Substation | ESB Networks | 38000 | 38000 | low | 23.476 | 24 | 0.195 | 1 | 0.195 | 3.45 | 3.45 | 2124940 | 1 | 615924.6377 | 1.6236 | 3.45 | 202.6493
51 | 51 | CL1-051 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.891 | 16 | 0.111 | 1 | 0.111 | 3.45 | 3.45 | 1703340 | 1 | 493721.7391 | 2.0254 | 3.45 | 615.9246
52 | 52 | CL1-052 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.806 | 16 | 0.437 | 1 | 0.437 | 3.45 | 3.45 | 1703340 | 1 | 493721.7391 | 2.0254 | 3.45 | 493.7217
53 | 53 | CL1-053 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.451 | 12 | 0.189 | 1 | 0.189 | 3.45 | 3.45 | 1492540 | 1 | 432620.2899 | 2.3115 | 3.45 | 493.7217
54 | 54 | CL1-054 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.715 | 6 | 0.331 | 1 | 0.331 | 3.45 | 3.45 | 769410 | 4 | 223017.3913 | 4.484 | 3.45 | 432.6203
55 | 55 | CL1-055 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.746 | 5 | 0.316 | 1 | 0.316 | 3.45 | 3.45 | 699140 | 4 | 202649.2754 | 4.9346 | 3.45 | 223.0174
56 | 56 | CL1-056 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.998 | 15 | 0.394 | 1 | 0.394 | 3.45 | 3.45 | 1650640 | 1 | 478446.3768 | 2.0901 | 3.45 | 202.6493
57 | 57 | CL1-057 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 15.493 | 16 | 0.104 | 1 | 0.104 | 3.45 | 3.45 | 1703340 | 1 | 493721.7391 | 2.0254 | 3.45 | 478.4464
58 | 58 | CL1-058 | GALWAY | GALWAY | SS-638 | Oughterard 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 12.648 | 13 | 0.377 | 1 | 0.377 | 3.45 | 3.45 | 1545240 | 1 | 447895.6522 | 2.2327 | 3.45 | 493.7217
59 | 59 | CL1-059 | GALWAY | GALWAY | SS-638 | Oughterard 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.696 | 9 | 0.246 | 1 | 0.246 | 3.45 | 3.45 | 1334440 | 1 | 386794.2029 | 2.5854 | 3.45 | 447.8957
60 | 60 | CL1-060 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 23.516 | 24 | 0.218 | 1 | 0.218 | 3.45 | 3.45 | 2681270 | 7 | 777179.7101 | 1.2867 | 3.45 | 386.7942
61 | 61 | CL1-061 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 23.133 | 24 | 0.191 | 1 | 0.191 | 3.45 | 3.45 | 2681270 | 7 | 777179.7101 | 1.2867 | 3.45 | 777.1797
62 | 62 | CL1-062 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 20.874 | 21 | 0.106 | 1 | 0.106 | 3.45 | 3.45 | 2523170 | 7 | 731353.6232 | 1.3673 | 3.45 | 777.1797
63 | 63 | CL1-063 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.98 | 4 | 0.279 | 1 | 0.279 | 3.45 | 3.45 | 628870 | 4 | 182281.1594 | 5.486 | 3.45 | 731.3536
64 | 64 | CL1-064 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.894 | 12 | 0.276 | 1 | 0.276 | 3.45 | 3.45 | 1492540 | 1 | 432620.2899 | 2.3115 | 3.45 | 182.2812
65 | 65 | CL1-065 | MAYO | MAYO | SS-317 | Newport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.804 | 12 | 0.167 | 1 | 0.167 | 3.45 | 3.45 | 1492540 | 1 | 432620.2899 | 2.3115 | 3.45 | 432.6203
66 | 66 | CL1-066 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 10.284 | 11 | 0.094 | 1 | 0.094 | 3.45 | 3.45 | 1996170 | 7 | 578600 | 1.7283 | 3.45 | 432.6203
67 | 67 | CL1-067 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.543 | 6 | 0.698 | 1 | 0.5235 | 3.45 | 3.45 | 769410 | 4 | 223017.3913 | 4.484 | 3.45 | 578.6
68 | 68 | CL1-068 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.459 | 15 | 0.288 | 1 | 0.288 | 3.45 | 3.45 | 1650640 | 1 | 478446.3768 | 2.0901 | 3.45 | 223.0174
69 | 69 | CL1-069 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.611 | 16 | 0.148 | 1 | 0.148 | 3.45 | 3.45 | 1703340 | 1 | 493721.7391 | 2.0254 | 3.45 | 478.4464
70 | 70 | CL1-070 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.467 | 16 | 0.187 | 1 | 0.187 | 3.45 | 3.45 | 1703340 | 1 | 493721.7391 | 2.0254 | 3.45 | 493.7217
71 | 71 | CL1-071 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 16.38 | 17 | 0.131 | 1 | 0.131 | 3.45 | 3.45 | 1756040 | 1 | 508997.1014 | 1.9646 | 3.45 | 493.7217
72 | 72 | CL1-072 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 1.724 | 2 | 0.688 | 1 | 0.516 | 3.45 | 3.45 | 488330 | 4 | 141544.9275 | 7.0649 | 3.45 | 508.9971
73 | 73 | CL1-073 | MAYO | MAYO | SS-234 | Crossmolina 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.238 | 14 | 0.596 | 1 | 0.447 | 3.45 | 3.45 | 1597940 | 1 | 463171.0145 | 2.159 | 3.45 | 141.5449
74 | 74 | CL1-074 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 13.919 | 14 | 0.619 | 1 | 0.46425 | 3.45 | 3.45 | 2154270 | 7 | 624426.087 | 1.6015 | 3.45 | 463.171
75 | 75 | CL1-075 | MAYO | MAYO | SS-710 | Tawnaghmore 110kV Substation | EirGrid | 110000 | low | 110000 | 14.333 | 15 | 0.103 | 1 | 0.103 | 3.45 | 3.45 | 2206970 | 7 | 639701.4493 | 1.5632 | 3.45 | 624.4261
76 | 76 | CL1-076 | MAYO | MAYO | SS-710 | Tawnaghmore 110kV Substation | EirGrid | 110000 | low | 110000 | 16.962 | 17 | 0.325 | 1 | 0.325 | 3.45 | 3.45 | 2312370 | 7 | 670252.1739 | 1.492 | 3.45 | 639.7014
77 | 77 | CL1-077 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.99 | 8 | 0.129 | 1 | 0.129 | 3.45 | 3.45 | 909950 | 4 | 263753.6232 | 3.7914 | 3.45 | 670.2522
78 | 78 | CL1-078 | SLIGO | SLIGO | SS-075 | Cunghill 110kV Substation | EirGrid | 110000 | 110000 | medium | 11.375 | 12 | 0.246 | 1 | 0.246 | 3.45 | 3.45 | 2048870 | 7 | 593875.3623 | 1.6839 | 3.45 | 263.7536
79 | 79 | CL1-079 | SLIGO | SLIGO | SS-075 | Cunghill 110kV Substation | EirGrid | 110000 | 110000 | medium | 11.206 | 12 | 0.242 | 1 | 0.242 | 3.45 | 3.45 | 2048870 | 7 | 593875.3623 | 1.6839 | 3.45 | 593.8754
80 | 80 | CL1-080 | SLIGO | LEITRIM | SS-042 | Ballytivnan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 10.22 | 11 | 0.206 | 1 | 0.206 | 3.45 | 3.45 | 1439840 | 1 | 417344.9275 | 2.3961 | 3.45 | 593.8754
81 | 81 | CL1-081 | SLIGO | SLIGO | SS-042 | Ballytivnan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.688 | 9 | 0.249 | 1 | 0.249 | 3.45 | 3.45 | 1334440 | 1 | 386794.2029 | 2.5854 | 3.45 | 417.3449
82 | 82 | CL1-082 | SLIGO | SLIGO | SS-042 | Ballytivnan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.236 | 9 | 0.132 | 1 | 0.132 | 3.45 | 3.45 | 1334440 | 1 | 386794.2029 | 2.5854 | 3.45 | 386.7942
83 | 83 | CL1-083 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 4.929 | 5 | 0.527 | 1 | 0.527 | 3.45 | 3.45 | 699140 | 4 | 202649.2754 | 4.9346 | 3.45 | 386.7942
84 | 84 | CL1-084 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 13.065 | 14 | 0.101 | 1 | 0.101 | 3.45 | 3.45 | 1597940 | 1 | 463171.0145 | 2.159 | 3.45 | 202.6493
85 | 85 | CL1-085 | DONEGAL | DONEGAL | SS-090 | Corkermore 38kV Substation | ESB Networks | 38000 | low | 38000 | 9.143 | 10 | 0.599 | 1 | 0.44925 | 3.45 | 3.45 | 1387140 | 1 | 402069.5652 | 2.4871 | 3.45 | 463.171
86 | 86 | CL1-086 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 11.022 | 12 | 0.205 | 1 | 0.205 | 3.45 | 3.45 | 1492540 | 1 | 432620.2899 | 2.3115 | 3.45 | 402.0696
87 | 87 | CL1-087 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 3.316 | 4 | 0.442 | 1 | 0.442 | 3.45 | 3.45 | 628870 | 4 | 182281.1594 | 5.486 | 3.45 | 432.6203
88 | 88 | CL1-088 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 2.243 | 3 | 0.097 | 1 | 0.097 | 3.45 | 3.45 | 558600 | 4 | 161913.0435 | 6.1762 | 3.45 | 182.2812
89 | 89 | CL1-089 | DONEGAL | DONEGAL | SS-252 | Killybegs 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 4.306 | 5 | 0.197 | 1 | 0.197 | 3.45 | 3.45 | 699140 | 4 | 202649.2754 | 4.9346 | 3.45 | 161.913
90 | 90 | CL1-090 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 3.787 | 4 | 0.318 | 1 | 0.318 | 3.45 | 3.45 | 1627270 | 7 | 471672.4638 | 2.1201 | 3.45 | 202.6493
91 | 91 | CL1-091 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 3.504 | 4 | 0.395 | 1 | 0.395 | 3.45 | 3.45 | 1627270 | 7 | 471672.4638 | 2.1201 | 3.45 | 471.6725
92 | 92 | CL1-092 | DONEGAL | DONEGAL | SS-123 | Derrybeg 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 10.189 | 11 | 0.286 | 1 | 0.286 | 3.45 | 3.45 | 1439840 | 1 | 417344.9275 | 2.3961 | 3.45 | 471.6725
93 | 93 | CL1-093 | DONEGAL | DONEGAL | SS-119 | Drumlough Hill (1) 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.583 | 2 | 0.166 | 1 | 0.166 | 3.45 | 3.45 | 488330 | 4 | 141544.9275 | 7.0649 | 3.45 | 417.3449
94 | 94 | CL1-094 | DONEGAL | DONEGAL | SS-239 | Moville 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 3.296 | 4 | 0.115 | 1 | 0.115 | 3.45 | 3.45 | 628870 | 4 | 182281.1594 | 5.486 | 3.45 | 141.5449
95 | 95 | CL1-095 | DONEGAL | DONEGAL | SS-689 |  | ESB Networks | 38000 |  |  | 5.174 | 6 | 0.108 | 1 | 0.108 | 3.45 | 3.45 | 769410 | 4 | 223017.3913 | 4.484 | 3.45 | 182.2812
96 | 96 | CL1-096 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.713 | 11 | 0.108 | 1 | 0.108 | 3.45 | 3.45 | 1439840 | 1 | 417344.9275 | 2.3961 | 3.45 | 223.0174
97 | 97 | CL1-097 | CARLOW | CARLOW | SS-481 | Castledockrell 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 10.637 | 11 | 0.364 | 1 | 0.364 | 3.45 | 3.45 | 1996170 | 7 | 578600 | 1.7283 | 3.45 | 417.3449
98 | 98 | CL1-098 | CARLOW | WEXFORD | SS-481 | Castledockrell 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 9.874 | 10 | 0.328 | 1 | 0.328 | 3.45 | 3.45 | 1943470 | 7 | 563324.6377 | 1.7752 | 3.45 | 578.6
99 | 99 | CL1-099 | CARLOW | CARLOW | SS-494 | Bunclody 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.975 | 10 | 0.438 | 1 | 0.438 | 3.45 | 3.45 | 1387140 | 1 | 402069.5652 | 2.4871 | 3.45 | 563.3246
100 | 100 | CL1-100 | WICKLOW | WICKLOW | SS-062 | Stratford 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.266 | 9 | 1.033 | 1 | 0.77475 | 6.9 | 6.9 | 1890770 | 7 | 274024.6377 | 3.6493 | 3.45 | 402.0696
101 | 101 | CL1-101 | WICKLOW | WICKLOW | SS-062 | Stratford 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 10.241 | 11 | 0.101 | 1 | 0.101 | 3.45 | 3.45 | 1996170 | 7 | 578600 | 1.7283 | 6.9 | 274.0246
102 | 102 | CL1-102 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.313 | 10 | 0.157 | 1 | 0.157 | 3.45 | 3.45 | 1387140 | 1 | 402069.5652 | 2.4871 | 3.45 | 578.6
103 | 103 | CL1-103 | WICKLOW | WICKLOW | SS-209 | Blessington 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.176 | 7 | 0.405 | 1 | 0.405 | 3.45 | 3.45 | 839680 | 4 | 243385.5072 | 4.1087 | 3.45 | 402.0696
104 | 104 | CL1-104 | WICKLOW | WICKLOW | SS-209 | Blessington 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.937 | 11 | 0.309 | 1 | 0.309 | 3.45 | 3.45 | 1439840 | 1 | 417344.9275 | 2.3961 | 3.45 | 243.3855
105 | 105 | CL1-105 | DUBLIN | DUBLIN | SS-018 | Old Bawn 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 10.006 | 11 | 0.442 | 1 | 0.442 | 3.45 | 3.45 | 1439840 | 1 | 417344.9275 | 2.3961 | 3.45 | 417.3449
106 | 106 | CL1-106 | DUBLIN | DUBLIN | SS-017 | Sandyford 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.975 | 4 | 0.279 | 1 | 0.279 | 3.45 | 3.45 | 628870 | 4 | 182281.1594 | 5.486 | 3.45 | 417.3449
107 | 107 | CL1-107 | DUBLIN | DUBLIN | SS-018 | Old Bawn 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 5.83 | 6 | 0.405 | 1 | 0.405 | 3.45 | 3.45 | 769410 | 4 | 223017.3913 | 4.484 | 3.45 | 182.2812
108 | 108 | CL1-108 | KERRY | KERRY | SS-637 | Kilgarvan 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.286 | 5 | 0.503 | 1 | 0.503 | 3.45 | 3.45 | 699140 | 4 | 202649.2754 | 4.9346 | 3.45 | 223.0174
109 | 109 | CL1-109 | CORK | CORK | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.288 | 4 | 0.491 | 1 | 0.491 | 3.45 | 3.45 | 628870 | 4 | 182281.1594 | 5.486 | 3.45 | 202.6493
110 | 110 | CL1-110 | CORK | CORK | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.534 | 3 | 0.277 | 1 | 0.277 | 3.45 | 3.45 | 558600 | 4 | 161913.0435 | 6.1762 | 3.45 | 182.2812
111 | 111 | CL1-111 | TIPPERARY | TIPPERARY | SS-645 | Toomevara 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.354 | 8 | 0.314 | 1 | 0.314 | 3.45 | 3.45 | 909950 | 4 | 263753.6232 | 3.7914 | 3.45 | 161.913
112 | 112 | CL1-112 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 4.496 | 5 | 0.154 | 1 | 0.154 | 3.45 | 3.45 | 1679970 | 7 | 486947.8261 | 2.0536 | 3.45 | 263.7536
113 | 113 | CL1-113 | DONEGAL | DONEGAL | SS-686 | Dungloe 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.425 | 9 | 0.894 | 1 | 0.6705 | 6.9 | 6.9 | 1379800 | 2 | 199971.0145 | 5.0007 | 3.45 | 486.9478
114 | 114 | CL1-114 | DONEGAL | DONEGAL | SS-195 | Cark 110kV Substation | EirGrid | 110000 | low | 110000 | 3.157 | 4 | 0.159 | 1 | 0.159 | 3.45 | 3.45 | 1627270 | 7 | 471672.4638 | 2.1201 | 6.9 | 199.971
115 | 115 | CL1-115 | CAVAN | LEITRIM | SS-110 | Corraclassy 110kV Substation | EirGrid | 110000 |  |  | 10.141 | 11 | 0.273 | 1 | 0.273 | 3.45 | 3.45 | 1996170 | 7 | 578600 | 1.7283 | 3.45 | 471.6725
116 | 116 | CL1-116 | LEITRIM | LEITRIM | SS-304 | Arigna 110kV Substation | EirGrid | 110000 | 110000 | 20000 | 9.782 | 10 | 0.13 | 1 | 0.13 | 3.45 | 3.45 | 1943470 | 7 | 563324.6377 | 1.7752 | 3.45 | 578.6
117 | 117 | CL1-117 | SLIGO | SLIGO | SS-078 | Glenree 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 4.591 | 5 | 0.175 | 1 | 0.175 | 3.45 | 3.45 | 1679970 | 7 | 486947.8261 | 2.0536 | 3.45 | 563.3246
118 | 118 | CL1-118 | DONEGAL | DONEGAL | SS-195 | Cark 110kV Substation | EirGrid | 110000 | low | 110000 | 3.643 | 4 | 0.246 | 1 | 0.246 | 3.45 | 3.45 | 1627270 | 7 | 471672.4638 | 2.1201 | 3.45 | 486.9478
119 | 119 | CL1-119 | DONEGAL | DONEGAL | SS-643 | Donegal 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.667 | 7 | 0.213 | 1 | 0.213 | 3.45 | 3.45 | 839680 | 4 | 243385.5072 | 4.1087 | 3.45 | 471.6725
120 | 120 | CL1-120 | DONEGAL | DONEGAL | SS-688 | Clogher 110kV Substation | EirGrid | 110000 |  |  | 4.568 | 5 | 1.008 | 1 | 0.756 | 6.9 | 6.9 | 1679970 | 7 | 243473.913 | 4.1072 | 3.45 | 243.3855
121 | 121 | CL1-121 | DONEGAL | DONEGAL | SS-083 | Golagh 110kV Substation | EirGrid | 110000 | 38000 | 110000 | 8.397 | 9 | 0.146 | 1 | 0.146 | 3.45 | 3.45 | 1890770 | 7 | 548049.2754 | 1.8247 | 6.9 | 243.4739
122 | 122 | CL1-122 | DONEGAL | DONEGAL | SS-688 | Clogher 110kV Substation | EirGrid | 110000 |  |  | 9.522 | 10 | 0.479 | 1 | 0.479 | 3.45 | 3.45 | 1943470 | 7 | 563324.6377 | 1.7752 | 3.45 | 548.0493
123 | 123 | CL1-123 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 7.106 | 8 | 0.523 | 1 | 0.523 | 3.45 | 3.45 | 1838070 | 7 | 532773.913 | 1.877 | 3.45 | 563.3246
124 | 124 | CL1-124 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 9.667 | 10 | 0.187 | 1 | 0.187 | 3.45 | 3.45 | 1943470 | 7 | 563324.6377 | 1.7752 | 3.45 | 532.7739
125 | 125 | CL1-125 | GALWAY | GALWAY | SS-662 | Cloosh 110kV Substation | EirGrid | 110000 | low | 110000 | 6.474 | 7 | 0.621 | 1 | 0.46575 | 3.45 | 3.45 | 1785370 | 7 | 517498.5507 | 1.9324 | 3.45 | 563.3246
126 | 126 | CL1-126 | GALWAY | GALWAY | SS-623 | Uggool 110kV Substation | EirGrid | 110000 | 33000 | 110000 | 6.479 | 7 | 0.665 | 1 | 0.49875 | 3.45 | 3.45 | 1785370 | 7 | 517498.5507 | 1.9324 | 3.45 | 517.4986
127 | 127 | CL1-127 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 6.76 | 7 | 0.109 | 1 | 0.109 | 3.45 | 3.45 | 1785370 | 7 | 517498.5507 | 1.9324 | 3.45 | 517.4986
128 | 128 | CL1-128 | WATERFORD | TIPPERARY | SS-455 | Ardfinnan 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.754 | 8 | 0.315 | 1 | 0.315 | 3.45 | 3.45 | 909950 | 4 | 263753.6232 | 3.7914 | 3.45 | 517.4986
129 | 129 | CL1-129 | WATERFORD | WATERFORD | SS-659 | Spa Road 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 4.24 | 5 | 0.563 | 1 | 0.563 | 3.45 | 3.45 | 699140 | 4 | 202649.2754 | 4.9346 | 3.45 | 263.7536
130 | 130 | CL1-130 | WATERFORD | WATERFORD | SS-205 | Dungarvan 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 9.346 | 10 | 0.182 | 1 | 0.182 | 3.45 | 3.45 | 1943470 | 7 | 563324.6377 | 1.7752 | 3.45 | 202.6493
131 | 131 | CL1-131 | TIPPERARY | TIPPERARY | SS-257 | Kilshanny 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.74 | 11 | 0.164 | 1 | 0.164 | 3.45 | 3.45 | 1439840 | 1 | 417344.9275 | 2.3961 | 3.45 | 563.3246
132 | 132 | CL1-132 | TIPPERARY | TIPPERARY | SS-315 | Cahir 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 9.181 | 10 | 0.101 | 1 | 0.101 | 3.45 | 3.45 | 1387140 | 1 | 402069.5652 | 2.4871 | 3.45 | 417.3449
133 | 133 | CL1-133 | TIPPERARY | TIPPERARY | SS-585 | Kilross Road 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.796 | 9 | 0.223 | 1 | 0.223 | 3.45 | 3.45 | 1334440 | 1 | 386794.2029 | 2.5854 | 3.45 | 402.0696
134 | 134 | CL1-134 | CARLOW | WEXFORD | SS-492 | Graigue 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.378 | 10 | 0.537 | 1 | 0.537 | 3.45 | 3.45 | 1387140 | 1 | 402069.5652 | 2.4871 | 3.45 | 386.7942
135 | 135 | CL1-135 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.92 | 16 | 0.552 | 1 | 0.552 | 3.45 | 3.45 | 1703340 | 1 | 493721.7391 | 2.0254 | 3.45 | 402.0696
136 | 136 | CL1-136 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.727 | 8 | 0.298 | 1 | 0.298 | 3.45 | 3.45 | 909950 | 4 | 263753.6232 | 3.7914 | 3.45 | 493.7217
137 | 137 | CL1-137 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.653 | 5 | 0.518 | 1 | 0.518 | 3.45 | 3.45 | 699140 | 4 | 202649.2754 | 4.9346 | 3.45 | 263.7536
138 | 138 | CL1-138 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.195 | 11 | 0.188 | 1 | 0.188 | 3.45 | 3.45 | 1439840 | 1 | 417344.9275 | 2.3961 | 3.45 | 202.6493
139 | 139 | CL1-139 | WEXFORD | WEXFORD | SS-616 | Ballinvally 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 6.932 | 7 | 0.165 | 1 | 0.165 | 3.45 | 3.45 | 839680 | 4 | 243385.5072 | 4.1087 | 3.45 | 417.3449
140 | 140 | CL1-140 | CORK | CORK | SS-562 | Bantry 38kV Substation | ESB Networks | 38000 | 38000 | low | 19.408 | 20 | 0.436 | 1 | 0.436 | 3.45 | 3.45 | 1914140 | 1 | 554823.1884 | 1.8024 | 3.45 | 243.3855
141 | 141 | CL1-141 | CORK | CORK | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 7.195 | 8 | 0.559 | 1 | 0.559 | 3.45 | 3.45 | 909950 | 4 | 263753.6232 | 3.7914 | 3.45 | 554.8232
142 | 142 | CL1-142 | CORK | CORK | SS-261 | Milane Hill 38kV Station | ESB Networks | 38000 |  |  | 4.465 | 5 | 0.223 | 1 | 0.223 | 3.45 | 3.45 | 699140 | 4 | 202649.2754 | 4.9346 | 3.45 | 263.7536
143 | 143 | CL1-143 | CLARE | CLARE | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.07 | 16 | 0.367 | 1 | 0.367 | 3.45 | 3.45 | 1703340 | 1 | 493721.7391 | 2.0254 | 3.45 | 202.6493
144 | 144 | CL1-144 | KILKENNY | KILKENNY | SS-492 | Graigue 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.279 | 4 | 0.606 | 1 | 0.4545 | 3.45 | 3.45 | 628870 | 4 | 182281.1594 | 5.486 | 3.45 | 493.7217
145 | 145 | CL1-145 | WICKLOW | WICKLOW | SS-591 | Shillelagh 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.399 | 5 | 0.227 | 1 | 0.227 | 3.45 | 3.45 | 699140 | 4 | 202649.2754 | 4.9346 | 3.45 | 182.2812
146 | 146 | CL1-146 | CLARE | CLARE | SS-503 | Scariff 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 9.263 | 10 | 0.449 | 1 | 0.449 | 3.45 | 3.45 | 1387140 | 1 | 402069.5652 | 2.4871 | 3.45 | 202.6493
147 | 147 | CL1-147 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.032 | 6 | 0.247 | 1 | 0.247 | 3.45 | 3.45 | 769410 | 4 | 223017.3913 | 4.484 | 3.45 | 402.0696
148 | 148 | CL1-148 | CORK | CORK | SS-355 | Carrigcannon 38kV Substation | ESB Networks | 38000 | low | 38000 | 6.544 | 7 | 0.653 | 1 | 0.48975 | 3.45 | 3.45 | 839680 | 4 | 243385.5072 | 4.1087 | 3.45 | 223.0174
149 | 149 | CL1-149 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 13.503 | 14 | 0.366 | 1 | 0.366 | 3.45 | 3.45 | 1597940 | 1 | 463171.0145 | 2.159 | 3.45 | 243.3855
150 | 150 | CL1-150 | WICKLOW | WICKLOW | SS-570 | Kilcoole 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.276 | 6 | 0.343 | 1 | 0.343 | 3.45 | 3.45 | 769410 | 4 | 223017.3913 | 4.484 | 3.45 | 463.171
151 | 151 | CL1-151 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.562 | 8 | 0.278 | 1 | 0.278 | 3.45 | 3.45 | 909950 | 4 | 263753.6232 | 3.7914 | 3.45 | 223.0174
152 | 152 | CL1-152 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.932 | 8 | 0.197 | 1 | 0.197 | 3.45 | 3.45 | 909950 | 4 | 263753.6232 | 3.7914 | 3.45 | 263.7536
153 | 153 | CL1-153 | CLARE | CLARE | SS-708 |  | EirGrid | 110000 | medium | 110000 | 4.096 | 5 | 0.188 | 1 | 0.188 | 3.45 | 3.45 | 1679970 | 7 | 486947.8261 | 2.0536 | 3.45 | 263.7536
154 | 154 | CL1-154 | DONEGAL | DONEGAL | SS-138 | Creeslough 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.186 | 9 | 0.287 | 1 | 0.287 | 3.45 | 3.45 | 1334440 | 1 | 386794.2029 | 2.5854 | 3.45 | 486.9478
155 | 155 | CL1-155 | DONEGAL | DONEGAL | SS-138 | Creeslough 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.543 | 7 | 0.85 | 1 | 0.6375 | 6.9 | 6.9 | 839680 | 4 | 121692.7536 | 8.2174 | 3.45 | 386.7942
156 | 156 | CL1-156 | DONEGAL | DONEGAL | SS-610 | Milford (North) 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.01 | 9 | 0.424 | 1 | 0.424 | 3.45 | 3.45 | 1334440 | 1 | 386794.2029 | 2.5854 | 6.9 | 121.6928
157 | 157 | CL1-157 | DONEGAL | DONEGAL | SS-610 | Milford (North) 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.213 | 8 | 0.457 | 1 | 0.457 | 3.45 | 3.45 | 909950 | 4 | 263753.6232 | 3.7914 | 3.45 | 386.7942
158 | 158 | CL1-158 | MAYO | MAYO | SS-234 | Crossmolina 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.817 | 11 | 0.405 | 1 | 0.405 | 3.45 | 3.45 | 1439840 | 1 | 417344.9275 | 2.3961 | 3.45 | 263.7536
159 | 159 | CL1-159 | MAYO | MAYO | SS-710 | Tawnaghmore 110kV Substation | EirGrid | 110000 | low | 110000 | 12.265 | 13 | 0.562 | 1 | 0.562 | 3.45 | 3.45 | 2101570 | 7 | 609150.7246 | 1.6416 | 3.45 | 417.3449
160 | 160 | CL1-160 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.322 | 10 | 0.224 | 1 | 0.224 | 3.45 | 3.45 | 1387140 | 1 | 402069.5652 | 2.4871 | 3.45 | 609.1507
161 | 161 | CL1-161 | SLIGO | SLIGO | SS-206 | Boyle 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 10.985 | 11 | 0.211 | 1 | 0.211 | 3.45 | 3.45 | 1439840 | 1 | 417344.9275 | 2.3961 | 3.45 | 402.0696
162 | 162 | CL1-162 | SLIGO | SLIGO | SS-068 | Ballymote 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.173 | 8 | 0.152 | 1 | 0.152 | 3.45 | 3.45 | 909950 | 4 | 263753.6232 | 3.7914 | 3.45 | 417.3449
163 | 163 | CL1-163 | MAYO | MAYO | SS-078 | Glenree 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 7.654 | 8 | 0.25 | 1 | 0.25 | 3.45 | 3.45 | 1838070 | 7 | 532773.913 | 1.877 | 3.45 | 263.7536
164 | 164 | CL1-164 | MAYO | MAYO | SS-203 | Foxford 38kV Substation | ESB Networks | 38000 |  |  | 4.082 | 5 | 0.202 | 1 | 0.202 | 3.45 | 3.45 | 699140 | 4 | 202649.2754 | 4.9346 | 3.45 | 532.7739
165 | 165 | CL1-165 | SLIGO | LEITRIM | SS-042 | Ballytivnan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.739 | 8 | 0.379 | 1 | 0.379 | 3.45 | 3.45 | 909950 | 4 | 263753.6232 | 3.7914 | 3.45 | 202.6493
166 | 166 | CL1-166 | SLIGO | LEITRIM | SS-042 | Ballytivnan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.068 | 8 | 0.265 | 1 | 0.265 | 3.45 | 3.45 | 909950 | 4 | 263753.6232 | 3.7914 | 3.45 | 263.7536
167 | 167 | CL1-167 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 3.702 | 4 | 0.159 | 1 | 0.159 | 3.45 | 3.45 | 628870 | 4 | 182281.1594 | 5.486 | 3.45 | 263.7536
168 | 168 | CL1-168 | DONEGAL | DONEGAL | SS-239 | Moville 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.191 | 5 | 0.178 | 1 | 0.178 | 3.45 | 3.45 | 699140 | 4 | 202649.2754 | 4.9346 | 3.45 | 182.2812
169 | 169 | CL1-169 | DONEGAL | DONEGAL | SS-272 | Carndonagh 38kV | ESB Networks | 38000 | 38000 | low | 5.402 | 6 | 0.25 | 1 | 0.25 | 3.45 | 3.45 | 769410 | 4 | 223017.3913 | 4.484 | 3.45 | 202.6493
170 | 170 | CL1-170 | DONEGAL | DONEGAL | SS-117 | Crockahenny 38kV Substation | ESB Networks | 38000 | low | 38000 | 6.305 | 7 | 0.442 | 1 | 0.442 | 3.45 | 3.45 | 839680 | 4 | 243385.5072 | 4.1087 | 3.45 | 223.0174
171 | 171 | CL1-171 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.1 | 14 | 0.44 | 1 | 0.44 | 3.45 | 3.45 | 1597940 | 1 | 463171.0145 | 2.159 | 3.45 | 243.3855
172 | 172 | CL1-172 | CAVAN | MEATH | SS-110 | Corraclassy 110kV Substation | EirGrid | 110000 |  |  | 6.682 | 7 | 2.542 | 1 | 1.9065 | 20.7 | 20.7 | 2086600 | 8 | 100801.9324 | 9.9204 | 3.45 | 463.171
173 | 173 | CL1-173 | LOUTH | LOUTH | SS-651 | Grange 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.29 | 6 | 2.45 | 1 | 1.8375 | 17.25 | 17.25 | 769410 | 4 | 44603.4783 | 22.4198 | 20.7 | 100.8019
174 | 174 | CL1-174 | CORK | CORK | SS-562 | Bantry 38kV Substation | ESB Networks | 38000 | 38000 | low | 24.774 | 25 | 1.095 | 1 | 0.82125 | 6.9 | 6.9 | 2223000 | 2 | 322173.913 | 3.1039 | 17.25 | 44.6035
175 | 175 | CL1-175 | CORK | CORK | SS-562 | Bantry 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.734 | 16 | 0.571 | 1 | 0.571 | 3.45 | 3.45 | 1703340 | 1 | 493721.7391 | 2.0254 | 6.9 | 322.1739
176 | 176 | CL1-176 | CORK | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 13.7 | 14 | 4.122 | 1 | 3.0915 | 31.05 | 31.05 | 1905430 | 6 | 61366.5056 | 16.2955 | 3.45 | 493.7217
177 | 177 | CL1-177 | CORK | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.203 | 11 | 13.51 | 1 | 10.1325 | 110.4 | 110.4 | 3237370 | 11 | 29324.0036 | 34.1018 | 31.05 | 61.3665
178 | 178 | CL1-178 | CORK | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.849 | 8 | 0.465 | 1 | 0.465 | 3.45 | 3.45 | 909950 | 4 | 263753.6232 | 3.7914 | 110.4 | 29.324
179 | 179 | CL1-179 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.332 | 10 | 1.394 | 1 | 1.0455 | 10.35 | 10.35 | 1469550 | 3 | 141985.5072 | 7.043 | 3.45 | 263.7536
180 | 180 | CL1-180 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.323 | 12 | 1.358 | 1 | 1.0185 | 10.35 | 10.35 | 1574950 | 3 | 152169.0821 | 6.5716 | 10.35 | 141.9855
181 | 181 | CL1-181 | CORK | KERRY | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.874 | 9 | 4.963 | 1 | 3.7222 | 37.95 | 37.95 | 1349130 | 6 | 35550.1976 | 28.1292 | 10.35 | 152.1691
182 | 182 | CL1-182 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.859 | 5 | 6.039 | 1 | 4.5292 | 48.3 | 48.3 | 1972510 | 11 | 40838.7164 | 24.4866 | 37.95 | 35.5502
183 | 183 | CL1-183 | CORK | KERRY | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.054 | 10 | 5.872 | 1 | 4.404 | 48.3 | 48.3 | 3026560 | 11 | 62661.6977 | 15.9587 | 48.3 | 40.8387
184 | 184 | CL1-184 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 15.354 | 16 | 8.86 | 1 | 6.645 | 72.45 | 72.45 | 4291420 | 11 | 59232.8502 | 16.8825 | 48.3 | 62.6617
185 | 185 | CL1-185 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 11.12 | 12 | 6.948 | 1 | 5.211 | 55.2 | 55.2 | 3448180 | 11 | 62467.029 | 16.0084 | 72.45 | 59.2329
186 | 186 | CL1-186 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.97 | 10 | 2.042 | 1 | 1.5315 | 13.8 | 13.8 | 1050490 | 4 | 76122.4638 | 13.1367 | 55.2 | 62.467
187 | 187 | CL1-187 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 10.584 | 11 | 2.392 | 1 | 1.794 | 17.25 | 17.25 | 1120760 | 4 | 64971.5942 | 15.3913 | 13.8 | 76.1225
188 | 188 | CL1-188 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 13.975 | 14 | 13.357 | 1 | 10.0177 | 106.95 | 106.95 | 3869800 | 11 | 36183.2632 | 27.6371 | 17.25 | 64.9716
189 | 189 | CL1-189 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 12.384 | 13 | 1.422 | 1 | 1.0665 | 10.35 | 10.35 | 1627650 | 3 | 157260.8696 | 6.3589 | 106.95 | 36.1833
190 | 190 | CL1-190 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.513 | 14 | 5.568 | 1 | 4.176 | 44.85 | 44.85 | 1905430 | 6 | 42484.5039 | 23.538 | 10.35 | 157.2609
191 | 191 | CL1-191 | KERRY | KERRY | SS-321 | Milltown 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 18.797 | 19 | 1.104 | 1 | 0.828 | 6.9 | 6.9 | 1906800 | 2 | 276347.8261 | 3.6186 | 44.85 | 42.4845
192 | 192 | CL1-192 | KERRY | KERRY | SS-321 | Milltown 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 14.896 | 15 | 15.406 | 1 | 11.5545 | 124.2 | 124.2 | 5849260 | 13 | 47095.4911 | 21.2335 | 6.9 | 276.3478
193 | 193 | CL1-193 | KERRY | KERRY | SS-387 | Coolcorcoran 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.408 | 11 | 2.861 | 1 | 2.1458 | 20.7 | 20.7 | 1120760 | 4 | 54142.9952 | 18.4696 | 124.2 | 47.0955
194 | 194 | CL1-194 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.569 | 6 | 2.152 | 1 | 1.614 | 17.25 | 17.25 | 769410 | 4 | 44603.4783 | 22.4198 | 20.7 | 54.143
195 | 195 | CL1-195 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.039 | 8 | 0.663 | 1 | 0.49725 | 3.45 | 3.45 | 909950 | 4 | 263753.6232 | 3.7914 | 17.25 | 44.6035
196 | 196 | CL1-196 | KERRY | KERRY | SS-637 | Kilgarvan 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.924 | 8 | 9.987 | 1 | 7.4902 | 79.35 | 79.35 | 2604940 | 11 | 32828.4814 | 30.4614 | 3.45 | 263.7536
197 | 197 | CL1-197 | KERRY | KERRY | SS-072 | Clonkeen 110kV Substation | EirGrid | 110000 |  |  | 5.594 | 6 | 2.063 | 1 | 1.5473 | 13.8 | 13.8 | 2016330 | 8 | 146110.8696 | 6.8441 | 79.35 | 32.8285
198 | 198 | CL1-198 | KERRY | KERRY | SS-636 | Garranebane 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.144 | 10 | 0.369 | 1 | 0.369 | 3.45 | 3.45 | 1387140 | 1 | 402069.5652 | 2.4871 | 13.8 | 146.1109
199 | 199 | CL1-199 | KERRY | KERRY | SS-636 | Garranebane 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.532 | 9 | 6.743 | 1 | 5.0572 | 55.2 | 55.2 | 2815750 | 11 | 51009.9638 | 19.604 | 3.45 | 402.0696
200 | 200 | CL1-200 | KERRY | KERRY | SS-636 | Garranebane 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.371 | 6 | 1.184 | 1 | 0.888 | 6.9 | 6.9 | 769410 | 4 | 111508.6957 | 8.9679 | 55.2 | 51.01
201 | 201 | CL1-201 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 8.279 | 9 | 17.913 | 1 | 13.4348 | 144.9 | 144.9 | 4339180 | 12 | 29946.0317 | 33.3934 | 6.9 | 111.5087
202 | 202 | CL1-202 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 13.341 | 14 | 0.966 | 1 | 0.7245 | 6.9 | 6.9 | 1643300 | 2 | 238159.4203 | 4.1989 | 144.9 | 29.946
203 | 203 | CL1-203 | KERRY | KERRY | SS-321 | Milltown 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 16.988 | 17 | 1.43 | 1 | 1.0725 | 10.35 | 10.35 | 1838450 | 3 | 177628.0193 | 5.6297 | 6.9 | 238.1594
204 | 204 | CL1-204 | CORK | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.629 | 9 | 12.789 | 1 | 9.5917 | 103.5 | 103.5 | 2815750 | 11 | 27205.314 | 36.7575 | 10.35 | 177.628
205 | 205 | CL1-205 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 3.383 | 4 | 3.72 | 1 | 2.79 | 27.6 | 27.6 | 703110 | 5 | 25475 | 39.2542 | 103.5 | 27.2053
206 | 206 | CL1-206 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 14.468 | 15 | 2.644 | 1 | 1.983 | 20.7 | 20.7 | 1401840 | 4 | 67721.7391 | 14.7663 | 27.6 | 25.475
207 | 207 | CL1-207 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.946 | 9 | 15.538 | 1 | 11.6535 | 127.65 | 127.65 | 4339180 | 12 | 33992.7928 | 29.418 | 20.7 | 67.7217
208 | 208 | CL1-208 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 3.081 | 4 | 6.578 | 1 | 4.9335 | 51.75 | 51.75 | 1761700 | 11 | 34042.5121 | 29.375 | 127.65 | 33.9928
209 | 209 | CL1-209 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.995 | 8 | 8.582 | 1 | 6.4365 | 69 | 69 | 2604940 | 11 | 37752.7536 | 26.4881 | 51.75 | 34.0425
210 | 210 | CL1-210 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.843 | 8 | 10.34 | 1 | 7.755 | 82.8 | 82.8 | 2604940 | 11 | 31460.628 | 31.7858 | 69 | 37.7528
211 | 211 | CL1-211 | KERRY | KERRY | SS-667 | Ballyrickard 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 9.133 | 10 | 16.492 | 1 | 12.369 | 134.55 | 134.55 | 4719260 | 12 | 35074.3961 | 28.5108 | 82.8 | 31.4606
212 | 212 | CL1-212 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.018 | 5 | 4.313 | 1 | 3.2348 | 34.5 | 34.5 | 904090 | 6 | 26205.5072 | 38.1599 | 134.55 | 35.0744
213 | 213 | CL1-213 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 21.669 | 22 | 1.913 | 1 | 1.4347 | 13.8 | 13.8 | 1893730 | 4 | 137226.8116 | 7.2872 | 34.5 | 26.2055
214 | 214 | CL1-214 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 22.972 | 23 | 4.004 | 1 | 3.003 | 31.05 | 31.05 | 2906770 | 6 | 93615.781 | 10.682 | 13.8 | 137.2268
215 | 215 | CL1-215 | CLARE | CLARE | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 19.212 | 20 | 1.345 | 1 | 1.0088 | 10.35 | 10.35 | 1996550 | 3 | 192903.3816 | 5.1839 | 31.05 | 93.6158
216 | 216 | CL1-216 | CLARE | CLARE | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 19.128 | 20 | 0.554 | 1 | 0.554 | 3.45 | 3.45 | 1914140 | 1 | 554823.1884 | 1.8024 | 10.35 | 192.9034
217 | 217 | CL1-217 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.741 | 14 | 5.485 | 1 | 4.1138 | 44.85 | 44.85 | 1905430 | 6 | 42484.5039 | 23.538 | 3.45 | 554.8232
218 | 218 | CL1-218 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.695 | 4 | 2.983 | 1 | 2.2372 | 24.15 | 24.15 | 703110 | 5 | 29114.2857 | 34.3474 | 44.85 | 42.4845
219 | 219 | CL1-219 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.263 | 7 | 11.505 | 1 | 8.6288 | 93.15 | 93.15 | 2394130 | 11 | 25701.8787 | 38.9077 | 24.15 | 29.1143
220 | 220 | CL1-220 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.121 | 8 | 1.63 | 1 | 1.2225 | 10.35 | 10.35 | 909950 | 4 | 87917.8744 | 11.3743 | 93.15 | 25.7019
221 | 221 | CL1-221 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.911 | 11 | 1.547 | 1 | 1.1603 | 10.35 | 10.35 | 1522250 | 3 | 147077.2947 | 6.7991 | 10.35 | 87.9179
222 | 222 | CL1-222 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.39 | 10 | 18.324 | 1 | 13.743 | 148.35 | 148.35 | 4719260 | 12 | 31811.6616 | 31.435 | 10.35 | 147.0773
223 | 223 | CL1-223 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.161 | 14 | 6.434 | 1 | 4.8255 | 51.75 | 51.75 | 3869800 | 11 | 74778.744 | 13.3728 | 148.35 | 31.8117
224 | 224 | CL1-224 | MAYO | GALWAY | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 20.358 | 21 | 20.53 | 1 | 15.3975 | 169.05 | 169.05 | 15643160 | 13 | 92535.6995 | 10.8066 | 51.75 | 74.7787
225 | 225 | CL1-225 | MAYO | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 18.419 | 19 | 2.496 | 1 | 1.872 | 17.25 | 17.25 | 1682920 | 4 | 97560.5797 | 10.25 | 169.05 | 92.5357
226 | 226 | CL1-226 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 16.926 | 17 | 10.236 | 1 | 7.677 | 82.8 | 82.8 | 4502230 | 11 | 54374.7585 | 18.3909 | 17.25 | 97.5606
227 | 227 | CL1-227 | GALWAY | GALWAY | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 15.008 | 16 | 1.758 | 1 | 1.3185 | 13.8 | 13.8 | 1472110 | 4 | 106674.6377 | 9.3743 | 82.8 | 54.3748
228 | 228 | CL1-228 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 17.091 | 18 | 12.993 | 1 | 9.7447 | 106.95 | 106.95 | 4713040 | 11 | 44067.6952 | 22.6924 | 13.8 | 106.6746
229 | 229 | CL1-229 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 13.438 | 14 | 8.719 | 1 | 6.5392 | 69 | 69 | 3869800 | 11 | 56084.058 | 17.8304 | 106.95 | 44.0677
230 | 230 | CL1-230 | GALWAY | GALWAY | SS-638 | Oughterard 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 10.127 | 11 | 2.15 | 1 | 1.6125 | 17.25 | 17.25 | 1120760 | 4 | 64971.5942 | 15.3913 | 69 | 56.0841
231 | 231 | CL1-231 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 12.156 | 13 | 1.283 | 1 | 0.96225 | 10.35 | 10.35 | 2101570 | 7 | 203050.2415 | 4.9249 | 17.25 | 64.9716
232 | 232 | CL1-232 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.141 | 8 | 1.998 | 1 | 1.4985 | 13.8 | 13.8 | 909950 | 4 | 65938.4058 | 15.1657 | 10.35 | 203.0502
233 | 233 | CL1-233 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.739 | 8 | 4.156 | 1 | 3.117 | 31.05 | 31.05 | 1237870 | 6 | 39866.9887 | 25.0834 | 13.8 | 65.9384
234 | 234 | CL1-234 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 24.853 | 25 | 4.089 | 1 | 3.0668 | 31.05 | 31.05 | 4735350 | 10 | 152507.2464 | 6.5571 | 31.05 | 39.867
235 | 235 | CL1-235 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 20.307 | 21 | 18.723 | 1 | 14.0422 | 151.8 | 151.8 | 7821580 | 13 | 51525.5599 | 19.4078 | 31.05 | 152.5072
236 | 236 | CL1-236 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 16.598 | 17 | 4.129 | 1 | 3.0967 | 31.05 | 31.05 | 2239210 | 6 | 72116.2641 | 13.8665 | 151.8 | 51.5256
237 | 237 | CL1-237 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.876 | 12 | 2.761 | 1 | 2.0708 | 20.7 | 20.7 | 1191030 | 4 | 57537.6812 | 17.3799 | 31.05 | 72.1163
238 | 238 | CL1-238 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 11.364 | 12 | 6.367 | 1 | 4.7752 | 51.75 | 51.75 | 3448180 | 11 | 66631.4976 | 15.0079 | 20.7 | 57.5377
239 | 239 | CL1-239 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 28.426 | 29 | 1.094 | 1 | 0.8205 | 6.9 | 6.9 | 2944770 | 7 | 426778.2609 | 2.3431 | 51.75 | 66.6315
240 | 240 | CL1-240 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 27.225 | 28 | 15.775 | 1 | 11.8313 | 127.65 | 127.65 | 10122620 | 13 | 79299.8042 | 12.6104 | 6.9 | 426.7783
241 | 241 | CL1-241 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.101 | 11 | 2.372 | 1 | 1.779 | 17.25 | 17.25 | 1120760 | 4 | 64971.5942 | 15.3913 | 127.65 | 79.2998
242 | 242 | CL1-242 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.846 | 11 | 10.837 | 1 | 8.1277 | 86.25 | 86.25 | 3237370 | 11 | 37534.7246 | 26.642 | 17.25 | 64.9716
243 | 243 | CL1-243 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.486 | 6 | 14.814 | 1 | 11.1105 | 120.75 | 120.75 | 2183320 | 11 | 18081.3251 | 55.3057 | 86.25 | 37.5347
244 | 244 | CL1-244 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 2.066 | 3 | 2.707 | 1 | 2.0302 | 20.7 | 20.7 | 558600 | 4 | 26985.5072 | 37.0569 | 120.75 | 18.0813
245 | 245 | CL1-245 | MAYO | MAYO | SS-317 | Newport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.604 | 9 | 2.832 | 1 | 2.124 | 20.7 | 20.7 | 980220 | 4 | 47353.6232 | 21.1177 | 20.7 | 26.9855
246 | 246 | CL1-246 | MAYO | MAYO | SS-317 | Newport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 12.316 | 13 | 9.635 | 1 | 7.2263 | 79.35 | 79.35 | 3658990 | 11 | 46112.0353 | 21.6863 | 20.7 | 47.3536
247 | 247 | CL1-247 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 11.611 | 12 | 1.172 | 1 | 0.879 | 6.9 | 6.9 | 2048870 | 7 | 296937.6812 | 3.3677 | 79.35 | 46.112
248 | 248 | CL1-248 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.216 | 6 | 2.556 | 1 | 1.917 | 20.7 | 20.7 | 769410 | 4 | 37169.5652 | 26.9037 | 6.9 | 296.9377
249 | 249 | CL1-249 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.999 | 7 | 0.758 | 1 | 0.5685 | 3.45 | 3.45 | 839680 | 4 | 243385.5072 | 4.1087 | 20.7 | 37.1696
250 | 250 | CL1-250 | MAYO | MAYO | SS-498 | Belmullet 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.885 | 14 | 0.782 | 1 | 0.5865 | 3.45 | 3.45 | 1597940 | 1 | 463171.0145 | 2.159 | 3.45 | 243.3855
251 | 251 | CL1-251 | MAYO | MAYO | SS-498 | Belmullet 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.205 | 9 | 1 | 1 | 0.75 | 6.9 | 6.9 | 1379800 | 2 | 199971.0145 | 5.0007 | 3.45 | 463.171
252 | 252 | CL1-252 | MAYO | MAYO | SS-498 | Belmullet 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.962 | 6 | 0.524 | 1 | 0.524 | 3.45 | 3.45 | 769410 | 4 | 223017.3913 | 4.484 | 6.9 | 199.971
253 | 253 | CL1-253 | MAYO | MAYO | SS-498 | Belmullet 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.933 | 8 | 4.247 | 1 | 3.1852 | 34.5 | 34.5 | 1237870 | 6 | 35880.2899 | 27.8705 | 3.45 | 223.0174
254 | 254 | CL1-254 | MAYO | MAYO | SS-498 | Belmullet 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.321 | 10 | 0.648 | 1 | 0.486 | 3.45 | 3.45 | 1387140 | 1 | 402069.5652 | 2.4871 | 34.5 | 35.8803
255 | 255 | CL1-255 | MAYO | MAYO | SS-170 | Derrynadivva 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.829 | 4 | 1.46 | 1 | 1.095 | 10.35 | 10.35 | 628870 | 4 | 60760.3865 | 16.4581 | 3.45 | 402.0696
256 | 256 | CL1-256 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 20.892 | 21 | 2.12 | 1 | 1.59 | 17.25 | 17.25 | 1823460 | 4 | 105707.8261 | 9.46 | 10.35 | 60.7604
257 | 257 | CL1-257 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 19.36 | 20 | 4.433 | 1 | 3.3247 | 34.5 | 34.5 | 2572990 | 6 | 74579.4203 | 13.4085 | 17.25 | 105.7078
258 | 258 | CL1-258 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 19.862 | 20 | 4.701 | 1 | 3.5257 | 37.95 | 37.95 | 2572990 | 6 | 67799.473 | 14.7494 | 34.5 | 74.5794
259 | 259 | CL1-259 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 18.649 | 19 | 3.594 | 1 | 2.6955 | 27.6 | 27.6 | 2035560 | 5 | 73752.1739 | 13.5589 | 37.95 | 67.7995
260 | 260 | CL1-260 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.249 | 6 | 4.087 | 1 | 3.0652 | 31.05 | 31.05 | 1015350 | 6 | 32700.4831 | 30.5806 | 27.6 | 73.7522
261 | 261 | CL1-261 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.634 | 8 | 13.508 | 1 | 10.131 | 110.4 | 110.4 | 2604940 | 11 | 23595.471 | 42.381 | 31.05 | 32.7005
262 | 262 | CL1-262 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 11.935 | 12 | 1.656 | 1 | 1.242 | 10.35 | 10.35 | 2048870 | 7 | 197958.4541 | 5.0516 | 110.4 | 23.5955
263 | 263 | CL1-263 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 12.838 | 13 | 0.609 | 1 | 0.45675 | 3.45 | 3.45 | 2101570 | 7 | 609150.7246 | 1.6416 | 10.35 | 197.9585
264 | 264 | CL1-264 | MAYO | MAYO | SS-710 | Tawnaghmore 110kV Substation | EirGrid | 110000 | low | 110000 | 14.993 | 15 | 2.679 | 1 | 2.0092 | 20.7 | 20.7 | 2648760 | 8 | 127959.4203 | 7.815 | 3.45 | 609.1507
265 | 265 | CL1-265 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 14.738 | 15 | 2.013 | 1 | 1.5097 | 13.8 | 13.8 | 2648760 | 8 | 191939.1304 | 5.21 | 20.7 | 127.9594
266 | 266 | CL1-266 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 18.245 | 19 | 15.594 | 1 | 11.6955 | 127.65 | 127.65 | 7164140 | 13 | 56123.3059 | 17.8179 | 13.8 | 191.9391
267 | 267 | CL1-267 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.128 | 11 | 2.296 | 1 | 1.722 | 17.25 | 17.25 | 1120760 | 4 | 64971.5942 | 15.3913 | 127.65 | 56.1233
268 | 268 | CL1-268 | MAYO | MAYO | SS-498 | Belmullet 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.132 | 9 | 5.163 | 1 | 3.8723 | 41.4 | 41.4 | 1349130 | 6 | 32587.6812 | 30.6864 | 17.25 | 64.9716
269 | 269 | CL1-269 | SLIGO | MAYO | SS-302 | Carrowleagh 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.842 | 3 | 2.725 | 1 | 2.0438 | 20.7 | 20.7 | 558600 | 4 | 26985.5072 | 37.0569 | 41.4 | 32.5877
270 | 270 | CL1-270 | SLIGO | SLIGO | SS-075 | Cunghill 110kV Substation | EirGrid | 110000 | 110000 | medium | 8.03 | 9 | 0.97 | 1 | 0.7275 | 6.9 | 6.9 | 1890770 | 7 | 274024.6377 | 3.6493 | 20.7 | 26.9855
271 | 271 | CL1-271 | SLIGO | SLIGO | SS-075 | Cunghill 110kV Substation | EirGrid | 110000 | 110000 | medium | 9.282 | 10 | 1.414 | 1 | 1.0605 | 10.35 | 10.35 | 1943470 | 7 | 187774.8792 | 5.3255 | 6.9 | 274.0246
272 | 272 | CL1-272 | SLIGO | SLIGO | SS-042 | Ballytivnan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 10.469 | 11 | 0.841 | 1 | 0.63075 | 6.9 | 6.9 | 1485200 | 2 | 215246.3768 | 4.6458 | 10.35 | 187.7749
273 | 273 | CL1-273 | SLIGO | LEITRIM | SS-227 | Bundoran 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.815 | 12 | 5.689 | 1 | 4.2668 | 44.85 | 44.85 | 1682910 | 6 | 37523.0769 | 26.6503 | 6.9 | 215.2464
274 | 274 | CL1-274 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 9.236 | 10 | 9.968 | 1 | 7.476 | 79.35 | 79.35 | 3026560 | 11 | 38141.903 | 26.2179 | 44.85 | 37.5231
275 | 275 | CL1-275 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 10.019 | 11 | 0.8 | 1 | 0.6 | 6.9 | 6.9 | 1485200 | 2 | 215246.3768 | 4.6458 | 79.35 | 38.1419
276 | 276 | CL1-276 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.646 | 8 | 2.904 | 1 | 2.178 | 20.7 | 20.7 | 909950 | 4 | 43958.9372 | 22.7485 | 6.9 | 215.2464
277 | 277 | CL1-277 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 9.77 | 10 | 4.818 | 1 | 3.6135 | 37.95 | 37.95 | 1460390 | 6 | 38481.9499 | 25.9862 | 20.7 | 43.9589
278 | 278 | CL1-278 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.452 | 9 | 0.912 | 1 | 0.684 | 6.9 | 6.9 | 1379800 | 2 | 199971.0145 | 5.0007 | 37.95 | 38.4819
279 | 279 | CL1-279 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 11.802 | 12 | 0.67 | 1 | 0.5025 | 3.45 | 3.45 | 1492540 | 1 | 432620.2899 | 2.3115 | 6.9 | 199.971
280 | 280 | CL1-280 | DONEGAL | DONEGAL | SS-090 | Corkermore 38kV Substation | ESB Networks | 38000 | low | 38000 | 8.711 | 9 | 2.276 | 1 | 1.707 | 17.25 | 17.25 | 980220 | 4 | 56824.3478 | 17.5981 | 3.45 | 432.6203
281 | 281 | CL1-281 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 12.646 | 13 | 1.967 | 1 | 1.4752 | 13.8 | 13.8 | 1261300 | 4 | 91398.5507 | 10.9411 | 17.25 | 56.8243
282 | 282 | CL1-282 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 11.973 | 12 | 11.981 | 1 | 8.9857 | 96.6 | 96.6 | 3448180 | 11 | 35695.4451 | 28.0148 | 13.8 | 91.3986
283 | 283 | CL1-283 | DONEGAL | DONEGAL | SS-252 | Killybegs 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 4.503 | 5 | 1.343 | 1 | 1.0072 | 10.35 | 10.35 | 699140 | 4 | 67549.7585 | 14.8039 | 96.6 | 35.6954
284 | 284 | CL1-284 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 2.813 | 3 | 1.037 | 1 | 0.77775 | 6.9 | 6.9 | 558600 | 4 | 80956.5217 | 12.3523 | 10.35 | 67.5498
285 | 285 | CL1-285 | DONEGAL | DONEGAL | SS-090 | Corkermore 38kV Substation | ESB Networks | 38000 | low | 38000 | 7.324 | 8 | 3.946 | 1 | 2.9595 | 31.05 | 31.05 | 1237870 | 6 | 39866.9887 | 25.0834 | 6.9 | 80.9565
286 | 286 | CL1-286 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 5.937 | 6 | 1.646 | 1 | 1.2345 | 10.35 | 10.35 | 769410 | 4 | 74339.1304 | 13.4519 | 31.05 | 39.867
287 | 287 | CL1-287 | DONEGAL | DONEGAL | SS-090 | Corkermore 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.155 | 4 | 1.55 | 1 | 1.1625 | 10.35 | 10.35 | 628870 | 4 | 60760.3865 | 16.4581 | 10.35 | 74.3391
288 | 288 | CL1-288 | DONEGAL | DONEGAL | SS-686 | Dungloe 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.46 | 7 | 0.554 | 1 | 0.554 | 3.45 | 3.45 | 839680 | 4 | 243385.5072 | 4.1087 | 10.35 | 60.7604
289 | 289 | CL1-289 | DONEGAL | DONEGAL | SS-138 | Creeslough 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.95 | 11 | 0.831 | 1 | 0.62325 | 6.9 | 6.9 | 1485200 | 2 | 215246.3768 | 4.6458 | 3.45 | 243.3855
290 | 290 | CL1-290 | DONEGAL | DONEGAL | SS-610 | Milford (North) 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.05 | 11 | 2.185 | 1 | 1.6387 | 17.25 | 17.25 | 1120760 | 4 | 64971.5942 | 15.3913 | 6.9 | 215.2464
291 | 291 | CL1-291 | DONEGAL | DONEGAL | SS-119 | Drumlough Hill (1) 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.531 | 3 | 2.733 | 1 | 2.0497 | 20.7 | 20.7 | 558600 | 4 | 26985.5072 | 37.0569 | 17.25 | 64.9716
292 | 292 | CL1-292 | DONEGAL | DONEGAL | SS-119 | Drumlough Hill (1) 38kV Substation | ESB Networks | 38000 | low | 38000 | 5.448 | 6 | 5.765 | 1 | 4.3237 | 44.85 | 44.85 | 1015350 | 6 | 22638.796 | 44.172 | 20.7 | 26.9855
293 | 293 | CL1-293 | DONEGAL | DONEGAL | SS-272 | Carndonagh 38kV | ESB Networks | 38000 | 38000 | low | 11.922 | 12 | 1.662 | 1 | 1.2465 | 10.35 | 10.35 | 1574950 | 3 | 152169.0821 | 6.5716 | 44.85 | 22.6388
294 | 294 | CL1-294 | DONEGAL | DONEGAL | SS-239 | Moville 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.566 | 7 | 5.047 | 1 | 3.7852 | 41.4 | 41.4 | 1126610 | 6 | 27212.8019 | 36.7474 | 10.35 | 152.1691
295 | 295 | CL1-295 | DONEGAL | DONEGAL | SS-272 | Carndonagh 38kV | ESB Networks | 38000 | 38000 | low | 4.304 | 5 | 1.5 | 1 | 1.125 | 10.35 | 10.35 | 699140 | 4 | 67549.7585 | 14.8039 | 41.4 | 27.2128
296 | 296 | CL1-296 | DONEGAL | DONEGAL | SS-125 | Drumlough Hill (2) 38kV Substation | ESB Networks | 38000 | low | 38000 | 6.28 | 7 | 10.893 | 1 | 8.1698 | 89.7 | 89.7 | 2394130 | 11 | 26690.4125 | 37.4666 | 10.35 | 67.5498
297 | 297 | CL1-297 | DONEGAL | DONEGAL | SS-689 |  | ESB Networks | 38000 |  |  | 3.247 | 4 | 6.507 | 1 | 4.8803 | 51.75 | 51.75 | 1761700 | 11 | 34042.5121 | 29.375 | 89.7 | 26.6904
298 | 298 | CL1-298 | DONEGAL | DONEGAL | SS-689 |  | ESB Networks | 38000 |  |  | 5.159 | 6 | 0.583 | 1 | 0.583 | 3.45 | 3.45 | 769410 | 4 | 223017.3913 | 4.484 | 51.75 | 34.0425
299 | 299 | CL1-299 | DONEGAL | DONEGAL | SS-689 |  | ESB Networks | 38000 |  |  | 2.28 | 3 | 1.624 | 1 | 1.218 | 10.35 | 10.35 | 558600 | 4 | 53971.0145 | 18.5285 | 3.45 | 223.0174
300 | 300 | CL1-300 | DONEGAL | DONEGAL | SS-687 | Gweedore Wind Farm 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.454 | 3 | 6.746 | 1 | 5.0595 | 55.2 | 55.2 | 1550890 | 11 | 28095.8333 | 35.5925 | 10.35 | 53.971
301 | 301 | CL1-301 | DONEGAL | DONEGAL | SS-687 | Gweedore Wind Farm 38kV Substation | ESB Networks | 38000 | low | 38000 | 5.054 | 6 | 4.506 | 1 | 3.3795 | 34.5 | 34.5 | 1015350 | 6 | 29430.4348 | 33.9784 | 55.2 | 28.0958
302 | 302 | CL1-302 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.459 | 8 | 1.977 | 1 | 1.4828 | 13.8 | 13.8 | 909950 | 4 | 65938.4058 | 15.1657 | 34.5 | 29.4304
303 | 303 | CL1-303 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.238 | 7 | 4.423 | 1 | 3.3173 | 34.5 | 34.5 | 1126610 | 6 | 32655.3623 | 30.6228 | 13.8 | 65.9384
304 | 304 | CL1-304 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.479 | 8 | 1.943 | 1 | 1.4573 | 13.8 | 13.8 | 909950 | 4 | 65938.4058 | 15.1657 | 34.5 | 32.6554
305 | 305 | CL1-305 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.634 | 10 | 1.036 | 1 | 0.777 | 6.9 | 6.9 | 1432500 | 2 | 207608.6957 | 4.8168 | 13.8 | 65.9384
306 | 306 | CL1-306 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.101 | 11 | 1.13 | 1 | 0.8475 | 6.9 | 6.9 | 1485200 | 2 | 215246.3768 | 4.6458 | 6.9 | 207.6087
307 | 307 | CL1-307 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 13.898 | 14 | 4.42 | 1 | 3.315 | 34.5 | 34.5 | 1905430 | 6 | 55229.8551 | 18.1061 | 6.9 | 215.2464
308 | 308 | CL1-308 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 18.984 | 19 | 14.303 | 1 | 10.7273 | 117.3 | 117.3 | 4923850 | 11 | 41976.5558 | 23.8228 | 34.5 | 55.2299
309 | 309 | CL1-309 | DONEGAL | DONEGAL | SS-686 | Dungloe 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.432 | 14 | 3.26 | 1 | 2.445 | 24.15 | 24.15 | 1591410 | 5 | 65896.8944 | 15.1752 | 117.3 | 41.9766
311 | 311 | CL1-311 | WEXFORD | WEXFORD | SS-481 | Castledockrell 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 7.589 | 8 | 2.162 | 1 | 1.6215 | 17.25 | 17.25 | 2156870 | 8 | 125035.942 | 7.9977 | 24.15 | 65.8969
312 | 312 | CL1-312 | CARLOW | CARLOW | SS-481 | Castledockrell 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 11.318 | 12 | 1.034 | 1 | 0.7755 | 6.9 | 6.9 | 2048870 | 7 | 296937.6812 | 3.3677 | 17.25 | 125.0359
313 | 313 | CL1-313 | WICKLOW | WICKLOW | SS-062 | Stratford 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 7.135 | 8 | 1.989 | 1 | 1.4918 | 13.8 | 13.8 | 2156870 | 8 | 156294.9275 | 6.3982 | 6.9 | 296.9377
314 | 314 | CL1-314 | WICKLOW | WICKLOW | SS-222 | Poulaphouca 110kV Substation | EirGrid | 110000 | low | 110000 | 7.433 | 8 | 1.038 | 1 | 0.7785 | 6.9 | 6.9 | 1838070 | 7 | 266386.9565 | 3.7539 | 13.8 | 156.2949
315 | 315 | CL1-315 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.011 | 10 | 0.807 | 1 | 0.60525 | 6.9 | 6.9 | 1432500 | 2 | 207608.6957 | 4.8168 | 6.9 | 266.387
316 | 316 | CL1-316 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.015 | 8 | 0.346 | 1 | 0.346 | 3.45 | 3.45 | 909950 | 4 | 263753.6232 | 3.7914 | 6.9 | 207.6087
317 | 317 | CL1-317 | WICKLOW | WICKLOW | SS-062 | Stratford 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 7.293 | 8 | 2.401 | 1 | 1.8007 | 17.25 | 17.25 | 2156870 | 8 | 125035.942 | 7.9977 | 3.45 | 263.7536
318 | 318 | CL1-318 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.852 | 9 | 6.064 | 1 | 4.548 | 48.3 | 48.3 | 2815750 | 11 | 58297.1014 | 17.1535 | 17.25 | 125.0359
319 | 319 | CL1-319 | WICKLOW | WICKLOW | SS-699 | Ballycumber 38kV Substation | ESB Networks | 38000 | low | 38000 | 12.249 | 13 | 1.659 | 1 | 1.2443 | 10.35 | 10.35 | 1627650 | 3 | 157260.8696 | 6.3589 | 48.3 | 58.2971
320 | 320 | CL1-320 | WICKLOW | WICKLOW | SS-222 | Poulaphouca 110kV Substation | EirGrid | 110000 | low | 110000 | 14.393 | 15 | 0.194 | 1 | 0.194 | 3.45 | 3.45 | 2206970 | 7 | 639701.4493 | 1.5632 | 10.35 | 157.2609
321 | 321 | CL1-321 | WICKLOW | WICKLOW | SS-209 | Blessington 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.332 | 11 | 0.422 | 1 | 0.422 | 3.45 | 3.45 | 1439840 | 1 | 417344.9275 | 2.3961 | 3.45 | 639.7014
322 | 322 | CL1-322 | WICKLOW | WICKLOW | SS-570 | Kilcoole 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.819 | 12 | 0.672 | 1 | 0.504 | 3.45 | 3.45 | 1492540 | 1 | 432620.2899 | 2.3115 | 3.45 | 417.3449
323 | 323 | CL1-323 | WICKLOW | WICKLOW | SS-570 | Kilcoole 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.044 | 14 | 0.584 | 1 | 0.584 | 3.45 | 3.45 | 1597940 | 1 | 463171.0145 | 2.159 | 3.45 | 432.6203
324 | 324 | CL1-324 | WEXFORD | WICKLOW | SS-616 | Ballinvally 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 2.575 | 3 | 1.018 | 1 | 0.7635 | 6.9 | 6.9 | 558600 | 4 | 80956.5217 | 12.3523 | 3.45 | 463.171
325 | 325 | CL1-325 | CORK | KERRY | SS-668 | Coomataggart 110 kV Substation | EirGrid | 110000 | low | 110000 | 4.598 | 5 | 8.841 | 1 | 6.6307 | 72.45 | 72.45 | 1972510 | 11 | 27225.8109 | 36.7299 | 6.9 | 80.9565
326 | 326 | CL1-326 | CORK | KERRY | SS-668 | Coomataggart 110 kV Substation | EirGrid | 110000 | low | 110000 | 1.293 | 2 | 1.653 | 1 | 1.2397 | 10.35 | 10.35 | 1340080 | 11 | 129476.3285 | 7.7234 | 72.45 | 27.2258
327 | 327 | CL1-327 | CORK | CORK | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 6.498 | 7 | 1.688 | 1 | 1.266 | 13.8 | 13.8 | 839680 | 4 | 60846.3768 | 16.4348 | 10.35 | 129.4763
328 | 328 | CL1-328 | CORK | KERRY | SS-668 | Coomataggart 110 kV Substation | EirGrid | 110000 | low | 110000 | 3.847 | 4 | 0.928 | 1 | 0.696 | 6.9 | 6.9 | 1627270 | 7 | 235836.2319 | 4.2402 | 13.8 | 60.8464
329 | 329 | CL1-329 | CORK | KERRY | SS-162 | Garrow 110kV Substation | EirGrid | 110000 | 38000 | 110000 | 1.679 | 2 | 0.778 | 1 | 0.5835 | 3.45 | 3.45 | 1340080 | 11 | 388428.9855 | 2.5745 | 6.9 | 235.8362
330 | 330 | CL1-330 | KERRY | KERRY | SS-072 | Clonkeen 110kV Substation | EirGrid | 110000 |  |  | 3.747 | 4 | 2.918 | 1 | 2.1885 | 20.7 | 20.7 | 1875790 | 8 | 90617.8744 | 11.0354 | 3.45 | 388.429
331 | 331 | CL1-331 | KERRY | KERRY | SS-072 | Clonkeen 110kV Substation | EirGrid | 110000 |  |  | 6.185 | 7 | 1.525 | 1 | 1.1437 | 10.35 | 10.35 | 1785370 | 7 | 172499.5169 | 5.7971 | 20.7 | 90.6179
332 | 332 | CL1-332 | CORK | KERRY | SS-161 | Gneeves 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.021 | 5 | 6.163 | 1 | 4.6223 | 48.3 | 48.3 | 1972510 | 11 | 40838.7164 | 24.4866 | 10.35 | 172.4995
333 | 333 | CL1-333 | CORK | CORK | SS-615 | Knockduff 110kv Substation | EirGrid | 110000 |  |  | 5.262 | 6 | 1.717 | 1 | 1.2877 | 13.8 | 13.8 | 2016330 | 8 | 146110.8696 | 6.8441 | 48.3 | 40.8387
334 | 334 | CL1-334 | DONEGAL | DONEGAL | SS-686 | Dungloe 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.824 | 5 | 0.787 | 1 | 0.59025 | 3.45 | 3.45 | 699140 | 4 | 202649.2754 | 4.9346 | 13.8 | 146.1109
335 | 335 | CL1-335 | DONEGAL | DONEGAL | SS-333 | Clady 38kV Substation | ESB Networks | 38000 |  |  | 4.422 | 5 | 1.552 | 1 | 1.164 | 10.35 | 10.35 | 699140 | 4 | 67549.7585 | 14.8039 | 3.45 | 202.6493
336 | 336 | CL1-336 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.097 | 9 | 2.353 | 1 | 1.7648 | 17.25 | 17.25 | 2227140 | 8 | 129109.5652 | 7.7454 | 10.35 | 67.5498
337 | 337 | CL1-337 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 4.966 | 5 | 5.023 | 1 | 3.7672 | 41.4 | 41.4 | 2510150 | 10 | 60631.6425 | 16.493 | 17.25 | 129.1096
338 | 338 | CL1-338 | LEITRIM | LEITRIM | SS-227 | Bundoran 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.889 | 9 | 1.9 | 1 | 1.425 | 13.8 | 13.8 | 980220 | 4 | 71030.4348 | 14.0785 | 41.4 | 60.6316
339 | 339 | CL1-339 | LEITRIM | LEITRIM | SS-227 | Bundoran 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.917 | 9 | 8.488 | 1 | 6.366 | 69 | 69 | 2815750 | 11 | 40807.971 | 24.505 | 13.8 | 71.0304
340 | 340 | CL1-340 | LEITRIM | LEITRIM | SS-227 | Bundoran 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.87 | 9 | 2.771 | 1 | 2.0782 | 20.7 | 20.7 | 980220 | 4 | 47353.6232 | 21.1177 | 69 | 40.808
341 | 341 | CL1-341 | LEITRIM | LEITRIM | SS-304 | Arigna 110kV Substation | EirGrid | 110000 | 110000 | 20000 | 6.203 | 7 | 2.189 | 1 | 1.6418 | 17.25 | 17.25 | 2086600 | 8 | 120962.3188 | 8.267 | 20.7 | 47.3536
342 | 342 | CL1-342 | LEITRIM | LEITRIM | SS-304 | Arigna 110kV Substation | EirGrid | 110000 | 110000 | 20000 | 7.547 | 8 | 1.88 | 1 | 1.41 | 13.8 | 13.8 | 2156870 | 8 | 156294.9275 | 6.3982 | 17.25 | 120.9623
343 | 343 | CL1-343 | CAVAN | LEITRIM | SS-304 | Arigna 110kV Substation | EirGrid | 110000 | 110000 | 20000 | 12.263 | 13 | 2.756 | 1 | 2.067 | 20.7 | 20.7 | 2508220 | 8 | 121170.0483 | 8.2529 | 13.8 | 156.2949
344 | 344 | CL1-344 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.699 | 7 | 1.083 | 1 | 0.81225 | 6.9 | 6.9 | 839680 | 4 | 121692.7536 | 8.2174 | 20.7 | 121.17
345 | 345 | CL1-345 | SLIGO | MAYO | SS-078 | Glenree 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 3.298 | 4 | 5.047 | 1 | 3.7852 | 41.4 | 41.4 | 2398890 | 10 | 57944.2029 | 17.258 | 6.9 | 121.6928
346 | 346 | CL1-346 | MAYO | MAYO | SS-170 | Derrynadivva 38kV Substation | ESB Networks | 38000 | low | 38000 | 8.009 | 9 | 1.369 | 1 | 1.0268 | 10.35 | 10.35 | 1416850 | 3 | 136893.7198 | 7.3049 | 41.4 | 57.9442
347 | 347 | CL1-347 | MAYO | MAYO | SS-234 | Crossmolina 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.18 | 12 | 5.554 | 1 | 4.1655 | 44.85 | 44.85 | 1682910 | 6 | 37523.0769 | 26.6503 | 10.35 | 136.8937
348 | 348 | CL1-348 | DONEGAL | DONEGAL | SS-102 | Binbane 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 2.585 | 3 | 2.703 | 1 | 2.0272 | 20.7 | 20.7 | 1550890 | 11 | 74922.2222 | 13.3472 | 44.85 | 37.5231
349 | 349 | CL1-349 | DONEGAL | DONEGAL | SS-688 | Clogher 110kV Substation | EirGrid | 110000 |  |  | 6.776 | 7 | 3.551 | 1 | 2.6633 | 27.6 | 27.6 | 2575660 | 9 | 93321.0145 | 10.7157 | 20.7 | 74.9222
350 | 350 | CL1-350 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.61 | 9 | 0.601 | 1 | 0.45075 | 3.45 | 3.45 | 1890770 | 7 | 548049.2754 | 1.8247 | 27.6 | 93.321
351 | 351 | CL1-351 | DONEGAL | DONEGAL | SS-688 | Clogher 110kV Substation | EirGrid | 110000 |  |  | 10.138 | 11 | 14.991 | 1 | 11.2432 | 120.75 | 120.75 | 3237370 | 11 | 26810.5176 | 37.2988 | 3.45 | 548.0493
352 | 352 | CL1-352 | DONEGAL | DONEGAL | SS-196 | Culliagh 110kV Substation | EirGrid | 110000 | low | 110000 | 11.387 | 12 | 1.79 | 1 | 1.3425 | 13.8 | 13.8 | 2437950 | 8 | 176663.0435 | 5.6605 | 120.75 | 26.8105
353 | 353 | CL1-353 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 9.466 | 10 | 2.878 | 1 | 2.1585 | 20.7 | 20.7 | 2297410 | 8 | 110985.9903 | 9.0101 | 13.8 | 176.663
354 | 354 | CL1-354 | DONEGAL | DONEGAL | SS-196 | Culliagh 110kV Substation | EirGrid | 110000 | low | 110000 | 10.717 | 11 | 1.836 | 1 | 1.377 | 13.8 | 13.8 | 2367680 | 8 | 171571.0145 | 5.8285 | 20.7 | 110.986
355 | 355 | CL1-355 | DONEGAL | DONEGAL | SS-196 | Culliagh 110kV Substation | EirGrid | 110000 | low | 110000 | 8.105 | 9 | 0.547 | 1 | 0.547 | 3.45 | 3.45 | 1890770 | 7 | 548049.2754 | 1.8247 | 13.8 | 171.571
356 | 356 | CL1-356 | GALWAY | GALWAY | SS-623 | Uggool 110kV Substation | EirGrid | 110000 | 33000 | 110000 | 9.236 | 10 | 2.297 | 1 | 1.7228 | 17.25 | 17.25 | 2297410 | 8 | 133183.1884 | 7.5085 | 3.45 | 548.0493
357 | 357 | CL1-357 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 7.172 | 8 | 4.848 | 1 | 3.636 | 37.95 | 37.95 | 2843930 | 10 | 74938.8669 | 13.3442 | 17.25 | 133.1832
358 | 358 | CL1-358 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 4.082 | 5 | 1.768 | 1 | 1.326 | 13.8 | 13.8 | 1946060 | 8 | 141018.8406 | 7.0913 | 37.95 | 74.9389
359 | 359 | CL1-359 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 6.15 | 7 | 1.289 | 1 | 0.96675 | 10.35 | 10.35 | 1785370 | 7 | 172499.5169 | 5.7971 | 13.8 | 141.0188
360 | 360 | CL1-360 | KERRY | KERRY | SS-636 | Garranebane 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.635 | 6 | 1.725 | 1 | 1.2938 | 13.8 | 13.8 | 769410 | 4 | 55754.3478 | 17.9358 | 10.35 | 172.4995
361 | 361 | CL1-361 | CORK | CORK | SS-192 | Ballylickey 110kV Station | EirGrid | 110000 | 110000 | 38000 | 7.786 | 8 | 1.241 | 1 | 0.93075 | 6.9 | 6.9 | 1838070 | 7 | 266386.9565 | 3.7539 | 13.8 | 55.7543
362 | 362 | CL1-362 | TIPPERARY | WATERFORD | SS-455 | Ardfinnan 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.503 | 10 | 1.994 | 1 | 1.4955 | 13.8 | 13.8 | 1050490 | 4 | 76122.4638 | 13.1367 | 6.9 | 266.387
363 | 363 | CL1-363 | TIPPERARY | WATERFORD | SS-455 | Ardfinnan 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.598 | 9 | 2.784 | 1 | 2.088 | 20.7 | 20.7 | 980220 | 4 | 47353.6232 | 21.1177 | 13.8 | 76.1225
364 | 364 | CL1-364 | TIPPERARY | WATERFORD | SS-455 | Ardfinnan 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.11 | 10 | 0.688 | 1 | 0.516 | 3.45 | 3.45 | 1387140 | 1 | 402069.5652 | 2.4871 | 20.7 | 47.3536
365 | 365 | CL1-365 | TIPPERARY | TIPPERARY | SS-622 | Barranafaddock 38kV Substation | ESB Networks | 38000 | low | 38000 | 10.261 | 11 | 1.054 | 1 | 0.7905 | 6.9 | 6.9 | 1485200 | 2 | 215246.3768 | 4.6458 | 3.45 | 402.0696
366 | 366 | CL1-366 | WATERFORD | WATERFORD | SS-505 | Kilmacthomas 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.166 | 13 | 23.269 | 1 | 17.4517 | 189.75 | 189.75 | 10383640 | 13 | 54722.7404 | 18.2739 | 6.9 | 215.2464
367 | 367 | CL1-367 | LIMERICK | LIMERICK | SS-695 | Castlepook 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 3.561 | 4 | 1.56 | 1 | 1.17 | 10.35 | 10.35 | 628870 | 4 | 60760.3865 | 16.4581 | 189.75 | 54.7227
368 | 368 | CL1-368 | LIMERICK | LIMERICK | SS-257 | Kilshanny 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.142 | 9 | 1.717 | 1 | 1.2877 | 13.8 | 13.8 | 980220 | 4 | 71030.4348 | 14.0785 | 10.35 | 60.7604
369 | 369 | CL1-369 | TIPPERARY | LIMERICK | SS-585 | Kilross Road 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.095 | 12 | 11.912 | 1 | 8.934 | 96.6 | 96.6 | 3448180 | 11 | 35695.4451 | 28.0148 | 13.8 | 71.0304
370 | 370 | CL1-370 | CARLOW | WEXFORD | SS-492 | Graigue 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.064 | 12 | 3.091 | 1 | 2.3182 | 24.15 | 24.15 | 1413750 | 5 | 58540.3727 | 17.0822 | 96.6 | 35.6954
371 | 371 | CL1-371 | TIPPERARY | TIPPERARY | SS-064 | Ballydine 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.022 | 9 | 2.632 | 1 | 1.974 | 20.7 | 20.7 | 2227140 | 8 | 107591.3043 | 9.2944 | 24.15 | 58.5404
372 | 372 | CL1-372 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 17.982 | 18 | 5.172 | 1 | 3.879 | 41.4 | 41.4 | 2350470 | 6 | 56774.6377 | 17.6135 | 20.7 | 107.5913
373 | 373 | CL1-373 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 18.012 | 19 | 1.064 | 1 | 0.798 | 6.9 | 6.9 | 1906800 | 2 | 276347.8261 | 3.6186 | 41.4 | 56.7746
374 | 374 | CL1-374 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.349 | 8 | 1.487 | 1 | 1.1153 | 10.35 | 10.35 | 909950 | 4 | 87917.8744 | 11.3743 | 6.9 | 276.3478
375 | 375 | CL1-375 | CORK | CORK | SS-261 | Milane Hill 38kV Station | ESB Networks | 38000 |  |  | 6.673 | 7 | 0.822 | 1 | 0.6165 | 6.9 | 6.9 | 839680 | 4 | 121692.7536 | 8.2174 | 10.35 | 87.9179
376 | 376 | CL1-376 | GALWAY | CLARE | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.593 | 13 | 1.678 | 1 | 1.2585 | 13.8 | 13.8 | 1261300 | 4 | 91398.5507 | 10.9411 | 6.9 | 121.6928
377 | 377 | CL1-377 | GALWAY | CLARE | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.301 | 15 | 0.791 | 1 | 0.59325 | 3.45 | 3.45 | 1650640 | 1 | 478446.3768 | 2.0901 | 13.8 | 91.3986
378 | 378 | CL1-378 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 12.594 | 13 | 1.657 | 1 | 1.2428 | 10.35 | 10.35 | 1627650 | 3 | 157260.8696 | 6.3589 | 3.45 | 478.4464
379 | 379 | CL1-379 | CLARE | CLARE | SS-503 | Scariff 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.445 | 9 | 1.098 | 1 | 0.8235 | 6.9 | 6.9 | 1379800 | 2 | 199971.0145 | 5.0007 | 10.35 | 157.2609
380 | 380 | CL1-380 | WICKLOW | WICKLOW | SS-699 | Ballycumber 38kV Substation | ESB Networks | 38000 | low | 38000 | 6.186 | 7 | 1.285 | 1 | 0.96375 | 10.35 | 10.35 | 839680 | 4 | 81128.5024 | 12.3261 | 6.9 | 199.971
381 | 381 | CL1-381 | DONEGAL | DONEGAL | SS-610 | Milford (North) 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.001 | 7 | 4.038 | 1 | 3.0285 | 31.05 | 31.05 | 1126610 | 6 | 36283.7359 | 27.5606 | 10.35 | 81.1285
382 | 382 | CL1-382 | GALWAY | GALWAY | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 10.631 | 11 | 1.42 | 1 | 1.065 | 10.35 | 10.35 | 1522250 | 3 | 147077.2947 | 6.7991 | 31.05 | 36.2837
383 | 383 | CL1-383 | MAYO | MAYO | SS-710 | Tawnaghmore 110kV Substation | EirGrid | 110000 | low | 110000 | 11.377 | 12 | 0.716 | 1 | 0.537 | 3.45 | 3.45 | 2048870 | 7 | 593875.3623 | 1.6839 | 10.35 | 147.0773
384 | 384 | CL1-384 | MAYO | MAYO | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 12.936 | 13 | 0.665 | 1 | 0.49875 | 3.45 | 3.45 | 1545240 | 1 | 447895.6522 | 2.2327 | 3.45 | 593.8754
385 | 385 | CL1-385 | DONEGAL | DONEGAL | SS-117 | Crockahenny 38kV Substation | ESB Networks | 38000 | low | 38000 | 5.462 | 6 | 0.804 | 1 | 0.603 | 6.9 | 6.9 | 769410 | 4 | 111508.6957 | 8.9679 | 3.45 | 447.8957
386 | 386 | CL1-386 | MAYO | MAYO | SS-498 | Belmullet 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.255 | 14 | 1.149 | 1 | 0.86175 | 6.9 | 6.9 | 1643300 | 2 | 238159.4203 | 4.1989 | 6.9 | 111.5087
387 | 387 | CL2-001 | DONEGAL | DONEGAL | SS-118 | Sorne Hill 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 1.519 | 2 | 0.136 | 2 | 0.136 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341 | 6.9 | 238.1594
388 | 388 | CL2-002 | DONEGAL | DONEGAL | SS-688 | Clogher 110kV Substation | EirGrid | 110000 |  |  | 2.046 | 3 | 0.292 | 2 | 0.292 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674 | 4.2 | 319.0667
389 | 389 | CL2-003 | DONEGAL | DONEGAL | SS-643 | Donegal 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.945 | 5 | 0.288 | 2 | 0.288 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 374.8976
390 | 390 | CL2-004 | WEXFORD | WEXFORD | SS-237 | Carnsore 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 2.07 | 3 | 0.091 | 2 | 0.091 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 166.4619
391 | 391 | CL2-005 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.145 | 7 | 0.094 | 2 | 0.094 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 133
392 | 392 | CL2-006 | CLARE | CLARE | SS-595 | Kilkee 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.668 | 6 | 0.09 | 2 | 0.09 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 199.9238
393 | 393 | CL2-007 | CLARE | CLARE | SS-595 | Kilkee 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.385 | 6 | 0.192 | 2 | 0.192 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 183.1929
394 | 394 | CL2-008 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 3.407 | 4 | 0.143 | 2 | 0.143 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581 | 4.2 | 183.1929
395 | 395 | CL2-009 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 12.305 | 13 | 0.114 | 2 | 0.114 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718 | 4.2 | 387.4452
396 | 396 | CL2-010 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.624 | 7 | 0.09 | 2 | 0.09 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 367.9143
397 | 397 | CL2-011 | MAYO | MAYO | SS-170 | Derrynadivva 38kV Substation | ESB Networks | 38000 | low | 38000 | 7.282 | 8 | 0.144 | 2 | 0.144 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 199.9238
398 | 398 | CL2-012 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 17.352 | 18 | 0.096 | 2 | 0.096 | 4.2 | 4.2 | 1808740 | 1 | 430652.381 | 2.3221 | 4.2 | 216.6548
399 | 399 | CL2-013 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 21.42 | 22 | 0.099 | 2 | 0.099 | 4.2 | 4.2 | 2575870 | 7 | 613302.381 | 1.6305 | 4.2 | 430.6524
400 | 400 | CL2-014 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.424 | 8 | 0.094 | 2 | 0.094 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 613.3024
401 | 401 | CL2-015 | SLIGO | SLIGO | SS-075 | Cunghill 110kV Substation | EirGrid | 110000 | 110000 | medium | 8.315 | 9 | 0.101 | 2 | 0.101 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213 | 4.2 | 216.6548
402 | 402 | CL2-016 | SLIGO | SLIGO | SS-042 | Ballytivnan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 9.487 | 10 | 0.165 | 2 | 0.165 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 4.2 | 450.1833
403 | 403 | CL2-017 | DONEGAL | DONEGAL | SS-670 | Acres 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 6.088 | 7 | 0.144 | 2 | 0.144 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 330.2714
404 | 404 | CL2-018 | DONEGAL | DONEGAL | SS-697 | Clogheravaddy 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.188 | 2 | 0.169 | 2 | 0.169 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007 | 4.2 | 199.9238
405 | 405 | CL2-019 | DONEGAL | DONEGAL | SS-252 | Killybegs 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 4.884 | 5 | 0.094 | 2 | 0.094 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 116.269
406 | 406 | CL2-020 | DONEGAL | DONEGAL | SS-125 | Drumlough Hill (2) 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.634 | 5 | 0.129 | 2 | 0.129 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 166.4619
407 | 407 | CL2-021 | DONEGAL | DONEGAL | SS-689 |  | ESB Networks | 38000 |  |  | 5.587 | 6 | 0.12 | 2 | 0.12 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 166.4619
408 | 408 | CL2-022 | DONEGAL | DONEGAL | SS-686 | Dungloe 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.287 | 4 | 0.336 | 2 | 0.336 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 183.1929
409 | 409 | CL2-023 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 4.945 | 5 | 0.105 | 2 | 0.105 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5 | 4.2 | 149.731
410 | 410 | CL2-024 | MAYO | MAYO | SS-702 |  | ESB Networks | 38000 | low | 38000 | 1.455 | 2 | 0.101 | 2 | 0.101 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007 | 4.2 | 399.9929
411 | 411 | CL2-025 | CARLOW | CARLOW | SS-494 | Bunclody 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.386 | 7 | 0.099 | 2 | 0.099 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 116.269
412 | 412 | CL2-026 | WICKLOW | WICKLOW | SS-222 | Poulaphouca 110kV Substation | EirGrid | 110000 | low | 110000 | 10.122 | 11 | 0.094 | 2 | 0.094 | 4.2 | 4.2 | 1996170 | 7 | 475278.5714 | 2.104 | 4.2 | 199.9238
413 | 413 | CL2-027 | WICKLOW | WICKLOW | SS-222 | Poulaphouca 110kV Substation | EirGrid | 110000 | low | 110000 | 10.942 | 11 | 0.132 | 2 | 0.132 | 4.2 | 4.2 | 1996170 | 7 | 475278.5714 | 2.104 | 4.2 | 475.2786
414 | 414 | CL2-028 | WICKLOW | WICKLOW | SS-222 | Poulaphouca 110kV Substation | EirGrid | 110000 | low | 110000 | 8.578 | 9 | 0.145 | 2 | 0.145 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213 | 4.2 | 475.2786
415 | 415 | CL2-029 | DUBLIN | DUBLIN | SS-018 | Old Bawn 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.02 | 8 | 0.272 | 2 | 0.272 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 450.1833
416 | 416 | CL2-030 | WICKLOW | WICKLOW | SS-010 | Fassaroe 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 7.03 | 8 | 0.156 | 2 | 0.156 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285 | 4.2 | 216.6548
417 | 417 | CL2-031 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.978 | 3 | 0.152 | 2 | 0.152 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 437.6357
418 | 418 | CL2-032 | CORK | CORK | SS-070 | Glanlee 110kV Substation | EirGrid | 110000 | low | 110000 | 1.568 | 2 | 0.247 | 2 | 0.247 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341 | 4.2 | 133
419 | 419 | CL2-033 | CORK | CORK | SS-162 | Garrow 110kV Substation | EirGrid | 110000 | 38000 | 110000 | 3.66 | 4 | 0.137 | 2 | 0.137 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581 | 4.2 | 319.0667
420 | 420 | CL2-034 | CORK | CORK | SS-161 | Gneeves 38kV Substation | ESB Networks | 38000 | low | 38000 | 5.787 | 6 | 0.091 | 2 | 0.091 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 387.4452
421 | 421 | CL2-035 | CORK | CORK | SS-096 | Boggeragh 110kV Substation | EirGrid | 110000 |  |  | 3.731 | 4 | 0.136 | 2 | 0.136 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581 | 4.2 | 183.1929
422 | 422 | CL2-036 | LIMERICK | LIMERICK | SS-378 | Foynes 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.661 | 5 | 0.178 | 2 | 0.178 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 387.4452
423 | 423 | CL2-037 | DONEGAL | DONEGAL | SS-090 | Corkermore 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.324 | 2 | 0.127 | 2 | 0.127 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007 | 4.2 | 166.4619
424 | 424 | CL2-038 | ROSCOMMON | ROSCOMMON | SS-384 | Largan Hill 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.345 | 2 | 0.108 | 2 | 0.108 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007 | 4.2 | 116.269
425 | 425 | CL2-039 | DONEGAL | DONEGAL | SS-196 | Culliagh 110kV Substation | EirGrid | 110000 | low | 110000 | 2.274 | 3 | 0.189 | 2 | 0.189 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674 | 4.2 | 116.269
426 | 426 | CL2-040 | DONEGAL | DONEGAL | SS-196 | Culliagh 110kV Substation | EirGrid | 110000 | low | 110000 | 9.903 | 10 | 0.224 | 2 | 0.224 | 4.2 | 4.2 | 1943470 | 7 | 462730.9524 | 2.1611 | 4.2 | 374.8976
427 | 427 | CL2-041 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 8.467 | 9 | 0.166 | 2 | 0.166 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213 | 4.2 | 462.731
428 | 428 | CL2-042 | DONEGAL | DONEGAL | SS-690 | Stranrolar 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.52 | 4 | 0.17 | 2 | 0.17 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 450.1833
429 | 429 | CL2-043 | KERRY | KERRY | SS-636 | Garranebane 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.126 | 8 | 0.224 | 2 | 0.224 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 149.731
430 | 430 | CL2-044 | TIPPERARY | TIPPERARY | SS-347 | Glengoole 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.444 | 9 | 0.104 | 2 | 0.104 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 216.6548
431 | 431 | CL2-045 | WEXFORD | WEXFORD | SS-251 | Ballybrennan 38kV Substation | ESB Networks | 38000 | 38000 | low | 1.758 | 2 | 0.195 | 2 | 0.195 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007 | 4.2 | 317.7238
432 | 432 | CL2-046 | KILKENNY | KILKENNY | SS-372 | Ballyconra 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.024 | 13 | 0.197 | 2 | 0.197 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718 | 4.2 | 116.269
433 | 433 | CL2-047 | TIPPERARY | TIPPERARY | SS-645 | Toomevara 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.541 | 8 | 0.138 | 2 | 0.138 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 367.9143
434 | 434 | CL2-048 | GALWAY | GALWAY | SS-131 | Ros a Mh├¡l 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.764 | 11 | 0.332 | 2 | 0.332 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 216.6548
435 | 435 | CL2-049 | TIPPERARY | TIPPERARY | SS-660 | Nenagh 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.321 | 10 | 0.12 | 2 | 0.12 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 4.2 | 342.819
436 | 436 | CL2-050 | TIPPERARY | TIPPERARY | SS-397 | Glenough 38kV Substation | ESB Networks | 38000 | low | 38000 | 5.796 | 6 | 0.218 | 2 | 0.218 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 330.2714
437 | 437 | CL2-051 | OFFALY | OFFALY | SS-537 | Monaincha 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 8.055 | 9 | 0.206 | 2 | 0.206 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 183.1929
438 | 438 | CL2-052 | WICKLOW | WICKLOW | SS-209 | Blessington 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.753 | 7 | 0.128 | 2 | 0.128 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 317.7238
439 | 439 | CL2-053 | WICKLOW | WICKLOW | SS-222 | Poulaphouca 110kV Substation | EirGrid | 110000 | low | 110000 | 7.819 | 8 | 0.112 | 2 | 0.112 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285 | 4.2 | 199.9238
440 | 440 | CL2-054 | GALWAY | GALWAY | SS-057 | Galway 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.136 | 6 | 0.29 | 2 | 0.29 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424 | 4.2 | 437.6357
441 | 441 | CL2-055 | GALWAY | GALWAY | SS-038 | Salthill 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 6.375 | 7 | 0.21 | 2 | 0.21 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525 | 4.2 | 412.5405
442 | 442 | CL2-056 | CORK | CORK | SS-562 | Bantry 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.792 | 7 | 0.163 | 2 | 0.163 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 425.0881
443 | 443 | CL2-057 | GALWAY | GALWAY | SS-131 | Ros a Mh├¡l 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.18 | 3 | 0.255 | 2 | 0.255 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 199.9238
444 | 444 | CL2-058 | CORK | CORK | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 6.514 | 7 | 0.166 | 2 | 0.166 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 133
445 | 445 | CL2-059 | GALWAY | GALWAY | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 5.907 | 6 | 0.109 | 2 | 0.109 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 199.9238
446 | 446 | CL2-060 | GALWAY | GALWAY | SS-638 | Oughterard 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 4.42 | 5 | 0.131 | 2 | 0.131 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 183.1929
447 | 447 | CL2-061 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.053 | 11 | 0.112 | 2 | 0.112 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 166.4619
448 | 448 | CL2-062 | CLARE | CLARE | SS-595 | Kilkee 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.87 | 5 | 0.127 | 2 | 0.127 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 342.819
449 | 449 | CL2-063 | WATERFORD | WATERFORD | SS-607 | Curraglass 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.549 | 9 | 0.282 | 2 | 0.282 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 166.4619
450 | 450 | CL2-064 | LIMERICK | LIMERICK | SS-596 | Cappamore 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.113 | 7 | 0.097 | 2 | 0.097 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 317.7238
451 | 451 | CL2-065 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 2.567 | 3 | 0.208 | 2 | 0.208 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674 | 4.2 | 199.9238
452 | 452 | CL2-066 | CORK | CORK | SS-607 | Curraglass 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.605 | 9 | 0.094 | 2 | 0.094 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 374.8976
453 | 453 | CL2-067 | CORK | CORK | SS-536 | Knockacummer 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 4.482 | 5 | 0.099 | 2 | 0.099 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5 | 4.2 | 317.7238
454 | 454 | CL2-068 | WICKLOW | WICKLOW | SS-616 | Ballinvally 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 9.164 | 10 | 0.111 | 2 | 0.111 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 4.2 | 399.9929
455 | 455 | CL2-069 | GALWAY | GALWAY | SS-646 | Oranmore 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.744 | 5 | 0.108 | 2 | 0.108 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 330.2714
456 | 456 | CL2-070 | WEXFORD | WEXFORD | SS-033 | Ballywater 110kV Substation | EirGrid | 110000 | low | 110000 | 7.574 | 8 | 0.317 | 2 | 0.317 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285 | 4.2 | 166.4619
457 | 457 | CL2-071 | TIPPERARY | TIPPERARY | SS-535 | Garracummer 38kV Substation | ESB Networks | 38000 | low | 38000 | 7.443 | 8 | 0.294 | 2 | 0.294 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 437.6357
458 | 458 | CL2-072 | KERRY | LIMERICK | SS-703 |  | EirGrid | 110000 | low | 110000 | 7.224 | 8 | 0.111 | 2 | 0.111 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285 | 4.2 | 216.6548
459 | 459 | CL2-073 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 7.822 | 8 | 0.114 | 2 | 0.114 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285 | 4.2 | 437.6357
460 | 460 | CL2-074 | GALWAY | GALWAY | SS-131 | Ros a Mh├¡l 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.176 | 6 | 0.115 | 2 | 0.115 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 437.6357
461 | 461 | CL2-075 | CORK | CORK | SS-263 | Lake 38kV Station | ESB Networks | 38000 | 38000 | low | 4.225 | 5 | 0.383 | 2 | 0.383 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 183.1929
462 | 462 | CL2-076 | KERRY | KERRY | SS-189 | Knockearagh 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 6.526 | 7 | 0.113 | 2 | 0.113 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525 | 4.2 | 166.4619
463 | 463 | CL2-077 | WATERFORD | WATERFORD | SS-532 | Woodhouse 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 5.986 | 6 | 0.285 | 2 | 0.285 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424 | 4.2 | 425.0881
464 | 464 | CL2-078 | MAYO | MAYO | SS-203 | Foxford 38kV Substation | ESB Networks | 38000 |  |  | 6.169 | 7 | 0.196 | 2 | 0.196 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 412.5405
465 | 465 | CL2-079 | MAYO | MAYO | SS-640 | Ballinrobe 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.835 | 7 | 0.108 | 2 | 0.108 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 199.9238
466 | 466 | CL2-080 | MAYO | MAYO | SS-431 | Knockaphunta 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.056 | 12 | 0.166 | 2 | 0.166 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 199.9238
467 | 467 | CL2-081 | SLIGO | SLIGO | SS-095 | Collooney 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 6.099 | 7 | 0.137 | 2 | 0.137 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 355.3667
468 | 468 | CL2-082 | SLIGO | SLIGO | SS-095 | Collooney 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 3.086 | 4 | 0.157 | 2 | 0.157 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 199.9238
469 | 469 | CL2-083 | SLIGO | MAYO | SS-201 | Swinford 38kV Station | ESB Networks | 38000 | 38000 | low | 8.724 | 9 | 0.28 | 2 | 0.28 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 149.731
470 | 470 | CL2-084 | MAYO | MAYO | SS-170 | Derrynadivva 38kV Substation | ESB Networks | 38000 | low | 38000 | 11.466 | 12 | 0.13 | 2 | 0.13 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 317.7238
471 | 471 | CL2-085 | GALWAY | GALWAY | SS-598 | Glennamaddy 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.604 | 7 | 0.214 | 2 | 0.214 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 355.3667
472 | 472 | CL2-086 | GALWAY | GALWAY | SS-598 | Glennamaddy 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.383 | 8 | 0.103 | 2 | 0.103 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 199.9238
473 | 473 | CL2-087 | GALWAY | GALWAY | SS-598 | Glennamaddy 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.079 | 8 | 0.124 | 2 | 0.124 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 216.6548
474 | 474 | CL2-088 | MAYO | MAYO | SS-234 | Crossmolina 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.983 | 6 | 0.208 | 2 | 0.208 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 216.6548
475 | 475 | CL2-089 | LOUTH | LOUTH | SS-650 | Ballymascanlan 38kV Substation | ESB Networks | 38000 | 38000 | low | 1.639 | 2 | 0.222 | 2 | 0.222 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007 | 4.2 | 183.1929
476 | 476 | CL2-090 | GALWAY | GALWAY | SS-549 | Tuam North 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.713 | 7 | 0.343 | 2 | 0.343 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 116.269
477 | 477 | CL2-091 | MAYO | MAYO | SS-639 | Tonroe 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.212 | 9 | 0.385 | 2 | 0.385 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 199.9238
478 | 478 | CL2-092 | MAYO | MAYO | SS-640 | Ballinrobe 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.744 | 7 | 0.211 | 2 | 0.211 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 317.7238
479 | 479 | CL2-093 | MAYO | MAYO | SS-640 | Ballinrobe 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.292 | 8 | 0.274 | 2 | 0.274 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 199.9238
480 | 480 | CL2-094 | DONEGAL | DONEGAL | SS-272 | Carndonagh 38kV | ESB Networks | 38000 | 38000 | low | 6.06 | 7 | 0.134 | 2 | 0.134 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 216.6548
481 | 481 | CL2-095 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.372 | 10 | 0.128 | 2 | 0.128 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 4.2 | 199.9238
482 | 482 | CL2-096 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 12.004 | 13 | 0.103 | 2 | 0.103 | 4.2 | 4.2 | 2101570 | 7 | 500373.8095 | 1.9985 | 4.2 | 330.2714
483 | 483 | CL2-097 | SLIGO | SLIGO | SS-302 | Carrowleagh 38kV Substation | ESB Networks | 38000 | low | 38000 | 8.565 | 9 | 0.113 | 2 | 0.113 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 500.3738
484 | 484 | CL2-098 | MAYO | MAYO | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 5.78 | 6 | 0.109 | 2 | 0.109 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 317.7238
485 | 485 | CL2-099 | DONEGAL | DONEGAL | SS-083 | Golagh 110kV Substation | EirGrid | 110000 | 38000 | 110000 | 1.279 | 2 | 0.329 | 2 | 0.329 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341 | 4.2 | 183.1929
486 | 486 | CL2-100 | MAYO | MAYO | SS-170 | Derrynadivva 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.818 | 2 | 0.301 | 2 | 0.301 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007 | 4.2 | 319.0667
487 | 487 | CL2-101 | GALWAY | GALWAY | SS-109 | Cloon 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 9.631 | 10 | 0.517 | 2 | 0.517 | 4.2 | 4.2 | 1943470 | 7 | 462730.9524 | 2.1611 | 4.2 | 116.269
488 | 488 | CL2-102 | CORK | CORK | SS-161 | Gneeves 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.338 | 3 | 0.512 | 2 | 0.512 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 462.731
489 | 489 | CL2-103 | KERRY | KERRY | SS-636 | Garranebane 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.235 | 11 | 0.488 | 2 | 0.488 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 133
490 | 490 | CL2-104 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.346 | 9 | 0.103 | 2 | 0.103 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 342.819
491 | 491 | CL2-105 | KILKENNY | KILKENNY | SS-347 | Glengoole 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.804 | 12 | 0.154 | 2 | 0.154 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 317.7238
492 | 492 | CL2-106 | WATERFORD | WATERFORD | SS-505 | Kilmacthomas 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.321 | 7 | 0.412 | 2 | 0.412 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 355.3667
493 | 493 | CL2-107 | DONEGAL | DONEGAL | SS-689 |  | ESB Networks | 38000 |  |  | 11.25 | 12 | 0.312 | 2 | 0.312 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 199.9238
494 | 494 | CL2-108 | SLIGO | SLIGO | SS-227 | Bundoran 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.622 | 13 | 0.393 | 2 | 0.393 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718 | 4.2 | 355.3667
495 | 495 | CL2-109 | MAYO | MAYO | SS-201 | Swinford 38kV Station | ESB Networks | 38000 | 38000 | low | 7.333 | 8 | 0.148 | 2 | 0.148 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 367.9143
496 | 496 | CL2-110 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.874 | 11 | 0.438 | 2 | 0.438 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 216.6548
497 | 497 | CL2-111 | DONEGAL | DONEGAL | SS-617 | Mulreavy 110kV Substation | EirGrid | 110000 | 33000 | 110000 | 8.807 | 9 | 0.316 | 2 | 0.316 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213 | 4.2 | 342.819
498 | 498 | CL2-112 | LOUTH | LOUTH | SS-651 | Grange 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.124 | 7 | 0.109 | 2 | 0.109 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 450.1833
499 | 499 | CL2-113 | LOUTH | LOUTH | SS-651 | Grange 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.509 | 5 | 0.093 | 2 | 0.093 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 199.9238
500 | 500 | CL2-114 | LOUTH | LOUTH | SS-650 | Ballymascanlan 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.596 | 9 | 0.272 | 2 | 0.272 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 166.4619
501 | 501 | CL2-115 | CORK | CORK | SS-253 | Ballydehob 38kV Substation | ESB Networks | 38000 | 38000 | low | 20.362 | 21 | 0.19 | 2 | 0.19 | 4.2 | 4.2 | 1966840 | 1 | 468295.2381 | 2.1354 | 4.2 | 317.7238
502 | 502 | CL2-116 | CORK | CORK | SS-562 | Bantry 38kV Substation | ESB Networks | 38000 | 38000 | low | 25.701 | 26 | 0.154 | 2 | 0.154 | 4.2 | 4.2 | 2230340 | 1 | 531033.3333 | 1.8831 | 4.2 | 468.2952
503 | 503 | CL2-117 | CORK | CORK | SS-562 | Bantry 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.634 | 16 | 0.15 | 2 | 0.15 | 4.2 | 4.2 | 1703340 | 1 | 405557.1429 | 2.4657 | 4.2 | 531.0333
504 | 504 | CL2-118 | CORK | CORK | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.195 | 11 | 0.12 | 2 | 0.12 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 405.5571
505 | 505 | CL2-119 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.503 | 7 | 0.139 | 2 | 0.139 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 342.819
506 | 506 | CL2-120 | CORK | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.068 | 6 | 0.151 | 2 | 0.151 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 199.9238
507 | 507 | CL2-121 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.211 | 14 | 0.269 | 2 | 0.269 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284 | 4.2 | 183.1929
508 | 508 | CL2-122 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 17.54 | 18 | 0.241 | 2 | 0.241 | 4.2 | 4.2 | 1808740 | 1 | 430652.381 | 2.3221 | 4.2 | 380.4619
509 | 509 | CL2-123 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 17.443 | 18 | 0.348 | 2 | 0.348 | 4.2 | 4.2 | 1808740 | 1 | 430652.381 | 2.3221 | 4.2 | 430.6524
510 | 510 | CL2-124 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.848 | 9 | 0.199 | 2 | 0.199 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 430.6524
511 | 511 | CL2-125 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.643 | 9 | 0.155 | 2 | 0.155 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 317.7238
512 | 512 | CL2-126 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 18.412 | 19 | 0.118 | 2 | 0.118 | 4.2 | 4.2 | 1861440 | 1 | 443200 | 2.2563 | 4.2 | 317.7238
513 | 513 | CL2-127 | KERRY | KERRY | SS-321 | Milltown 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 19.015 | 20 | 0.4 | 2 | 0.4 | 4.2 | 4.2 | 1914140 | 1 | 455747.619 | 2.1942 | 4.2 | 443.2
514 | 514 | CL2-128 | KERRY | KERRY | SS-387 | Coolcorcoran 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.843 | 9 | 0.454 | 2 | 0.454 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 455.7476
515 | 515 | CL2-129 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.158 | 15 | 0.156 | 2 | 0.156 | 4.2 | 4.2 | 1650640 | 1 | 393009.5238 | 2.5445 | 4.2 | 317.7238
516 | 516 | CL2-130 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.708 | 8 | 0.132 | 2 | 0.132 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 393.0095
517 | 517 | CL2-131 | KERRY | KERRY | SS-636 | Garranebane 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.801 | 9 | 0.109 | 2 | 0.109 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 216.6548
518 | 518 | CL2-132 | KERRY | KERRY | SS-321 | Milltown 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 16.282 | 17 | 0.144 | 2 | 0.144 | 4.2 | 4.2 | 1756040 | 1 | 418104.7619 | 2.3917 | 4.2 | 317.7238
519 | 519 | CL2-133 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.432 | 3 | 0.208 | 2 | 0.208 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 418.1048
520 | 520 | CL2-134 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.545 | 2 | 0.093 | 2 | 0.093 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007 | 4.2 | 133
521 | 521 | CL2-135 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.3 | 3 | 0.405 | 2 | 0.405 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 116.269
522 | 522 | CL2-136 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 12.421 | 13 | 0.108 | 2 | 0.108 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718 | 4.2 | 133
523 | 523 | CL2-137 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.419 | 9 | 0.495 | 2 | 0.495 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 367.9143
524 | 524 | CL2-138 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 3.448 | 4 | 0.351 | 2 | 0.351 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 317.7238
525 | 525 | CL2-139 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 3.687 | 4 | 0.42 | 2 | 0.42 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 149.731
526 | 526 | CL2-140 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.867 | 7 | 0.21 | 2 | 0.21 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 149.731
527 | 527 | CL2-141 | KERRY | KERRY | SS-555 | Ballybunion 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.189 | 6 | 0.147 | 2 | 0.147 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 199.9238
528 | 528 | CL2-142 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 20.278 | 21 | 0.33 | 2 | 0.33 | 4.2 | 4.2 | 1966840 | 1 | 468295.2381 | 2.1354 | 4.2 | 183.1929
529 | 529 | CL2-143 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 22.224 | 23 | 0.092 | 2 | 0.092 | 4.2 | 4.2 | 2072240 | 1 | 493390.4762 | 2.0268 | 4.2 | 468.2952
530 | 530 | CL2-144 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.655 | 15 | 0.171 | 2 | 0.171 | 4.2 | 4.2 | 1650640 | 1 | 393009.5238 | 2.5445 | 4.2 | 493.3905
531 | 531 | CL2-145 | CLARE | CLARE | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 18.608 | 19 | 0.312 | 2 | 0.312 | 4.2 | 4.2 | 1861440 | 1 | 443200 | 2.2563 | 4.2 | 393.0095
532 | 532 | CL2-146 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.936 | 11 | 0.172 | 2 | 0.172 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 443.2
533 | 533 | CL2-147 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.888 | 15 | 0.174 | 2 | 0.174 | 4.2 | 4.2 | 1650640 | 1 | 393009.5238 | 2.5445 | 4.2 | 342.819
534 | 534 | CL2-148 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.564 | 12 | 0.433 | 2 | 0.433 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 393.0095
535 | 535 | CL2-149 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.629 | 5 | 0.272 | 2 | 0.272 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 355.3667
536 | 536 | CL2-150 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.222 | 6 | 0.248 | 2 | 0.248 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 166.4619
537 | 537 | CL2-151 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.288 | 9 | 0.207 | 2 | 0.207 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 183.1929
538 | 538 | CL2-152 | MAYO | MAYO | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 18.506 | 19 | 0.212 | 2 | 0.212 | 4.2 | 4.2 | 1861440 | 1 | 443200 | 2.2563 | 4.2 | 317.7238
539 | 539 | CL2-153 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 16.36 | 17 | 0.41 | 2 | 0.41 | 4.2 | 4.2 | 1756040 | 1 | 418104.7619 | 2.3917 | 4.2 | 443.2
540 | 540 | CL2-154 | GALWAY | GALWAY | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 14.183 | 15 | 0.476 | 2 | 0.476 | 4.2 | 4.2 | 1650640 | 1 | 393009.5238 | 2.5445 | 4.2 | 418.1048
541 | 541 | CL2-155 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 16.065 | 17 | 0.117 | 2 | 0.117 | 4.2 | 4.2 | 2312370 | 7 | 550564.2857 | 1.8163 | 4.2 | 393.0095
542 | 542 | CL2-156 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 15.196 | 16 | 0.198 | 2 | 0.198 | 4.2 | 4.2 | 2259670 | 7 | 538016.6667 | 1.8587 | 4.2 | 550.5643
543 | 543 | CL2-157 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.059 | 16 | 0.27 | 2 | 0.27 | 4.2 | 4.2 | 1703340 | 1 | 405557.1429 | 2.4657 | 4.2 | 538.0167
544 | 544 | CL2-158 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.984 | 15 | 0.217 | 2 | 0.217 | 4.2 | 4.2 | 1650640 | 1 | 393009.5238 | 2.5445 | 4.2 | 405.5571
545 | 545 | CL2-159 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.57 | 15 | 0.111 | 2 | 0.111 | 4.2 | 4.2 | 1650640 | 1 | 393009.5238 | 2.5445 | 4.2 | 393.0095
546 | 546 | CL2-160 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.119 | 7 | 0.201 | 2 | 0.201 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 393.0095
547 | 547 | CL2-161 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 18.275 | 19 | 0.094 | 2 | 0.094 | 4.2 | 4.2 | 1861440 | 1 | 443200 | 2.2563 | 4.2 | 199.9238
548 | 548 | CL2-162 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 6.147 | 7 | 0.107 | 2 | 0.107 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525 | 4.2 | 443.2
549 | 549 | CL2-163 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.226 | 10 | 0.353 | 2 | 0.353 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 4.2 | 425.0881
550 | 550 | CL2-164 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.486 | 7 | 0.371 | 2 | 0.371 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 330.2714
551 | 551 | CL2-165 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.285 | 6 | 0.406 | 2 | 0.406 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 199.9238
552 | 552 | CL2-166 | MAYO | MAYO | SS-317 | Newport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 12.325 | 13 | 0.11 | 2 | 0.11 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718 | 4.2 | 183.1929
553 | 553 | CL2-167 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 12.785 | 13 | 0.09 | 2 | 0.09 | 4.2 | 4.2 | 2101570 | 7 | 500373.8095 | 1.9985 | 4.2 | 367.9143
554 | 554 | CL2-168 | MAYO | MAYO | SS-170 | Derrynadivva 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.362 | 5 | 0.33 | 2 | 0.33 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 500.3738
555 | 555 | CL2-169 | MAYO | MAYO | SS-170 | Derrynadivva 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.767 | 4 | 0.391 | 2 | 0.391 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 166.4619
556 | 556 | CL2-170 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.967 | 12 | 0.192 | 2 | 0.192 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 149.731
557 | 557 | CL2-171 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 16.383 | 17 | 0.36 | 2 | 0.36 | 4.2 | 4.2 | 1756040 | 1 | 418104.7619 | 2.3917 | 4.2 | 355.3667
558 | 558 | CL2-172 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 19.204 | 20 | 0.648 | 2 | 0.486 | 4.2 | 4.2 | 1914140 | 1 | 455747.619 | 2.1942 | 4.2 | 418.1048
559 | 559 | CL2-173 | MAYO | MAYO | SS-710 | Tawnaghmore 110kV Substation | EirGrid | 110000 | low | 110000 | 13.533 | 14 | 0.243 | 2 | 0.243 | 4.2 | 4.2 | 2154270 | 7 | 512921.4286 | 1.9496 | 4.2 | 455.7476
560 | 560 | CL2-174 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.677 | 6 | 0.281 | 2 | 0.281 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 512.9214
561 | 561 | CL2-175 | SLIGO | SLIGO | SS-198 | Enniscrone 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 3.204 | 4 | 0.603 | 2 | 0.603 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 183.1929
562 | 562 | CL2-176 | SLIGO | SLIGO | SS-042 | Ballytivnan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 11.373 | 12 | 0.284 | 2 | 0.284 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 149.731
563 | 563 | CL2-177 | SLIGO | SLIGO | SS-042 | Ballytivnan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.941 | 8 | 0.153 | 2 | 0.153 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 355.3667
564 | 564 | CL2-178 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.751 | 7 | 0.344 | 2 | 0.344 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 216.6548
565 | 565 | CL2-179 | DONEGAL | DONEGAL | SS-643 | Donegal 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.074 | 8 | 0.402 | 2 | 0.402 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 199.9238
566 | 566 | CL2-180 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 6.814 | 7 | 0.107 | 2 | 0.107 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 216.6548
567 | 567 | CL2-181 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 5.533 | 6 | 0.332 | 2 | 0.332 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 199.9238
568 | 568 | CL2-182 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 5.79 | 6 | 0.621 | 2 | 0.46575 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 183.1929
569 | 569 | CL2-183 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 12.903 | 13 | 0.638 | 2 | 0.4785 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718 | 4.2 | 183.1929
570 | 570 | CL2-184 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.589 | 9 | 0.301 | 2 | 0.301 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 367.9143
571 | 571 | CL2-185 | DONEGAL | DONEGAL | SS-252 | Killybegs 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.054 | 9 | 0.204 | 2 | 0.204 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 317.7238
572 | 572 | CL2-186 | DONEGAL | DONEGAL | SS-252 | Killybegs 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 5.256 | 6 | 0.121 | 2 | 0.121 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 317.7238
573 | 573 | CL2-187 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 10.587 | 11 | 0.182 | 2 | 0.182 | 4.2 | 4.2 | 1996170 | 7 | 475278.5714 | 2.104 | 4.2 | 183.1929
574 | 574 | CL2-188 | DONEGAL | DONEGAL | SS-686 | Dungloe 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.116 | 8 | 0.098 | 2 | 0.098 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 475.2786
575 | 575 | CL2-189 | DONEGAL | DONEGAL | SS-687 | Gweedore Wind Farm 38kV Substation | ESB Networks | 38000 | low | 38000 | 10.865 | 11 | 0.261 | 2 | 0.261 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 216.6548
576 | 576 | CL2-190 | DONEGAL | DONEGAL | SS-138 | Creeslough 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.187 | 6 | 0.451 | 2 | 0.451 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 342.819
577 | 577 | CL2-191 | DONEGAL | DONEGAL | SS-119 | Drumlough Hill (1) 38kV Substation | ESB Networks | 38000 | low | 38000 | 6.5 | 7 | 0.41 | 2 | 0.41 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 183.1929
578 | 578 | CL2-192 | DONEGAL | DONEGAL | SS-119 | Drumlough Hill (1) 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.362 | 4 | 0.168 | 2 | 0.168 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 199.9238
579 | 579 | CL2-193 | DONEGAL | DONEGAL | SS-125 | Drumlough Hill (2) 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.583 | 2 | 0.16 | 2 | 0.16 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007 | 4.2 | 149.731
580 | 580 | CL2-194 | DONEGAL | DONEGAL | SS-239 | Moville 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.499 | 9 | 0.269 | 2 | 0.269 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 116.269
581 | 581 | CL2-195 | DONEGAL | DONEGAL | SS-272 | Carndonagh 38kV | ESB Networks | 38000 | 38000 | low | 3.406 | 4 | 0.14 | 2 | 0.14 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 317.7238
582 | 582 | CL2-196 | DONEGAL | DONEGAL | SS-689 |  | ESB Networks | 38000 |  |  | 2.678 | 3 | 0.181 | 2 | 0.181 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 149.731
583 | 583 | CL2-197 | DONEGAL | DONEGAL | SS-687 | Gweedore Wind Farm 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.067 | 3 | 0.095 | 2 | 0.095 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 133
584 | 584 | CL2-198 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.348 | 6 | 0.136 | 2 | 0.136 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 133
585 | 585 | CL2-199 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.028 | 11 | 0.43 | 2 | 0.43 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 183.1929
586 | 586 | CL2-200 | CORK | KERRY | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.494 | 11 | 0.132 | 2 | 0.132 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 342.819
587 | 587 | CL2-201 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 18.922 | 19 | 0.366 | 2 | 0.366 | 4.2 | 4.2 | 1861440 | 1 | 443200 | 2.2563 | 4.2 | 342.819
588 | 588 | CL2-202 | LEITRIM | LEITRIM | SS-534 | Garvagh Glebe 110kV Substation Extension | EirGrid | 110000 | 20000 | 110000 | 2.074 | 3 | 0.236 | 2 | 0.236 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674 | 4.2 | 443.2
589 | 589 | CL2-203 | WICKLOW | WICKLOW | SS-222 | Poulaphouca 110kV Substation | EirGrid | 110000 | low | 110000 | 11.628 | 12 | 0.411 | 2 | 0.411 | 4.2 | 4.2 | 2048870 | 7 | 487826.1905 | 2.0499 | 4.2 | 374.8976
590 | 590 | CL2-204 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.271 | 9 | 0.128 | 2 | 0.128 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 487.8262
591 | 591 | CL2-205 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.191 | 11 | 0.395 | 2 | 0.395 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 317.7238
592 | 592 | CL2-206 | WICKLOW | WICKLOW | SS-062 | Stratford 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 7.029 | 8 | 0.315 | 2 | 0.315 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285 | 4.2 | 342.819
593 | 593 | CL2-207 | WICKLOW | WICKLOW | SS-209 | Blessington 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.407 | 7 | 0.414 | 2 | 0.414 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 437.6357
594 | 594 | CL2-208 | WICKLOW | WICKLOW | SS-209 | Blessington 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.957 | 5 | 0.128 | 2 | 0.128 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 199.9238
595 | 595 | CL2-209 | WICKLOW | WICKLOW | SS-209 | Blessington 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.185 | 12 | 0.213 | 2 | 0.213 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 166.4619
596 | 596 | CL2-210 | WICKLOW | WICKLOW | SS-570 | Kilcoole 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.539 | 12 | 0.094 | 2 | 0.094 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 355.3667
597 | 597 | CL2-211 | DUBLIN | DUBLIN | SS-091 | Whitestown 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.173 | 7 | 0.101 | 2 | 0.101 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 355.3667
598 | 598 | CL2-212 | WICKLOW | WICKLOW | SS-699 | Ballycumber 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.313 | 2 | 0.407 | 2 | 0.407 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007 | 4.2 | 199.9238
599 | 599 | CL2-213 | WICKLOW | WICKLOW | SS-699 | Ballycumber 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.392 | 3 | 0.143 | 2 | 0.143 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 116.269
600 | 600 | CL2-214 | KERRY | KERRY | SS-637 | Kilgarvan 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.281 | 5 | 0.265 | 2 | 0.265 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 133
601 | 601 | CL2-215 | CORK | CORK | SS-668 | Coomataggart 110 kV Substation | EirGrid | 110000 | low | 110000 | 1.6 | 2 | 0.187 | 2 | 0.187 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341 | 4.2 | 166.4619
602 | 602 | CL2-216 | CORK | CORK | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 7.879 | 8 | 0.091 | 2 | 0.091 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 319.0667
603 | 603 | CL2-217 | CORK | CORK | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 7.009 | 8 | 0.105 | 2 | 0.105 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 216.6548
604 | 604 | CL2-218 | CORK | CORK | SS-161 | Gneeves 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.873 | 5 | 0.35 | 2 | 0.35 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 216.6548
605 | 605 | CL2-219 | CORK | CORK | SS-161 | Gneeves 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.263 | 3 | 0.247 | 2 | 0.247 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 166.4619
606 | 606 | CL2-220 | CORK | CORK | SS-161 | Gneeves 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.572 | 4 | 0.136 | 2 | 0.136 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 133
607 | 607 | CL2-221 | CORK | CORK | SS-161 | Gneeves 38kV Substation | ESB Networks | 38000 | low | 38000 | 6.496 | 7 | 0.311 | 2 | 0.311 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 149.731
608 | 608 | CL2-222 | CORK | CORK | SS-096 | Boggeragh 110kV Substation | EirGrid | 110000 |  |  | 1.741 | 2 | 0.601 | 2 | 0.601 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341 | 4.2 | 199.9238
609 | 609 | CL2-223 | WATERFORD | WATERFORD | SS-532 | Woodhouse 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 1.491 | 2 | 0.586 | 2 | 0.586 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341 | 4.2 | 319.0667
610 | 610 | CL2-224 | KILKENNY | KILKENNY | SS-495 | New Ross (West) 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.894 | 10 | 0.121 | 2 | 0.121 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 4.2 | 319.0667
611 | 611 | CL2-225 | LIMERICK | LIMERICK | SS-069 | Garryspillane 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.414 | 5 | 0.324 | 2 | 0.324 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 330.2714
612 | 612 | CL2-226 | LIMERICK | LIMERICK | SS-069 | Garryspillane 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.875 | 4 | 0.382 | 2 | 0.382 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 166.4619
613 | 613 | CL2-227 | TIPPERARY | TIPPERARY | SS-645 | Toomevara 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.683 | 8 | 0.128 | 2 | 0.128 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 149.731
614 | 614 | CL2-228 | TIPPERARY | TIPPERARY | SS-645 | Toomevara 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.306 | 7 | 0.431 | 2 | 0.431 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 216.6548
615 | 615 | CL2-229 | TIPPERARY | TIPPERARY | SS-540 | Templemore 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.271 | 9 | 0.236 | 2 | 0.236 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 199.9238
616 | 616 | CL2-230 | DONEGAL | DONEGAL | SS-686 | Dungloe 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.555 | 6 | 0.403 | 2 | 0.403 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 317.7238
617 | 617 | CL2-231 | DONEGAL | DONEGAL | SS-686 | Dungloe 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.384 | 13 | 0.193 | 2 | 0.193 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718 | 4.2 | 183.1929
618 | 618 | CL2-232 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 11.409 | 12 | 0.513 | 2 | 0.513 | 4.2 | 4.2 | 2048870 | 7 | 487826.1905 | 2.0499 | 4.2 | 367.9143
619 | 619 | CL2-233 | LEITRIM | LEITRIM | SS-097 | Corderry 110kV Substation | EirGrid | 110000 |  |  | 8.369 | 9 | 0.104 | 2 | 0.104 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213 | 4.2 | 487.8262
620 | 620 | CL2-234 | MAYO | MAYO | SS-234 | Crossmolina 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.452 | 10 | 0.149 | 2 | 0.149 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 4.2 | 450.1833
621 | 621 | CL2-235 | MAYO | MAYO | SS-234 | Crossmolina 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.266 | 9 | 0.167 | 2 | 0.167 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 330.2714
622 | 622 | CL2-236 | DONEGAL | DONEGAL | SS-698 | Binbane 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.433 | 2 | 0.288 | 2 | 0.288 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007 | 4.2 | 317.7238
623 | 623 | CL2-237 | DONEGAL | DONEGAL | SS-102 | Binbane 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 4.317 | 5 | 0.091 | 2 | 0.091 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5 | 4.2 | 116.269
624 | 624 | CL2-238 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 2.458 | 3 | 0.1 | 2 | 0.1 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674 | 4.2 | 399.9929
625 | 625 | CL2-239 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 1.606 | 2 | 0.188 | 2 | 0.188 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341 | 4.2 | 374.8976
626 | 626 | CL2-240 | WATERFORD | WATERFORD | SS-354 | Twomilebridge 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.166 | 6 | 0.155 | 2 | 0.155 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 319.0667
627 | 627 | CL2-241 | WATERFORD | WATERFORD | SS-205 | Dungarvan 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 10.171 | 11 | 0.329 | 2 | 0.329 | 4.2 | 4.2 | 1996170 | 7 | 475278.5714 | 2.104 | 4.2 | 183.1929
628 | 628 | CL2-242 | CORK | CORK | SS-695 | Castlepook 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 4.594 | 5 | 0.316 | 2 | 0.316 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 475.2786
629 | 629 | CL2-243 | CORK | CORK | SS-695 | Castlepook 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 5.101 | 6 | 0.189 | 2 | 0.189 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 166.4619
630 | 630 | CL2-244 | LIMERICK | LIMERICK | SS-256 | Mitchelstown West 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.474 | 8 | 0.213 | 2 | 0.213 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 183.1929
631 | 631 | CL2-245 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.582 | 14 | 0.11 | 2 | 0.11 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284 | 4.2 | 216.6548
632 | 632 | CL2-246 | WATERFORD | WATERFORD | SS-016 | Portlaw 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.653 | 3 | 0.464 | 2 | 0.464 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 380.4619
633 | 633 | CL2-247 | TIPPERARY | TIPPERARY | SS-692 | Hollyford 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.199 | 3 | 0.476 | 2 | 0.476 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 133
634 | 634 | CL2-248 | CARLOW | CARLOW | SS-368 | Gortahile 38kV Substation | ESB Networks | 38000 | low | 38000 | 9.017 | 10 | 0.378 | 2 | 0.378 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 4.2 | 133
635 | 635 | CL2-249 | OFFALY | OFFALY | SS-084 | Birr 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.639 | 12 | 0.154 | 2 | 0.154 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 330.2714
636 | 636 | CL2-250 | CORK | CORK | SS-668 | Coomataggart 110 kV Substation | EirGrid | 110000 | low | 110000 | 8.509 | 9 | 0.225 | 2 | 0.225 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213 | 4.2 | 355.3667
637 | 637 | CL2-251 | LIMERICK | LIMERICK | SS-069 | Garryspillane 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.348 | 9 | 0.211 | 2 | 0.211 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 450.1833
638 | 638 | CL2-252 | LIMERICK | LIMERICK | SS-695 | Castlepook 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 8.884 | 9 | 0.347 | 2 | 0.347 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 317.7238
639 | 639 | CL2-253 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.565 | 9 | 0.201 | 2 | 0.201 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 317.7238
640 | 640 | CL2-254 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.54 | 9 | 0.099 | 2 | 0.099 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 317.7238
641 | 641 | CL2-255 | CORK | CORK | SS-197 | Midleton 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 7.187 | 8 | 0.104 | 2 | 0.104 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285 | 4.2 | 317.7238
642 | 642 | CL2-256 | WATERFORD | WATERFORD | SS-622 | Barranafaddock 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.004 | 5 | 0.105 | 2 | 0.105 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 437.6357
643 | 643 | CL2-257 | KILKENNY | KILKENNY | SS-489 | Ballyhale 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.903 | 3 | 0.09 | 2 | 0.09 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 166.4619
644 | 644 | CL2-258 | WICKLOW | WICKLOW | SS-591 | Shillelagh 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.038 | 7 | 0.227 | 2 | 0.227 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 133
645 | 645 | CL2-259 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.431 | 5 | 0.123 | 2 | 0.123 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 199.9238
646 | 646 | CL2-260 | CORK | CORK | SS-406 | Kanturk 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.163 | 7 | 0.146 | 2 | 0.146 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 166.4619
647 | 647 | CL2-261 | LAOIS | LAOIS | SS-486 | Castlecomer 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.156 | 13 | 0.326 | 2 | 0.326 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718 | 4.2 | 199.9238
648 | 648 | CL2-262 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 13.313 | 14 | 0.094 | 2 | 0.094 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284 | 4.2 | 367.9143
649 | 649 | CL2-263 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 14.175 | 15 | 0.227 | 2 | 0.227 | 4.2 | 4.2 | 1650640 | 1 | 393009.5238 | 2.5445 | 4.2 | 380.4619
650 | 650 | CL2-264 | TIPPERARY | TIPPERARY | SS-347 | Glengoole 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.388 | 6 | 0.124 | 2 | 0.124 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 393.0095
651 | 651 | CL2-265 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.166 | 8 | 0.387 | 2 | 0.387 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 183.1929
652 | 652 | CL2-266 | TIPPERARY | TIPPERARY | SS-585 | Kilross Road 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.344 | 6 | 0.287 | 2 | 0.287 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 216.6548
653 | 653 | CL2-267 | WEXFORD | WEXFORD | SS-033 | Ballywater 110kV Substation | EirGrid | 110000 | low | 110000 | 3.45 | 4 | 0.421 | 2 | 0.421 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581 | 4.2 | 183.1929
654 | 654 | CL2-268 | DONEGAL | DONEGAL | SS-610 | Milford (North) 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.511 | 8 | 0.203 | 2 | 0.203 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 387.4452
655 | 655 | CL2-269 | DONEGAL | DONEGAL | SS-610 | Milford (North) 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.345 | 7 | 0.198 | 2 | 0.198 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 216.6548
656 | 656 | CL2-270 | DONEGAL | DONEGAL | SS-610 | Milford (North) 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.562 | 8 | 0.494 | 2 | 0.494 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 199.9238
657 | 657 | CL2-271 | DONEGAL | DONEGAL | SS-138 | Creeslough 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.954 | 7 | 0.176 | 2 | 0.176 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 216.6548
658 | 658 | CL2-272 | GALWAY | GALWAY | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 10.861 | 11 | 0.265 | 2 | 0.265 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 199.9238
659 | 659 | CL2-273 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 24.442 | 25 | 0.246 | 2 | 0.246 | 4.2 | 4.2 | 2733970 | 7 | 650945.2381 | 1.5362 | 4.2 | 342.819
660 | 660 | CL2-274 | SLIGO | SLIGO | SS-206 | Boyle 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 10.978 | 11 | 0.175 | 2 | 0.175 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 650.9452
661 | 661 | CL2-275 | MAYO | MAYO | SS-203 | Foxford 38kV Substation | ESB Networks | 38000 |  |  | 7.233 | 8 | 0.185 | 2 | 0.185 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 342.819
662 | 662 | CL2-276 | ROSCOMMON | SLIGO | SS-206 | Boyle 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 5.549 | 6 | 0.167 | 2 | 0.167 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 216.6548
663 | 663 | CL2-277 | GALWAY | GALWAY | SS-598 | Glennamaddy 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.923 | 5 | 0.545 | 2 | 0.545 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 183.1929
664 | 664 | CL2-278 | MAYO | MAYO | SS-203 | Foxford 38kV Substation | ESB Networks | 38000 |  |  | 4.731 | 5 | 0.215 | 2 | 0.215 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 166.4619
665 | 665 | CL2-279 | WESTMEATH | WESTMEATH | SS-246 | Loughanalla 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 5.824 | 6 | 0.202 | 2 | 0.202 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 166.4619
666 | 666 | CL2-280 | WESTMEATH | WESTMEATH | SS-517 | Delvin 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.091 | 4 | 0.612 | 2 | 0.459 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 183.1929
667 | 667 | CL2-281 | MEATH | MEATH | SS-388 | Oldcastle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.07 | 5 | 0.284 | 2 | 0.284 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 149.731
668 | 668 | CL2-282 | GALWAY | GALWAY | SS-109 | Cloon 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.626 | 9 | 0.457 | 2 | 0.457 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213 | 4.2 | 166.4619
669 | 669 | CL2-283 | MAYO | MAYO | SS-640 | Ballinrobe 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.053 | 5 | 0.119 | 2 | 0.119 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 450.1833
670 | 670 | CL2-284 | DONEGAL | DONEGAL | SS-117 | Crockahenny 38kV Substation | ESB Networks | 38000 | low | 38000 | 5.614 | 6 | 0.14 | 2 | 0.14 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 166.4619
671 | 671 | CL2-285 | DONEGAL | DONEGAL | SS-239 | Moville 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.258 | 5 | 0.315 | 2 | 0.315 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 183.1929
672 | 672 | CL2-286 | DONEGAL | DONEGAL | SS-117 | Crockahenny 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.215 | 4 | 7.249 | 2 | 5.4367 | 67.2 | 67.2 | 1761700 | 11 | 26215.7738 | 38.145 | 4.2 | 166.4619
673 | 673 | CL2-287 | DONEGAL | DONEGAL | SS-690 | Stranrolar 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.433 | 8 | 1.678 | 2 | 1.2585 | 12.6 | 12.6 | 909950 | 4 | 72218.254 | 13.8469 | 67.2 | 26.2158
674 | 674 | CL2-288 | DONEGAL | DONEGAL | SS-083 | Golagh 110kV Substation | EirGrid | 110000 | 38000 | 110000 | 4.239 | 5 | 8.595 | 2 | 6.4463 | 79.8 | 79.8 | 1972510 | 11 | 24718.1704 | 40.4561 | 12.6 | 72.2183
675 | 675 | CL2-289 | DONEGAL | DONEGAL | SS-690 | Stranrolar 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.111 | 8 | 0.832 | 2 | 0.624 | 8.4 | 8.4 | 909950 | 4 | 108327.381 | 9.2313 | 79.8 | 24.7182
676 | 676 | CL2-290 | DONEGAL | DONEGAL | SS-617 | Mulreavy 110kV Substation | EirGrid | 110000 | 33000 | 110000 | 6.22 | 7 | 3.117 | 2 | 2.3377 | 25.2 | 25.2 | 2575660 | 9 | 102208.7302 | 9.7839 | 8.4 | 108.3274
677 | 677 | CL2-291 | DONEGAL | DONEGAL | SS-617 | Mulreavy 110kV Substation | EirGrid | 110000 | 33000 | 110000 | 11.976 | 12 | 2.83 | 2 | 2.1225 | 25.2 | 25.2 | 3019810 | 9 | 119833.7302 | 8.3449 | 25.2 | 102.2087
678 | 678 | CL2-292 | DONEGAL | DONEGAL | SS-617 | Mulreavy 110kV Substation | EirGrid | 110000 | 33000 | 110000 | 8.888 | 9 | 12.212 | 2 | 9.159 | 113.4 | 113.4 | 2815750 | 11 | 24830.2469 | 40.2735 | 25.2 | 119.8337
679 | 679 | CL2-293 | DONEGAL | DONEGAL | SS-617 | Mulreavy 110kV Substation | EirGrid | 110000 | 33000 | 110000 | 3.834 | 4 | 12.925 | 2 | 9.6938 | 117.6 | 117.6 | 1761700 | 11 | 14980.4422 | 66.7537 | 113.4 | 24.8302
680 | 680 | CL2-294 | DONEGAL | DONEGAL | SS-083 | Golagh 110kV Substation | EirGrid | 110000 | 38000 | 110000 | 11.56 | 12 | 9.009 | 2 | 6.7568 | 84 | 84 | 3448180 | 11 | 41049.7619 | 24.3607 | 117.6 | 14.9804
681 | 681 | CL2-295 | DONEGAL | DONEGAL | SS-087 | Cliff 110kV Substation | EirGrid | 110000 | low | 110000 | 10.692 | 11 | 3.2 | 2 | 2.4 | 29.4 | 29.4 | 2930980 | 9 | 99693.1973 | 10.0308 | 84 | 41.0498
682 | 682 | CL2-296 | DONEGAL | DONEGAL | SS-083 | Golagh 110kV Substation | EirGrid | 110000 | 38000 | 110000 | 15.523 | 16 | 0.849 | 2 | 0.63675 | 8.4 | 8.4 | 2259670 | 7 | 269008.3333 | 3.7174 | 29.4 | 99.6932
683 | 683 | CL2-297 | DONEGAL | DONEGAL | SS-087 | Cliff 110kV Substation | EirGrid | 110000 | low | 110000 | 4.515 | 5 | 1.499 | 2 | 1.1242 | 12.6 | 12.6 | 1679970 | 7 | 133330.9524 | 7.5001 | 8.4 | 269.0083
684 | 684 | CL2-298 | DONEGAL | DONEGAL | SS-087 | Cliff 110kV Substation | EirGrid | 110000 | low | 110000 | 5.378 | 6 | 1.796 | 2 | 1.347 | 12.6 | 12.6 | 1732670 | 7 | 137513.4921 | 7.272 | 12.6 | 133.331
685 | 685 | CL2-299 | DONEGAL | DONEGAL | SS-617 | Mulreavy 110kV Substation | EirGrid | 110000 | 33000 | 110000 | 1.486 | 2 | 1.813 | 2 | 1.3598 | 16.8 | 16.8 | 1340080 | 11 | 79766.6667 | 12.5366 | 12.6 | 137.5135
686 | 686 | CL2-300 | CAVAN | CAVAN | SS-110 | Corraclassy 110kV Substation | EirGrid | 110000 |  |  | 15.501 | 16 | 0.978 | 2 | 0.7335 | 8.4 | 8.4 | 2259670 | 7 | 269008.3333 | 3.7174 | 16.8 | 79.7667
687 | 687 | CL2-301 | CAVAN | CAVAN | SS-110 | Corraclassy 110kV Substation | EirGrid | 110000 |  |  | 9.916 | 10 | 4.855 | 2 | 3.6413 | 42 | 42 | 3066450 | 10 | 73010.7143 | 13.6966 | 8.4 | 269.0083
688 | 688 | CL2-302 | CAVAN | CAVAN | SS-110 | Corraclassy 110kV Substation | EirGrid | 110000 |  |  | 5.003 | 6 | 6.143 | 2 | 4.6072 | 54.6 | 54.6 | 2183320 | 11 | 39987.5458 | 25.0078 | 42 | 73.0107
689 | 689 | CL2-303 | CAVAN | MEATH | SS-111 | Gortawee 110kV Station | EirGrid | 110000 | 110000 | low | 4.966 | 5 | 5.016 | 2 | 3.762 | 46.2 | 46.2 | 1972510 | 11 | 42695.0216 | 23.4219 | 54.6 | 39.9875
690 | 690 | CL2-304 | LOUTH | LOUTH | SS-650 | Ballymascanlan 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.2 | 6 | 0.96 | 2 | 0.72 | 8.4 | 8.4 | 769410 | 4 | 91596.4286 | 10.9175 | 46.2 | 42.695
691 | 691 | CL2-305 | LOUTH | LOUTH | SS-650 | Ballymascanlan 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.84 | 6 | 0.534 | 2 | 0.534 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 8.4 | 91.5964
692 | 692 | CL2-306 | LOUTH | LOUTH | SS-650 | Ballymascanlan 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.469 | 5 | 4.021 | 2 | 3.0157 | 33.6 | 33.6 | 904090 | 6 | 26907.4405 | 37.1644 | 4.2 | 183.1929
693 | 693 | CL2-307 | LOUTH | LOUTH | SS-650 | Ballymascanlan 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.443 | 9 | 0.963 | 2 | 0.72225 | 8.4 | 8.4 | 1379800 | 2 | 164261.9048 | 6.0878 | 33.6 | 26.9074
694 | 694 | CL2-308 | WEXFORD | WEXFORD | SS-314 | Richfield 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.174 | 4 | 0.844 | 2 | 0.633 | 8.4 | 8.4 | 628870 | 4 | 74865.4762 | 13.3573 | 8.4 | 164.2619
695 | 695 | CL2-309 | CORK | CORK | SS-253 | Ballydehob 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.485 | 12 | 0.605 | 2 | 0.605 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 8.4 | 74.8655
696 | 696 | CL2-310 | CORK | CORK | SS-254 | Glanta Commons 38kV Station | ESB Networks | 38000 |  |  | 5.551 | 6 | 0.625 | 2 | 0.46875 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 355.3667
697 | 697 | CL2-311 | CORK | CORK | SS-254 | Glanta Commons 38kV Station | ESB Networks | 38000 |  |  | 2.882 | 3 | 0.69 | 2 | 0.5175 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 183.1929
698 | 698 | CL2-312 | CORK | CORK | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.833 | 6 | 1.042 | 2 | 0.7815 | 8.4 | 8.4 | 769410 | 4 | 91596.4286 | 10.9175 | 4.2 | 133
699 | 699 | CL2-313 | CORK | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.385 | 12 | 9.018 | 2 | 6.7635 | 84 | 84 | 3448180 | 11 | 41049.7619 | 24.3607 | 8.4 | 91.5964
700 | 700 | CL2-314 | CORK | CORK | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 13.904 | 14 | 2.259 | 2 | 1.6942 | 21 | 21 | 1331570 | 4 | 63408.0952 | 15.7709 | 84 | 41.0498
701 | 701 | CL2-315 | KERRY | KERRY | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 14.198 | 15 | 1.14 | 2 | 0.855 | 8.4 | 8.4 | 1696000 | 2 | 201904.7619 | 4.9528 | 21 | 63.4081
702 | 702 | CL2-316 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 13.903 | 14 | 1.794 | 2 | 1.3455 | 12.6 | 12.6 | 1680350 | 3 | 133361.1111 | 7.4984 | 8.4 | 201.9048
703 | 703 | CL2-317 | CORK | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.126 | 9 | 7.779 | 2 | 5.8342 | 71.4 | 71.4 | 2815750 | 11 | 39436.2745 | 25.3574 | 12.6 | 133.3611
704 | 704 | CL2-318 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.671 | 11 | 0.831 | 2 | 0.62325 | 8.4 | 8.4 | 1485200 | 2 | 176809.5238 | 5.6558 | 71.4 | 39.4363
705 | 705 | CL2-319 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.388 | 11 | 0.743 | 2 | 0.55725 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 8.4 | 176.8095
706 | 706 | CL2-320 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.47 | 9 | 0.881 | 2 | 0.66075 | 8.4 | 8.4 | 1379800 | 2 | 164261.9048 | 6.0878 | 4.2 | 342.819
707 | 707 | CL2-321 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.847 | 11 | 0.653 | 2 | 0.48975 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 8.4 | 164.2619
708 | 708 | CL2-322 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.551 | 11 | 3.338 | 2 | 2.5035 | 29.4 | 29.4 | 1324920 | 5 | 45065.3061 | 22.19 | 4.2 | 342.819
709 | 709 | CL2-323 | CORK | KERRY | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 3.988 | 4 | 5.645 | 2 | 4.2337 | 50.4 | 50.4 | 1761700 | 11 | 34954.3651 | 28.6087 | 29.4 | 45.0653
710 | 710 | CL2-324 | CORK | KERRY | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.151 | 7 | 4.207 | 2 | 3.1552 | 37.8 | 37.8 | 1126610 | 6 | 29804.4974 | 33.552 | 50.4 | 34.9544
711 | 711 | CL2-325 | CORK | KERRY | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.789 | 10 | 2.449 | 2 | 1.8367 | 21 | 21 | 1050490 | 4 | 50023.3333 | 19.9907 | 37.8 | 29.8045
712 | 712 | CL2-326 | KERRY | KERRY | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.716 | 10 | 1.335 | 2 | 1.0012 | 8.4 | 8.4 | 1432500 | 2 | 170535.7143 | 5.8639 | 21 | 50.0233
713 | 713 | CL2-327 | KERRY | KERRY | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.683 | 10 | 0.46 | 2 | 0.46 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 8.4 | 170.5357
714 | 714 | CL2-328 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 17.138 | 18 | 2.312 | 2 | 1.734 | 21 | 21 | 1612650 | 4 | 76792.8571 | 13.022 | 4.2 | 330.2714
715 | 715 | CL2-329 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 15.665 | 16 | 0.252 | 2 | 0.252 | 4.2 | 4.2 | 1703340 | 1 | 405557.1429 | 2.4657 | 21 | 76.7929
716 | 716 | CL2-330 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 15.771 | 16 | 0.451 | 2 | 0.451 | 4.2 | 4.2 | 1703340 | 1 | 405557.1429 | 2.4657 | 4.2 | 405.5571
717 | 717 | CL2-331 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 15.333 | 16 | 1.488 | 2 | 1.116 | 12.6 | 12.6 | 1785750 | 3 | 141726.1905 | 7.0559 | 4.2 | 405.5571
718 | 718 | CL2-332 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 14.295 | 15 | 2.288 | 2 | 1.716 | 21 | 21 | 1401840 | 4 | 66754.2857 | 14.9803 | 12.6 | 141.7262
719 | 719 | CL2-333 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 12.313 | 13 | 3.128 | 2 | 2.346 | 25.2 | 25.2 | 1502580 | 5 | 59626.1905 | 16.7712 | 21 | 66.7543
720 | 720 | CL2-334 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 11.695 | 12 | 12.491 | 2 | 9.3682 | 113.4 | 113.4 | 3448180 | 11 | 30407.231 | 32.8869 | 25.2 | 59.6262
721 | 721 | CL2-335 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 15.603 | 16 | 12.868 | 2 | 9.651 | 117.6 | 117.6 | 4291420 | 11 | 36491.6667 | 27.4035 | 113.4 | 30.4072
722 | 722 | CL2-336 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 12.315 | 13 | 0.405 | 2 | 0.405 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718 | 117.6 | 36.4917
723 | 723 | CL2-337 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.756 | 11 | 2.849 | 2 | 2.1368 | 25.2 | 25.2 | 1324920 | 5 | 52576.1905 | 19.02 | 4.2 | 367.9143
724 | 724 | CL2-338 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 17.133 | 18 | 1.444 | 2 | 1.083 | 12.6 | 12.6 | 1891150 | 3 | 150091.2698 | 6.6626 | 25.2 | 52.5762
725 | 725 | CL2-339 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.416 | 12 | 3.178 | 2 | 2.3835 | 29.4 | 29.4 | 1413750 | 5 | 48086.7347 | 20.7958 | 12.6 | 150.0913
726 | 726 | CL2-340 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 16.462 | 17 | 0.493 | 2 | 0.493 | 4.2 | 4.2 | 1756040 | 1 | 418104.7619 | 2.3917 | 29.4 | 48.0867
727 | 727 | CL2-341 | KERRY | KERRY | SS-321 | Milltown 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 15.486 | 16 | 3.494 | 2 | 2.6205 | 29.4 | 29.4 | 1769070 | 5 | 60172.449 | 16.6189 | 4.2 | 418.1048
728 | 728 | CL2-342 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 18.593 | 19 | 1 | 2 | 0.75 | 8.4 | 8.4 | 1906800 | 2 | 227000 | 4.4053 | 29.4 | 60.1724
729 | 729 | CL2-343 | KERRY | KERRY | SS-157 | Oughtragh 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 13.653 | 14 | 5.252 | 2 | 3.939 | 46.2 | 46.2 | 3869800 | 11 | 83761.9048 | 11.9386 | 8.4 | 227
730 | 730 | CL2-344 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.314 | 14 | 5.042 | 2 | 3.7815 | 46.2 | 46.2 | 3869800 | 11 | 83761.9048 | 11.9386 | 46.2 | 83.7619
731 | 731 | CL2-345 | KERRY | KERRY | SS-637 | Kilgarvan 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.353 | 5 | 1.31 | 2 | 0.9825 | 8.4 | 8.4 | 699140 | 4 | 83230.9524 | 12.0148 | 46.2 | 83.7619
732 | 732 | CL2-346 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.799 | 6 | 4.905 | 2 | 3.6787 | 42 | 42 | 1015350 | 6 | 24175 | 41.365 | 8.4 | 83.231
733 | 733 | CL2-347 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.137 | 7 | 0.445 | 2 | 0.445 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 42 | 24.175
734 | 734 | CL2-348 | KERRY | KERRY | SS-637 | Kilgarvan 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.611 | 7 | 22.834 | 2 | 17.1255 | 210 | 210 | 7158040 | 12 | 34085.9048 | 29.3376 | 4.2 | 199.9238
735 | 735 | CL2-349 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.422 | 6 | 1.176 | 2 | 0.882 | 8.4 | 8.4 | 769410 | 4 | 91596.4286 | 10.9175 | 210 | 34.0859
736 | 736 | CL2-350 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.583 | 16 | 2.727 | 2 | 2.0452 | 25.2 | 25.2 | 1769070 | 5 | 70201.1905 | 14.2448 | 8.4 | 91.5964
737 | 737 | CL2-351 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 7.63 | 8 | 0.527 | 2 | 0.527 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 25.2 | 70.2012
738 | 738 | CL2-352 | KERRY | KERRY | SS-636 | Garranebane 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.985 | 7 | 0.45 | 2 | 0.45 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 216.6548
739 | 739 | CL2-353 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 9.092 | 10 | 1.297 | 2 | 0.97275 | 8.4 | 8.4 | 1432500 | 2 | 170535.7143 | 5.8639 | 4.2 | 199.9238
740 | 740 | CL2-354 | KERRY | KERRY | SS-636 | Garranebane 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.516 | 6 | 0.977 | 2 | 0.73275 | 8.4 | 8.4 | 769410 | 4 | 91596.4286 | 10.9175 | 8.4 | 170.5357
741 | 741 | CL2-355 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 9.204 | 10 | 4.029 | 2 | 3.0217 | 33.6 | 33.6 | 1460390 | 6 | 43463.9881 | 23.0076 | 8.4 | 91.5964
742 | 742 | CL2-356 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 15.202 | 16 | 2.145 | 2 | 1.6088 | 16.8 | 16.8 | 1472110 | 4 | 87625.5952 | 11.4122 | 33.6 | 43.464
743 | 743 | CL2-357 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 12.386 | 13 | 5.754 | 2 | 4.3155 | 50.4 | 50.4 | 3658990 | 11 | 72599.0079 | 13.7743 | 16.8 | 87.6256
744 | 744 | CL2-358 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 8.772 | 9 | 1.86 | 2 | 1.395 | 16.8 | 16.8 | 980220 | 4 | 58346.4286 | 17.139 | 50.4 | 72.599
745 | 745 | CL2-359 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.2 | 5 | 4.781 | 2 | 3.5857 | 42 | 42 | 904090 | 6 | 21525.9524 | 46.4556 | 16.8 | 58.3464
746 | 746 | CL2-360 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 6.55 | 7 | 1.419 | 2 | 1.0642 | 12.6 | 12.6 | 839680 | 4 | 66641.2698 | 15.0057 | 42 | 21.526
747 | 747 | CL2-361 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 9.046 | 10 | 2.388 | 2 | 1.791 | 21 | 21 | 1050490 | 4 | 50023.3333 | 19.9907 | 12.6 | 66.6413
748 | 748 | CL2-362 | KERRY | KERRY | SS-321 | Milltown 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 14.441 | 15 | 3.954 | 2 | 2.9655 | 33.6 | 33.6 | 2016690 | 6 | 60020.5357 | 16.661 | 21 | 50.0233
749 | 749 | CL2-363 | CORK | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.893 | 7 | 26.94 | 2 | 20.205 | 247.8 | 247.8 | 7158040 | 12 | 28886.36 | 34.6184 | 33.6 | 60.0205
750 | 750 | CL2-364 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.684 | 12 | 3.695 | 2 | 2.7712 | 33.6 | 33.6 | 1682910 | 6 | 50086.6071 | 19.9654 | 247.8 | 28.8864
751 | 751 | CL2-365 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.048 | 10 | 3.714 | 2 | 2.7855 | 33.6 | 33.6 | 1460390 | 6 | 43463.9881 | 23.0076 | 33.6 | 50.0866
752 | 752 | CL2-366 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.115 | 6 | 1.496 | 2 | 1.122 | 12.6 | 12.6 | 769410 | 4 | 61064.2857 | 16.3762 | 33.6 | 43.464
753 | 753 | CL2-367 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 2.639 | 3 | 1.152 | 2 | 0.864 | 8.4 | 8.4 | 558600 | 4 | 66500 | 15.0376 | 12.6 | 61.0643
754 | 754 | CL2-368 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.933 | 5 | 0.755 | 2 | 0.56625 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 8.4 | 66.5
755 | 755 | CL2-369 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.296 | 8 | 1.256 | 2 | 0.942 | 8.4 | 8.4 | 909950 | 4 | 108327.381 | 9.2313 | 4.2 | 166.4619
756 | 756 | CL2-370 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.988 | 10 | 1.839 | 2 | 1.3792 | 16.8 | 16.8 | 1050490 | 4 | 62529.1667 | 15.9925 | 8.4 | 108.3274
757 | 757 | CL2-371 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.22 | 10 | 0.981 | 2 | 0.73575 | 8.4 | 8.4 | 1432500 | 2 | 170535.7143 | 5.8639 | 16.8 | 62.5292
758 | 758 | CL2-372 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.912 | 5 | 5.159 | 2 | 3.8693 | 46.2 | 46.2 | 1972510 | 11 | 42695.0216 | 23.4219 | 8.4 | 170.5357
759 | 759 | CL2-373 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 2.385 | 3 | 0.672 | 2 | 0.504 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 46.2 | 42.695
760 | 760 | CL2-374 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.86 | 10 | 12.005 | 2 | 9.0038 | 109.2 | 109.2 | 3026560 | 11 | 27715.7509 | 36.0806 | 4.2 | 133
761 | 761 | CL2-375 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.104 | 10 | 2.273 | 2 | 1.7048 | 21 | 21 | 1050490 | 4 | 50023.3333 | 19.9907 | 109.2 | 27.7158
762 | 762 | CL2-376 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.168 | 6 | 0.348 | 2 | 0.348 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 21 | 50.0233
763 | 763 | CL2-377 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.606 | 11 | 0.39 | 2 | 0.39 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 183.1929
764 | 764 | CL2-378 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.385 | 9 | 16.042 | 2 | 12.0315 | 147 | 147 | 4339180 | 12 | 29518.2313 | 33.8774 | 4.2 | 342.819
765 | 765 | CL2-379 | KERRY | KERRY | SS-667 | Ballyrickard 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 9.573 | 10 | 0.937 | 2 | 0.70275 | 8.4 | 8.4 | 1432500 | 2 | 170535.7143 | 5.8639 | 147 | 29.5182
766 | 766 | CL2-380 | KERRY | KERRY | SS-667 | Ballyrickard 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.925 | 8 | 0.769 | 2 | 0.57675 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 8.4 | 170.5357
767 | 767 | CL2-381 | KERRY | KERRY | SS-140 | Ballyard 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 6.463 | 7 | 2.428 | 2 | 1.821 | 21 | 21 | 839680 | 4 | 39984.7619 | 25.0095 | 4.2 | 216.6548
768 | 768 | CL2-382 | KERRY | KERRY | SS-140 | Ballyard 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 4.535 | 5 | 2.451 | 2 | 1.8382 | 21 | 21 | 699140 | 4 | 33292.381 | 30.0369 | 21 | 39.9848
769 | 769 | CL2-383 | KERRY | KERRY | SS-147 | Smearla 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.052 | 9 | 0.708 | 2 | 0.531 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 21 | 33.2924
770 | 770 | CL2-384 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.054 | 15 | 0.716 | 2 | 0.537 | 4.2 | 4.2 | 1650640 | 1 | 393009.5238 | 2.5445 | 4.2 | 317.7238
771 | 771 | CL2-385 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.529 | 16 | 0.484 | 2 | 0.484 | 4.2 | 4.2 | 1703340 | 1 | 405557.1429 | 2.4657 | 4.2 | 393.0095
772 | 772 | CL2-386 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 21.77 | 22 | 1.206 | 2 | 0.9045 | 8.4 | 8.4 | 2064900 | 2 | 245821.4286 | 4.068 | 4.2 | 405.5571
773 | 773 | CL2-387 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 19.238 | 20 | 11.965 | 2 | 8.9737 | 109.2 | 109.2 | 5134660 | 11 | 47020.696 | 21.2672 | 8.4 | 245.8214
774 | 774 | CL2-388 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.059 | 14 | 5.511 | 2 | 4.1333 | 50.4 | 50.4 | 3869800 | 11 | 76781.746 | 13.0239 | 109.2 | 47.0207
775 | 775 | CL2-389 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 16.726 | 17 | 2.986 | 2 | 2.2395 | 25.2 | 25.2 | 1857900 | 5 | 73726.1905 | 13.5637 | 50.4 | 76.7817
776 | 776 | CL2-390 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.488 | 9 | 0.929 | 2 | 0.69675 | 8.4 | 8.4 | 1379800 | 2 | 164261.9048 | 6.0878 | 25.2 | 73.7262
777 | 777 | CL2-391 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 16.672 | 17 | 0.555 | 2 | 0.555 | 4.2 | 4.2 | 1756040 | 1 | 418104.7619 | 2.3917 | 8.4 | 164.2619
778 | 778 | CL2-392 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.941 | 12 | 3.141 | 2 | 2.3558 | 25.2 | 25.2 | 1413750 | 5 | 56101.1905 | 17.8249 | 4.2 | 418.1048
779 | 779 | CL2-393 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.869 | 14 | 0.886 | 2 | 0.6645 | 8.4 | 8.4 | 1643300 | 2 | 195630.9524 | 5.1117 | 25.2 | 56.1012
780 | 780 | CL2-394 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.01 | 14 | 0.314 | 2 | 0.314 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284 | 8.4 | 195.631
781 | 781 | CL2-395 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.669 | 10 | 0.475 | 2 | 0.475 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 4.2 | 380.4619
782 | 782 | CL2-396 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.002 | 6 | 4.355 | 2 | 3.2663 | 37.8 | 37.8 | 1015350 | 6 | 26861.1111 | 37.2285 | 4.2 | 330.2714
783 | 783 | CL2-397 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.067 | 6 | 1.898 | 2 | 1.4235 | 16.8 | 16.8 | 769410 | 4 | 45798.2143 | 21.8349 | 37.8 | 26.8611
784 | 784 | CL2-398 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.896 | 7 | 2.687 | 2 | 2.0152 | 21 | 21 | 839680 | 4 | 39984.7619 | 25.0095 | 16.8 | 45.7982
785 | 785 | CL2-399 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.839 | 5 | 14.672 | 2 | 11.004 | 134.4 | 134.4 | 2818860 | 12 | 20973.6607 | 47.6788 | 21 | 39.9848
786 | 786 | CL2-400 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.144 | 11 | 1.064 | 2 | 0.798 | 8.4 | 8.4 | 1485200 | 2 | 176809.5238 | 5.6558 | 134.4 | 20.9737
787 | 787 | CL2-401 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.586 | 11 | 5.715 | 2 | 4.2862 | 50.4 | 50.4 | 3237370 | 11 | 64233.5317 | 15.5682 | 8.4 | 176.8095
788 | 788 | CL2-402 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.771 | 13 | 0.617 | 2 | 0.46275 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718 | 50.4 | 64.2335
789 | 789 | CL2-403 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.806 | 15 | 0.55 | 2 | 0.55 | 4.2 | 4.2 | 1650640 | 1 | 393009.5238 | 2.5445 | 4.2 | 367.9143
790 | 790 | CL2-404 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.069 | 14 | 3.074 | 2 | 2.3055 | 25.2 | 25.2 | 1591410 | 5 | 63151.1905 | 15.835 | 4.2 | 393.0095
791 | 791 | CL2-405 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.819 | 12 | 7.286 | 2 | 5.4645 | 67.2 | 67.2 | 3448180 | 11 | 51312.2024 | 19.4885 | 25.2 | 63.1512
792 | 792 | CL2-406 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.307 | 12 | 0.668 | 2 | 0.501 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 67.2 | 51.3122
793 | 793 | CL2-407 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.886 | 9 | 2.332 | 2 | 1.749 | 21 | 21 | 980220 | 4 | 46677.1429 | 21.4238 | 4.2 | 355.3667
794 | 794 | CL2-408 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.63 | 12 | 1.894 | 2 | 1.4205 | 16.8 | 16.8 | 1191030 | 4 | 70894.6429 | 14.1054 | 21 | 46.6771
795 | 795 | CL2-409 | MAYO | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 18.431 | 19 | 8.176 | 2 | 6.132 | 75.6 | 75.6 | 4923850 | 11 | 65130.291 | 15.3538 | 16.8 | 70.8946
796 | 796 | CL2-410 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 18.316 | 19 | 1.301 | 2 | 0.97575 | 8.4 | 8.4 | 1906800 | 2 | 227000 | 4.4053 | 75.6 | 65.1303
797 | 797 | CL2-411 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 16.39 | 17 | 10.796 | 2 | 8.097 | 96.6 | 96.6 | 4502230 | 11 | 46606.9358 | 21.456 | 8.4 | 227
798 | 798 | CL2-412 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 14.798 | 15 | 0.436 | 2 | 0.436 | 4.2 | 4.2 | 1650640 | 1 | 393009.5238 | 2.5445 | 96.6 | 46.6069
799 | 799 | CL2-413 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 12.93 | 13 | 1.266 | 2 | 0.9495 | 8.4 | 8.4 | 1590600 | 2 | 189357.1429 | 5.281 | 4.2 | 393.0095
800 | 800 | CL2-414 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 13.856 | 14 | 3.982 | 2 | 2.9865 | 33.6 | 33.6 | 1905430 | 6 | 56709.2262 | 17.6338 | 8.4 | 189.3571
801 | 801 | CL2-415 | MAYO | MAYO | SS-640 | Ballinrobe 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.372 | 15 | 4.29 | 2 | 3.2175 | 37.8 | 37.8 | 2016690 | 6 | 53351.5873 | 18.7436 | 33.6 | 56.7092
802 | 802 | CL2-416 | MAYO | MAYO | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 18.244 | 19 | 1.409 | 2 | 1.0568 | 12.6 | 12.6 | 1943850 | 3 | 154273.8095 | 6.482 | 37.8 | 53.3516
803 | 803 | CL2-417 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 16.492 | 17 | 1.331 | 2 | 0.99825 | 8.4 | 8.4 | 1801400 | 2 | 214452.381 | 4.663 | 12.6 | 154.2738
804 | 804 | CL2-418 | GALWAY | GALWAY | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 17.324 | 18 | 1.863 | 2 | 1.3973 | 16.8 | 16.8 | 1612650 | 4 | 95991.0714 | 10.4176 | 8.4 | 214.4524
805 | 805 | CL2-419 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 16.325 | 17 | 1.005 | 2 | 0.75375 | 8.4 | 8.4 | 1801400 | 2 | 214452.381 | 4.663 | 16.8 | 95.9911
806 | 806 | CL2-420 | GALWAY | GALWAY | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 15.186 | 16 | 0.842 | 2 | 0.6315 | 8.4 | 8.4 | 1748700 | 2 | 208178.5714 | 4.8036 | 8.4 | 214.4524
807 | 807 | CL2-421 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 12.718 | 13 | 0.47 | 2 | 0.47 | 4.2 | 4.2 | 2101570 | 7 | 500373.8095 | 1.9985 | 8.4 | 208.1786
808 | 808 | CL2-422 | GALWAY | GALWAY | SS-638 | Oughterard 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.117 | 9 | 4.259 | 2 | 3.1943 | 37.8 | 37.8 | 1349130 | 6 | 35691.2698 | 28.0181 | 4.2 | 500.3738
809 | 809 | CL2-423 | GALWAY | GALWAY | SS-638 | Oughterard 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 11.242 | 12 | 2.266 | 2 | 1.6995 | 21 | 21 | 1191030 | 4 | 56715.7143 | 17.6318 | 37.8 | 35.6913
810 | 810 | CL2-424 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 11.454 | 12 | 4.255 | 2 | 3.1913 | 37.8 | 37.8 | 3288970 | 10 | 87009.7884 | 11.493 | 21 | 56.7157
811 | 811 | CL2-425 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.972 | 4 | 1.198 | 2 | 0.8985 | 8.4 | 8.4 | 628870 | 4 | 74865.4762 | 13.3573 | 37.8 | 87.0098
812 | 812 | CL2-426 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 22.098 | 23 | 3.497 | 2 | 2.6227 | 29.4 | 29.4 | 2390880 | 5 | 81322.449 | 12.2967 | 8.4 | 74.8655
813 | 813 | CL2-427 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 21.989 | 22 | 0.544 | 2 | 0.544 | 4.2 | 4.2 | 2575870 | 7 | 613302.381 | 1.6305 | 29.4 | 81.3224
814 | 814 | CL2-428 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 20.436 | 21 | 3.046 | 2 | 2.2845 | 25.2 | 25.2 | 3819280 | 9 | 151558.7302 | 6.5981 | 4.2 | 613.3024
815 | 815 | CL2-429 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 18.073 | 19 | 0.486 | 2 | 0.486 | 4.2 | 4.2 | 2417770 | 7 | 575659.5238 | 1.7371 | 25.2 | 151.5587
816 | 816 | CL2-430 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 12.261 | 13 | 9.945 | 2 | 7.4588 | 92.4 | 92.4 | 3658990 | 11 | 39599.4589 | 25.2529 | 4.2 | 575.6595
817 | 817 | CL2-431 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 11.499 | 12 | 0.986 | 2 | 0.7395 | 8.4 | 8.4 | 2048870 | 7 | 243913.0952 | 4.0998 | 92.4 | 39.5995
818 | 818 | CL2-432 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 18.517 | 19 | 13.319 | 2 | 9.9893 | 121.8 | 121.8 | 4923850 | 11 | 40425.6979 | 24.7367 | 8.4 | 243.9131
819 | 819 | CL2-433 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 18.616 | 19 | 1.505 | 2 | 1.1287 | 12.6 | 12.6 | 1943850 | 3 | 154273.8095 | 6.482 | 121.8 | 40.4257
820 | 820 | CL2-434 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 16.54 | 17 | 6.782 | 2 | 5.0865 | 63 | 63 | 4502230 | 11 | 71463.9683 | 13.9931 | 12.6 | 154.2738
821 | 821 | CL2-435 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 23.484 | 24 | 1.556 | 2 | 1.167 | 12.6 | 12.6 | 2681270 | 7 | 212799.2063 | 4.6993 | 63 | 71.464
822 | 822 | CL2-436 | MAYO | MAYO | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 21.148 | 22 | 3.306 | 2 | 2.4795 | 29.4 | 29.4 | 2302050 | 5 | 78301.0204 | 12.7712 | 12.6 | 212.7992
823 | 823 | CL2-437 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 25.893 | 26 | 0.891 | 2 | 0.66825 | 8.4 | 8.4 | 2786670 | 7 | 331746.4286 | 3.0144 | 29.4 | 78.301
824 | 824 | CL2-438 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 28.367 | 29 | 8.563 | 2 | 6.4223 | 79.8 | 79.8 | 7031950 | 11 | 88119.6742 | 11.3482 | 8.4 | 331.7464
825 | 825 | CL2-439 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 25.089 | 26 | 2.738 | 2 | 2.0535 | 25.2 | 25.2 | 4263430 | 9 | 169183.7302 | 5.9107 | 79.8 | 88.1197
826 | 826 | CL2-440 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 30.995 | 31 | 1.41 | 2 | 1.0575 | 12.6 | 12.6 | 3050170 | 7 | 242076.9841 | 4.1309 | 25.2 | 169.1837
827 | 827 | CL2-441 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.695 | 8 | 3.787 | 2 | 2.8403 | 33.6 | 33.6 | 1237870 | 6 | 36841.369 | 27.1434 | 12.6 | 242.077
828 | 828 | CL2-442 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.325 | 9 | 0.822 | 2 | 0.6165 | 8.4 | 8.4 | 1379800 | 2 | 164261.9048 | 6.0878 | 33.6 | 36.8414
829 | 829 | CL2-443 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.476 | 10 | 1.059 | 2 | 0.79425 | 8.4 | 8.4 | 1432500 | 2 | 170535.7143 | 5.8639 | 8.4 | 164.2619
830 | 830 | CL2-444 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.615 | 8 | 0.557 | 2 | 0.557 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 8.4 | 170.5357
831 | 831 | CL2-445 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.35 | 6 | 1.76 | 2 | 1.32 | 12.6 | 12.6 | 769410 | 4 | 61064.2857 | 16.3762 | 4.2 | 216.6548
832 | 832 | CL2-446 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.822 | 4 | 0.414 | 2 | 0.414 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 12.6 | 61.0643
833 | 833 | CL2-447 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.532 | 4 | 6.396 | 2 | 4.797 | 58.8 | 58.8 | 1761700 | 11 | 29960.8844 | 33.3769 | 4.2 | 149.731
834 | 834 | CL2-448 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.041 | 12 | 0.318 | 2 | 0.318 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 58.8 | 29.9609
835 | 835 | CL2-449 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.997 | 13 | 1.717 | 2 | 1.2877 | 12.6 | 12.6 | 1627650 | 3 | 129178.5714 | 7.7412 | 4.2 | 355.3667
836 | 836 | CL2-450 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.216 | 11 | 23.799 | 2 | 17.8492 | 218.4 | 218.4 | 9068760 | 13 | 41523.6264 | 24.0827 | 12.6 | 129.1786
837 | 837 | CL2-451 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.07 | 14 | 3.951 | 2 | 2.9632 | 33.6 | 33.6 | 1905430 | 6 | 56709.2262 | 17.6338 | 218.4 | 41.5236
838 | 838 | CL2-452 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.914 | 8 | 3.146 | 2 | 2.3595 | 25.2 | 25.2 | 1058430 | 5 | 42001.1905 | 23.8088 | 33.6 | 56.7092
839 | 839 | CL2-453 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 3.305 | 4 | 8.626 | 2 | 6.4695 | 79.8 | 79.8 | 1761700 | 11 | 22076.4411 | 45.2972 | 25.2 | 42.0012
840 | 840 | CL2-454 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.038 | 11 | 10.877 | 2 | 8.1578 | 100.8 | 100.8 | 3237370 | 11 | 32116.7659 | 31.1364 | 79.8 | 22.0764
841 | 841 | CL2-455 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.74 | 9 | 0.772 | 2 | 0.579 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 100.8 | 32.1168
842 | 842 | CL2-456 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.907 | 6 | 36.21 | 2 | 27.1575 | 336 | 336 | 6397880 | 12 | 19041.3095 | 52.5174 | 4.2 | 317.7238
843 | 843 | CL2-457 | MAYO | MAYO | SS-170 | Derrynadivva 38kV Substation | ESB Networks | 38000 | low | 38000 | 12.163 | 13 | 13.75 | 2 | 10.3125 | 126 | 126 | 5191820 | 13 | 41204.9206 | 24.2689 | 336 | 19.0413
844 | 844 | CL2-458 | MAYO | MAYO | SS-317 | Newport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.974 | 12 | 5.964 | 2 | 4.473 | 54.6 | 54.6 | 3448180 | 11 | 63153.4799 | 15.8344 | 126 | 41.2049
845 | 845 | CL2-459 | MAYO | MAYO | SS-317 | Newport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.521 | 10 | 3.132 | 2 | 2.349 | 25.2 | 25.2 | 1236090 | 5 | 49051.1905 | 20.3869 | 54.6 | 63.1535
846 | 846 | CL2-460 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 12.335 | 13 | 4.208 | 2 | 3.156 | 37.8 | 37.8 | 3400230 | 10 | 89953.1746 | 11.1169 | 25.2 | 49.0512
847 | 847 | CL2-461 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.302 | 5 | 0.437 | 2 | 0.437 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 37.8 | 89.9532
848 | 848 | CL2-462 | MAYO | MAYO | SS-317 | Newport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.317 | 9 | 0.933 | 2 | 0.69975 | 8.4 | 8.4 | 1379800 | 2 | 164261.9048 | 6.0878 | 4.2 | 166.4619
849 | 849 | CL2-463 | MAYO | MAYO | SS-317 | Newport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.864 | 12 | 1.173 | 2 | 0.87975 | 8.4 | 8.4 | 1537900 | 2 | 183083.3333 | 5.462 | 8.4 | 164.2619
850 | 850 | CL2-464 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.931 | 6 | 4.211 | 2 | 3.1583 | 37.8 | 37.8 | 1015350 | 6 | 26861.1111 | 37.2285 | 8.4 | 183.0833
851 | 851 | CL2-465 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.265 | 9 | 0.423 | 2 | 0.423 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 37.8 | 26.8611
852 | 852 | CL2-466 | MAYO | MAYO | SS-498 | Belmullet 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.325 | 9 | 8.357 | 2 | 6.2677 | 75.6 | 75.6 | 2815750 | 11 | 37245.3704 | 26.849 | 4.2 | 317.7238
853 | 853 | CL2-467 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.398 | 5 | 10.24 | 2 | 7.68 | 92.4 | 92.4 | 1972510 | 11 | 21347.5108 | 46.8439 | 75.6 | 37.2454
854 | 854 | CL2-468 | MAYO | MAYO | SS-170 | Derrynadivva 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.75 | 4 | 2.651 | 2 | 1.9882 | 21 | 21 | 628870 | 4 | 29946.1905 | 33.3932 | 92.4 | 21.3475
855 | 855 | CL2-469 | MAYO | MAYO | SS-317 | Newport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.862 | 5 | 3.095 | 2 | 2.3213 | 25.2 | 25.2 | 791940 | 5 | 31426.1905 | 31.8206 | 21 | 29.9462
856 | 856 | CL2-470 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 16.685 | 17 | 5.317 | 2 | 3.9878 | 46.2 | 46.2 | 4502230 | 11 | 97450.8658 | 10.2616 | 25.2 | 31.4262
857 | 857 | CL2-471 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.957 | 13 | 5.248 | 2 | 3.936 | 46.2 | 46.2 | 3658990 | 11 | 79198.9177 | 12.6264 | 46.2 | 97.4509
858 | 858 | CL2-472 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 17.137 | 18 | 1.138 | 2 | 0.8535 | 8.4 | 8.4 | 1854100 | 2 | 220726.1905 | 4.5305 | 46.2 | 79.1989
859 | 859 | CL2-473 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 19.07 | 20 | 1.675 | 2 | 1.2563 | 12.6 | 12.6 | 1996550 | 3 | 158456.3492 | 6.3109 | 8.4 | 220.7262
860 | 860 | CL2-474 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 9.301 | 10 | 159.806 | 2 | 119.8545 | 1491 | 1491 | 42473340 | 999999999 | 28486.4789 | 35.1044 | 12.6 | 158.4563
861 | 861 | CL2-475 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 16.595 | 17 | 4.189 | 2 | 3.1418 | 37.8 | 37.8 | 3845270 | 10 | 101726.7196 | 9.8303 | 1491 | 28.4865
862 | 862 | CL2-476 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.712 | 3 | 5.049 | 2 | 3.7868 | 46.2 | 46.2 | 1550890 | 11 | 33569.0476 | 29.7893 | 37.8 | 101.7267
863 | 863 | CL2-477 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 19.323 | 20 | 2.882 | 2 | 2.1615 | 25.2 | 25.2 | 3730450 | 9 | 148033.7302 | 6.7552 | 46.2 | 33.569
864 | 864 | CL2-478 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.401 | 11 | 0.452 | 2 | 0.452 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 25.2 | 148.0337
865 | 865 | CL2-479 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.639 | 8 | 0.668 | 2 | 0.501 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 342.819
866 | 866 | CL2-480 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.114 | 7 | 0.487 | 2 | 0.487 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 216.6548
867 | 867 | CL2-481 | SLIGO | MAYO | SS-302 | Carrowleagh 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.405 | 5 | 51.771 | 2 | 38.8282 | 483 | 483 | 8456580 | 12 | 17508.4472 | 57.1153 | 4.2 | 199.9238
868 | 868 | CL2-482 | SLIGO | SLIGO | SS-302 | Carrowleagh 38kV Substation | ESB Networks | 38000 | low | 38000 | 6.398 | 7 | 2.305 | 2 | 1.7288 | 21 | 21 | 839680 | 4 | 39984.7619 | 25.0095 | 483 | 17.5084
869 | 869 | CL2-483 | SLIGO | SLIGO | SS-075 | Cunghill 110kV Substation | EirGrid | 110000 | 110000 | medium | 9.416 | 10 | 7.447 | 2 | 5.5853 | 67.2 | 67.2 | 3026560 | 11 | 45038.0952 | 22.2034 | 21 | 39.9848
870 | 870 | CL2-484 | SLIGO | SLIGO | SS-075 | Cunghill 110kV Substation | EirGrid | 110000 | 110000 | medium | 7.276 | 8 | 6.104 | 2 | 4.578 | 54.6 | 54.6 | 2604940 | 11 | 47709.5238 | 20.9602 | 67.2 | 45.0381
871 | 871 | CL2-485 | SLIGO | SLIGO | SS-075 | Cunghill 110kV Substation | EirGrid | 110000 | 110000 | medium | 10.159 | 11 | 1.568 | 2 | 1.176 | 12.6 | 12.6 | 1996170 | 7 | 158426.1905 | 6.3121 | 54.6 | 47.7095
872 | 872 | CL2-486 | SLIGO | SLIGO | SS-075 | Cunghill 110kV Substation | EirGrid | 110000 | 110000 | medium | 8.513 | 9 | 0.41 | 2 | 0.41 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213 | 12.6 | 158.4262
873 | 873 | CL2-487 | SLIGO | SLIGO | SS-074 | Tobercurry 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.784 | 9 | 0.503 | 2 | 0.503 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 450.1833
874 | 874 | CL2-488 | SLIGO | SLIGO | SS-302 | Carrowleagh 38kV Substation | ESB Networks | 38000 | low | 38000 | 7.448 | 8 | 0.725 | 2 | 0.54375 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 317.7238
875 | 875 | CL2-489 | SLIGO | SLIGO | SS-227 | Bundoran 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.552 | 12 | 0.733 | 2 | 0.54975 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 216.6548
876 | 876 | CL2-490 | LEITRIM | LEITRIM | SS-227 | Bundoran 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.834 | 12 | 0.371 | 2 | 0.371 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 355.3667
877 | 877 | CL2-491 | SLIGO | LEITRIM | SS-042 | Ballytivnan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 11.555 | 12 | 13.159 | 2 | 9.8693 | 121.8 | 121.8 | 3448180 | 11 | 28310.1806 | 35.323 | 4.2 | 355.3667
878 | 878 | CL2-492 | SLIGO | SLIGO | SS-042 | Ballytivnan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.573 | 9 | 0.524 | 2 | 0.524 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 121.8 | 28.3102
879 | 879 | CL2-493 | SLIGO | SLIGO | SS-042 | Ballytivnan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 10.85 | 11 | 0.288 | 2 | 0.288 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 317.7238
880 | 880 | CL2-494 | SLIGO | SLIGO | SS-042 | Ballytivnan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.592 | 8 | 0.763 | 2 | 0.57225 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 342.819
881 | 881 | CL2-495 | SLIGO | SLIGO | SS-031 | Sligo 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 3.346 | 4 | 1.856 | 2 | 1.392 | 16.8 | 16.8 | 1875790 | 8 | 111654.1667 | 8.9562 | 4.2 | 216.6548
882 | 882 | CL2-496 | SLIGO | SLIGO | SS-227 | Bundoran 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.34 | 14 | 0.414 | 2 | 0.414 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284 | 16.8 | 111.6542
883 | 883 | CL2-497 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 9.054 | 10 | 2.989 | 2 | 2.2417 | 25.2 | 25.2 | 1236090 | 5 | 49051.1905 | 20.3869 | 4.2 | 380.4619
884 | 884 | CL2-498 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 6.55 | 7 | 0.813 | 2 | 0.60975 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 25.2 | 49.0512
885 | 885 | CL2-499 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 6.473 | 7 | 2.456 | 2 | 1.842 | 21 | 21 | 839680 | 4 | 39984.7619 | 25.0095 | 4.2 | 199.9238
886 | 886 | CL2-500 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 12.155 | 13 | 2.956 | 2 | 2.217 | 25.2 | 25.2 | 1502580 | 5 | 59626.1905 | 16.7712 | 21 | 39.9848
887 | 887 | CL2-501 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 12.862 | 13 | 1.308 | 2 | 0.981 | 8.4 | 8.4 | 1590600 | 2 | 189357.1429 | 5.281 | 25.2 | 59.6262
888 | 888 | CL2-502 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 12.042 | 13 | 0.891 | 2 | 0.66825 | 8.4 | 8.4 | 1590600 | 2 | 189357.1429 | 5.281 | 8.4 | 189.3571
889 | 889 | CL2-503 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 10.007 | 11 | 7.031 | 2 | 5.2732 | 63 | 63 | 3237370 | 11 | 51386.8254 | 19.4602 | 8.4 | 189.3571
890 | 890 | CL2-504 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 9.795 | 10 | 2.469 | 2 | 1.8518 | 21 | 21 | 1050490 | 4 | 50023.3333 | 19.9907 | 63 | 51.3868
891 | 891 | CL2-505 | DONEGAL | DONEGAL | SS-090 | Corkermore 38kV Substation | ESB Networks | 38000 | low | 38000 | 5.981 | 6 | 0.395 | 2 | 0.395 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 21 | 50.0233
892 | 892 | CL2-506 | DONEGAL | DONEGAL | SS-090 | Corkermore 38kV Substation | ESB Networks | 38000 | low | 38000 | 5.979 | 6 | 1.277 | 2 | 0.95775 | 8.4 | 8.4 | 769410 | 4 | 91596.4286 | 10.9175 | 4.2 | 183.1929
893 | 893 | CL2-507 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 4.969 | 5 | 18.342 | 2 | 13.7565 | 168 | 168 | 2818860 | 12 | 16778.9286 | 59.5986 | 8.4 | 91.5964
895 | 895 | CL2-509 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 4.561 | 5 | 4.409 | 2 | 3.3068 | 37.8 | 37.8 | 2510150 | 10 | 66406.0847 | 15.0589 | 168 | 16.7789
896 | 896 | CL2-510 | DONEGAL | DONEGAL | SS-089 | Loughderryduff 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.763 | 3 | 0.754 | 2 | 0.5655 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 37.8 | 66.4061
897 | 897 | CL2-511 | DONEGAL | DONEGAL | SS-089 | Loughderryduff 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.216 | 3 | 2.367 | 2 | 1.7752 | 21 | 21 | 558600 | 4 | 26600 | 37.594 | 4.2 | 133
898 | 898 | CL2-512 | DONEGAL | DONEGAL | SS-089 | Loughderryduff 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.317 | 4 | 2.994 | 2 | 2.2455 | 25.2 | 25.2 | 703110 | 5 | 27901.1905 | 35.8408 | 21 | 26.6
899 | 899 | CL2-513 | DONEGAL | DONEGAL | SS-090 | Corkermore 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.749 | 4 | 0.387 | 2 | 0.387 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 25.2 | 27.9012
900 | 900 | CL2-514 | DONEGAL | DONEGAL | SS-138 | Creeslough 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.386 | 8 | 0.645 | 2 | 0.48375 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 149.731
901 | 901 | CL2-515 | DONEGAL | DONEGAL | SS-610 | Milford (North) 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.811 | 10 | 0.503 | 2 | 0.503 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 4.2 | 216.6548
902 | 902 | CL2-516 | DONEGAL | DONEGAL | SS-119 | Drumlough Hill (1) 38kV Substation | ESB Networks | 38000 | low | 38000 | 6.26 | 7 | 0.923 | 2 | 0.69225 | 8.4 | 8.4 | 839680 | 4 | 99961.9048 | 10.0038 | 4.2 | 330.2714
903 | 903 | CL2-517 | DONEGAL | DONEGAL | SS-119 | Drumlough Hill (1) 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.36 | 4 | 3.142 | 2 | 2.3565 | 25.2 | 25.2 | 703110 | 5 | 27901.1905 | 35.8408 | 8.4 | 99.9619
904 | 904 | CL2-518 | DONEGAL | DONEGAL | SS-272 | Carndonagh 38kV | ESB Networks | 38000 | 38000 | low | 8.796 | 9 | 1.285 | 2 | 0.96375 | 8.4 | 8.4 | 1379800 | 2 | 164261.9048 | 6.0878 | 25.2 | 27.9012
905 | 905 | CL2-519 | DONEGAL | DONEGAL | SS-272 | Carndonagh 38kV | ESB Networks | 38000 | 38000 | low | 12.413 | 13 | 0.428 | 2 | 0.428 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718 | 8.4 | 164.2619
906 | 906 | CL2-520 | DONEGAL | DONEGAL | SS-239 | Moville 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 3.779 | 4 | 1.344 | 2 | 1.008 | 8.4 | 8.4 | 628870 | 4 | 74865.4762 | 13.3573 | 4.2 | 367.9143
907 | 907 | CL2-521 | DONEGAL | DONEGAL | SS-117 | Crockahenny 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.618 | 4 | 12.867 | 2 | 9.6502 | 117.6 | 117.6 | 1761700 | 11 | 14980.4422 | 66.7537 | 8.4 | 74.8655
908 | 908 | CL2-522 | DONEGAL | DONEGAL | SS-118 | Sorne Hill 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 4.867 | 5 | 1.793 | 2 | 1.3447 | 12.6 | 12.6 | 1679970 | 7 | 133330.9524 | 7.5001 | 117.6 | 14.9804
909 | 909 | CL2-523 | DONEGAL | DONEGAL | SS-125 | Drumlough Hill (2) 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.997 | 5 | 3.898 | 2 | 2.9235 | 33.6 | 33.6 | 904090 | 6 | 26907.4405 | 37.1644 | 12.6 | 133.331
910 | 910 | CL2-524 | DONEGAL | DONEGAL | SS-272 | Carndonagh 38kV | ESB Networks | 38000 | 38000 | low | 3.581 | 4 | 2.699 | 2 | 2.0242 | 21 | 21 | 628870 | 4 | 29946.1905 | 33.3932 | 33.6 | 26.9074
911 | 911 | CL2-525 | DONEGAL | DONEGAL | SS-272 | Carndonagh 38kV | ESB Networks | 38000 | 38000 | low | 3.963 | 4 | 1.812 | 2 | 1.359 | 16.8 | 16.8 | 628870 | 4 | 37432.7381 | 26.7146 | 21 | 29.9462
912 | 912 | CL2-526 | DONEGAL | DONEGAL | SS-689 |  | ESB Networks | 38000 |  |  | 3.007 | 4 | 3.248 | 2 | 2.436 | 29.4 | 29.4 | 703110 | 5 | 23915.3061 | 41.8142 | 16.8 | 37.4327
913 | 913 | CL2-527 | DONEGAL | DONEGAL | SS-689 |  | ESB Networks | 38000 |  |  | 4.437 | 5 | 2.934 | 2 | 2.2005 | 25.2 | 25.2 | 791940 | 5 | 31426.1905 | 31.8206 | 29.4 | 23.9153
914 | 914 | CL2-528 | DONEGAL | DONEGAL | SS-689 |  | ESB Networks | 38000 |  |  | 4.504 | 5 | 4.489 | 2 | 3.3667 | 37.8 | 37.8 | 904090 | 6 | 23917.7249 | 41.81 | 25.2 | 31.4262
915 | 915 | CL2-529 | DONEGAL | DONEGAL | SS-689 |  | ESB Networks | 38000 |  |  | 1.533 | 2 | 1.435 | 2 | 1.0762 | 12.6 | 12.6 | 488330 | 4 | 38756.3492 | 25.8022 | 37.8 | 23.9177
916 | 916 | CL2-530 | DONEGAL | DONEGAL | SS-689 |  | ESB Networks | 38000 |  |  | 3.465 | 4 | 5.323 | 2 | 3.9923 | 46.2 | 46.2 | 1761700 | 11 | 38132.0346 | 26.2247 | 12.6 | 38.7563
917 | 917 | CL2-531 | DONEGAL | DONEGAL | SS-689 |  | ESB Networks | 38000 |  |  | 4.983 | 5 | 1.491 | 2 | 1.1183 | 12.6 | 12.6 | 699140 | 4 | 55487.3016 | 18.0221 | 46.2 | 38.132
918 | 918 | CL2-532 | DONEGAL | DONEGAL | SS-687 | Gweedore Wind Farm 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.545 | 4 | 0.84 | 2 | 0.63 | 8.4 | 8.4 | 628870 | 4 | 74865.4762 | 13.3573 | 12.6 | 55.4873
919 | 919 | CL2-533 | DONEGAL | DONEGAL | SS-687 | Gweedore Wind Farm 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.401 | 5 | 2.551 | 2 | 1.9133 | 21 | 21 | 699140 | 4 | 33292.381 | 30.0369 | 8.4 | 74.8655
920 | 920 | CL2-534 | DONEGAL | DONEGAL | SS-289 | Gweedore 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 2.179 | 3 | 2.11 | 2 | 1.5825 | 16.8 | 16.8 | 558600 | 4 | 33250 | 30.0752 | 21 | 33.2924
921 | 921 | CL2-535 | DONEGAL | DONEGAL | SS-610 | Milford (North) 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.299 | 7 | 0.287 | 2 | 0.287 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 16.8 | 33.25
922 | 922 | CL2-536 | DONEGAL | DONEGAL | SS-610 | Milford (North) 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.896 | 5 | 0.622 | 2 | 0.4665 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 199.9238
923 | 923 | CL2-537 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.387 | 8 | 0.474 | 2 | 0.474 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 166.4619
924 | 924 | CL2-538 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.281 | 6 | 0.463 | 2 | 0.463 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 216.6548
925 | 925 | CL2-539 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.054 | 9 | 0.312 | 2 | 0.312 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 183.1929
926 | 926 | CL2-540 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.889 | 9 | 0.897 | 2 | 0.67275 | 8.4 | 8.4 | 1379800 | 2 | 164261.9048 | 6.0878 | 4.2 | 317.7238
927 | 927 | CL2-541 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.507 | 9 | 0.832 | 2 | 0.624 | 8.4 | 8.4 | 1379800 | 2 | 164261.9048 | 6.0878 | 8.4 | 164.2619
928 | 928 | CL2-542 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 20.452 | 21 | 0.389 | 2 | 0.389 | 4.2 | 4.2 | 1966840 | 1 | 468295.2381 | 2.1354 | 8.4 | 164.2619
929 | 929 | CL2-543 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 17.134 | 18 | 1.083 | 2 | 0.81225 | 8.4 | 8.4 | 1854100 | 2 | 220726.1905 | 4.5305 | 4.2 | 468.2952
930 | 930 | CL2-544 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 20.926 | 21 | 0.589 | 2 | 0.589 | 4.2 | 4.2 | 1966840 | 1 | 468295.2381 | 2.1354 | 8.4 | 220.7262
931 | 931 | CL2-545 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 18.272 | 19 | 1.881 | 2 | 1.4107 | 16.8 | 16.8 | 1682920 | 4 | 100173.8095 | 9.9826 | 4.2 | 468.2952
932 | 932 | CL2-546 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 13.482 | 14 | 0.579 | 2 | 0.579 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284 | 16.8 | 100.1738
933 | 933 | CL2-547 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.018 | 5 | 0.564 | 2 | 0.564 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 380.4619
934 | 934 | CL2-548 | KERRY | KERRY | SS-636 | Garranebane 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.46 | 12 | 0.605 | 2 | 0.605 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 166.4619
935 | 935 | CL2-549 | SLIGO | SLIGO | SS-128 | Garvagh Glebe 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 4.232 | 5 | 2.734 | 2 | 2.0505 | 25.2 | 25.2 | 2398000 | 9 | 95158.7302 | 10.5088 | 4.2 | 355.3667
936 | 936 | CL2-550 | SLIGO | LEITRIM | SS-128 | Garvagh Glebe 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 3.932 | 4 | 2.619 | 2 | 1.9643 | 21 | 21 | 1875790 | 8 | 89323.3333 | 11.1953 | 25.2 | 95.1587
937 | 937 | CL2-551 | ROSCOMMON | SLIGO | SS-304 | Arigna 110kV Substation | EirGrid | 110000 | 110000 | 20000 | 5.774 | 6 | 1.88 | 2 | 1.41 | 16.8 | 16.8 | 2016330 | 8 | 120019.6429 | 8.332 | 21 | 89.3233
938 | 938 | CL2-552 | WEXFORD | WEXFORD | SS-481 | Castledockrell 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 7.399 | 8 | 2.082 | 2 | 1.5615 | 16.8 | 16.8 | 2156870 | 8 | 128385.119 | 7.7891 | 16.8 | 120.0196
939 | 939 | CL2-553 | CARLOW | CARLOW | SS-494 | Bunclody 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.802 | 10 | 3.337 | 2 | 2.5028 | 29.4 | 29.4 | 1236090 | 5 | 42043.8776 | 23.7847 | 16.8 | 128.3851
940 | 940 | CL2-554 | CARLOW | CARLOW | SS-487 | Bagenalstown 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.734 | 12 | 0.537 | 2 | 0.537 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 29.4 | 42.0439
941 | 941 | CL2-555 | CARLOW | CARLOW | SS-481 | Castledockrell 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 11.413 | 12 | 0.456 | 2 | 0.456 | 4.2 | 4.2 | 2048870 | 7 | 487826.1905 | 2.0499 | 4.2 | 355.3667
942 | 942 | CL2-556 | CARLOW | WEXFORD | SS-481 | Castledockrell 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 9.519 | 10 | 4.49 | 2 | 3.3675 | 37.8 | 37.8 | 3066450 | 10 | 81123.0159 | 12.327 | 4.2 | 487.8262
943 | 943 | CL2-557 | WICKLOW | WICKLOW | SS-222 | Poulaphouca 110kV Substation | EirGrid | 110000 | low | 110000 | 12.857 | 13 | 0.172 | 2 | 0.172 | 4.2 | 4.2 | 2101570 | 7 | 500373.8095 | 1.9985 | 37.8 | 81.123
944 | 944 | CL2-558 | WICKLOW | WICKLOW | SS-062 | Stratford 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 6.613 | 7 | 1.519 | 2 | 1.1392 | 12.6 | 12.6 | 1785370 | 7 | 141696.0317 | 7.0574 | 4.2 | 500.3738
945 | 945 | CL2-559 | WICKLOW | WICKLOW | SS-062 | Stratford 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 7.608 | 8 | 3.499 | 2 | 2.6242 | 29.4 | 29.4 | 2664490 | 9 | 90628.9116 | 11.034 | 12.6 | 141.696
946 | 946 | CL2-560 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.807 | 7 | 2.474 | 2 | 1.8555 | 21 | 21 | 839680 | 4 | 39984.7619 | 25.0095 | 29.4 | 90.6289
947 | 947 | CL2-561 | WICKLOW | WICKLOW | SS-062 | Stratford 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.588 | 9 | 1.55 | 2 | 1.1625 | 12.6 | 12.6 | 1890770 | 7 | 150061.1111 | 6.664 | 21 | 39.9848
948 | 948 | CL2-562 | WICKLOW | WICKLOW | SS-062 | Stratford 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 6.829 | 7 | 0.64 | 2 | 0.48 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525 | 12.6 | 150.0611
949 | 949 | CL2-563 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.118 | 9 | 5.919 | 2 | 4.4392 | 54.6 | 54.6 | 2815750 | 11 | 51570.5128 | 19.3909 | 4.2 | 425.0881
950 | 950 | CL2-564 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.439 | 11 | 6.841 | 2 | 5.1307 | 63 | 63 | 3237370 | 11 | 51386.8254 | 19.4602 | 54.6 | 51.5705
951 | 951 | CL2-565 | WICKLOW | WICKLOW | SS-699 | Ballycumber 38kV Substation | ESB Networks | 38000 | low | 38000 | 10.708 | 11 | 2.331 | 2 | 1.7483 | 21 | 21 | 1120760 | 4 | 53369.5238 | 18.7373 | 63 | 51.3868
952 | 952 | CL2-566 | WICKLOW | WICKLOW | SS-699 | Ballycumber 38kV Substation | ESB Networks | 38000 | low | 38000 | 11.326 | 12 | 2.922 | 2 | 2.1915 | 25.2 | 25.2 | 1413750 | 5 | 56101.1905 | 17.8249 | 21 | 53.3695
953 | 953 | CL2-567 | WICKLOW | WICKLOW | SS-062 | Stratford 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 10.335 | 11 | 0.6 | 2 | 0.6 | 4.2 | 4.2 | 1996170 | 7 | 475278.5714 | 2.104 | 25.2 | 56.1012
954 | 954 | CL2-568 | WICKLOW | WICKLOW | SS-222 | Poulaphouca 110kV Substation | EirGrid | 110000 | low | 110000 | 13.099 | 14 | 3.656 | 2 | 2.742 | 33.6 | 33.6 | 3511490 | 10 | 104508.631 | 9.5686 | 4.2 | 475.2786
955 | 955 | CL2-569 | WICKLOW | WICKLOW | SS-222 | Poulaphouca 110kV Substation | EirGrid | 110000 | low | 110000 | 9.239 | 10 | 1.742 | 2 | 1.3065 | 12.6 | 12.6 | 1943470 | 7 | 154243.6508 | 6.4832 | 33.6 | 104.5086
956 | 956 | CL2-570 | WICKLOW | WICKLOW | SS-209 | Blessington 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.499 | 10 | 0.939 | 2 | 0.70425 | 8.4 | 8.4 | 1432500 | 2 | 170535.7143 | 5.8639 | 12.6 | 154.2437
957 | 957 | CL2-571 | DUBLIN | DUBLIN | SS-018 | Old Bawn 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.663 | 9 | 1.216 | 2 | 0.912 | 8.4 | 8.4 | 1379800 | 2 | 164261.9048 | 6.0878 | 8.4 | 170.5357
958 | 958 | CL2-572 | WICKLOW | WICKLOW | SS-570 | Kilcoole 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.873 | 14 | 0.866 | 2 | 0.6495 | 8.4 | 8.4 | 1643300 | 2 | 195630.9524 | 5.1117 | 8.4 | 164.2619
959 | 959 | CL2-573 | WEXFORD | WICKLOW | SS-616 | Ballinvally 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 3.179 | 4 | 2.376 | 2 | 1.782 | 21 | 21 | 628870 | 4 | 29946.1905 | 33.3932 | 8.4 | 195.631
960 | 960 | CL2-574 | WICKLOW | WICKLOW | SS-616 | Ballinvally 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 2.41 | 3 | 0.773 | 2 | 0.57975 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 21 | 29.9462
961 | 961 | CL2-575 | CORK | CORK | SS-261 | Milane Hill 38kV Station | ESB Networks | 38000 |  |  | 2.085 | 3 | 0.2 | 2 | 0.2 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 133
962 | 962 | CL2-576 | CORK | KERRY | SS-668 | Coomataggart 110 kV Substation | EirGrid | 110000 | low | 110000 | 5.555 | 6 | 5.051 | 2 | 3.7883 | 46.2 | 46.2 | 2183320 | 11 | 47258.0087 | 21.1604 | 4.2 | 133
963 | 963 | CL2-577 | KERRY | KERRY | SS-668 | Coomataggart 110 kV Substation | EirGrid | 110000 | low | 110000 | 2.323 | 3 | 7.915 | 2 | 5.9363 | 71.4 | 71.4 | 1550890 | 11 | 21721.1485 | 46.0381 | 46.2 | 47.258
964 | 964 | CL2-578 | CORK | CORK | SS-668 | Coomataggart 110 kV Substation | EirGrid | 110000 | low | 110000 | 2.107 | 3 | 1.287 | 2 | 0.96525 | 8.4 | 8.4 | 1574570 | 7 | 187448.8095 | 5.3348 | 71.4 | 21.7211
965 | 965 | CL2-579 | CORK | KERRY | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.211 | 4 | 1.54 | 2 | 1.155 | 12.6 | 12.6 | 628870 | 4 | 49910.3175 | 20.0359 | 8.4 | 187.4488
966 | 966 | CL2-580 | CORK | CORK | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.449 | 3 | 1.569 | 2 | 1.1767 | 12.6 | 12.6 | 558600 | 4 | 44333.3333 | 22.5564 | 12.6 | 49.9103
967 | 967 | CL2-581 | CORK | CORK | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.953 | 5 | 6.746 | 2 | 5.0595 | 58.8 | 58.8 | 1972510 | 11 | 33546.0884 | 29.8097 | 12.6 | 44.3333
968 | 968 | CL2-582 | KERRY | KERRY | SS-071 | Coomagearlahy Substation | EirGrid | 110000 | medium-low | 110000 | 1.84 | 2 | 0.8 | 2 | 0.6 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341 | 58.8 | 33.5461
969 | 969 | CL2-583 | KERRY | KERRY | SS-071 | Coomagearlahy Substation | EirGrid | 110000 | medium-low | 110000 | 3.81 | 4 | 1.026 | 2 | 0.7695 | 8.4 | 8.4 | 1627270 | 7 | 193722.619 | 5.162 | 4.2 | 319.0667
970 | 970 | CL2-584 | CORK | CORK | SS-070 | Glanlee 110kV Substation | EirGrid | 110000 | low | 110000 | 5.903 | 6 | 2.744 | 2 | 2.058 | 25.2 | 25.2 | 2486830 | 9 | 98683.7302 | 10.1334 | 8.4 | 193.7226
971 | 971 | CL2-585 | CORK | KERRY | SS-668 | Coomataggart 110 kV Substation | EirGrid | 110000 | low | 110000 | 2.797 | 3 | 0.799 | 2 | 0.59925 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674 | 25.2 | 98.6837
972 | 972 | CL2-586 | CORK | KERRY | SS-162 | Garrow 110kV Substation | EirGrid | 110000 | 38000 | 110000 | 6.116 | 7 | 9.38 | 2 | 7.035 | 84 | 84 | 2394130 | 11 | 28501.5476 | 35.0858 | 4.2 | 374.8976
973 | 973 | CL2-587 | KERRY | KERRY | SS-072 | Clonkeen 110kV Substation | EirGrid | 110000 |  |  | 3.115 | 4 | 6.361 | 2 | 4.7707 | 58.8 | 58.8 | 1761700 | 11 | 29960.8844 | 33.3769 | 84 | 28.5015
974 | 974 | CL2-588 | CORK | KERRY | SS-162 | Garrow 110kV Substation | EirGrid | 110000 | 38000 | 110000 | 5.282 | 6 | 7.26 | 2 | 5.445 | 67.2 | 67.2 | 2183320 | 11 | 32489.881 | 30.7788 | 58.8 | 29.9609
975 | 975 | CL2-589 | CORK | CORK | SS-162 | Garrow 110kV Substation | EirGrid | 110000 | 38000 | 110000 | 2.505 | 3 | 1.42 | 2 | 1.065 | 12.6 | 12.6 | 1574570 | 7 | 124965.873 | 8.0022 | 67.2 | 32.4899
976 | 976 | CL2-590 | CORK | CORK | SS-615 | Knockduff 110kv Substation | EirGrid | 110000 |  |  | 2.217 | 3 | 2.852 | 2 | 2.139 | 25.2 | 25.2 | 2220340 | 9 | 88108.7302 | 11.3496 | 12.6 | 124.9659
977 | 977 | CL2-591 | CORK | CORK | SS-615 | Knockduff 110kv Substation | EirGrid | 110000 |  |  | 5.262 | 6 | 0.653 | 2 | 0.48975 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424 | 25.2 | 88.1087
978 | 978 | CL2-592 | CORK | CORK | SS-394 | Kilberrihert 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.803 | 5 | 1.052 | 2 | 0.789 | 8.4 | 8.4 | 699140 | 4 | 83230.9524 | 12.0148 | 4.2 | 412.5405
979 | 979 | CL2-593 | CORK | CORK | SS-615 | Knockduff 110kv Substation | EirGrid | 110000 |  |  | 6.156 | 7 | 0.531 | 2 | 0.531 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525 | 8.4 | 83.231
980 | 980 | CL2-594 | CORK | CORK | SS-096 | Boggeragh 110kV Substation | EirGrid | 110000 |  |  | 3.048 | 4 | 0.714 | 2 | 0.5355 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581 | 4.2 | 425.0881
981 | 981 | CL2-595 | KERRY | KERRY | SS-387 | Coolcorcoran 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.706 | 7 | 0.695 | 2 | 0.52125 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 387.4452
982 | 982 | CL2-596 | KILKENNY | LAOIS | SS-372 | Ballyconra 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.376 | 7 | 0.831 | 2 | 0.62325 | 8.4 | 8.4 | 839680 | 4 | 99961.9048 | 10.0038 | 4.2 | 199.9238
983 | 983 | CL2-597 | CLARE | CLARE | SS-116 | Ardnacrusha 110kV Substation | EirGrid | 110000 | low | 110000 | 8.989 | 9 | 1.959 | 2 | 1.4693 | 16.8 | 16.8 | 2227140 | 8 | 132567.8571 | 7.5433 | 8.4 | 99.9619
984 | 984 | CL2-598 | TIPPERARY | TIPPERARY | SS-645 | Toomevara 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.145 | 9 | 0.931 | 2 | 0.69825 | 8.4 | 8.4 | 1379800 | 2 | 164261.9048 | 6.0878 | 16.8 | 132.5679
985 | 985 | CL2-599 | TIPPERARY | TIPPERARY | SS-540 | Templemore 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 6.733 | 7 | 1.102 | 2 | 0.8265 | 8.4 | 8.4 | 839680 | 4 | 99961.9048 | 10.0038 | 8.4 | 164.2619
986 | 986 | CL2-600 | CLARE | CLARE | SS-155 | Booltiagh 110kV Substation | EirGrid | 110000 | low | 110000 | 4.293 | 5 | 2.98 | 2 | 2.235 | 25.2 | 25.2 | 2398000 | 9 | 95158.7302 | 10.5088 | 8.4 | 99.9619
987 | 987 | CL2-601 | CLARE | CLARE | SS-700 | Letteragh 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.955 | 2 | 2.067 | 2 | 1.5503 | 16.8 | 16.8 | 488330 | 4 | 29067.2619 | 34.403 | 25.2 | 95.1587
988 | 988 | CL2-602 | CLARE | CLARE | SS-700 | Letteragh 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.828 | 5 | 0.577 | 2 | 0.577 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 16.8 | 29.0673
989 | 989 | CL2-603 | CLARE | CLARE | SS-700 | Letteragh 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.164 | 3 | 1.953 | 2 | 1.4647 | 16.8 | 16.8 | 558600 | 4 | 33250 | 30.0752 | 4.2 | 166.4619
990 | 990 | CL2-604 | DONEGAL | DONEGAL | SS-289 | Gweedore 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 1.282 | 2 | 1.766 | 2 | 1.3245 | 12.6 | 12.6 | 488330 | 4 | 38756.3492 | 25.8022 | 16.8 | 33.25
991 | 991 | CL2-605 | DONEGAL | DONEGAL | SS-333 | Clady 38kV Substation | ESB Networks | 38000 |  |  | 4.944 | 5 | 0.706 | 2 | 0.5295 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 12.6 | 38.7563
992 | 992 | CL2-606 | DONEGAL | DONEGAL | SS-195 | Cark 110kV Substation | EirGrid | 110000 | low | 110000 | 10.983 | 11 | 0.609 | 2 | 0.609 | 4.2 | 4.2 | 1996170 | 7 | 475278.5714 | 2.104 | 4.2 | 166.4619
993 | 993 | CL2-607 | DONEGAL | DONEGAL | SS-195 | Cark 110kV Substation | EirGrid | 110000 | low | 110000 | 8.739 | 9 | 8.38 | 2 | 6.285 | 75.6 | 75.6 | 2815750 | 11 | 37245.3704 | 26.849 | 4.2 | 475.2786
994 | 994 | CL2-608 | DONEGAL | DONEGAL | SS-196 | Culliagh 110kV Substation | EirGrid | 110000 | low | 110000 | 12.299 | 13 | 4.155 | 2 | 3.1162 | 37.8 | 37.8 | 3400230 | 10 | 89953.1746 | 11.1169 | 75.6 | 37.2454
995 | 995 | CL2-609 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 6.119 | 7 | 8.275 | 2 | 6.2063 | 75.6 | 75.6 | 2394130 | 11 | 31668.3862 | 31.5772 | 37.8 | 89.9532
996 | 996 | CL2-610 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 9.341 | 10 | 1.871 | 2 | 1.4032 | 16.8 | 16.8 | 2297410 | 8 | 136750.5952 | 7.3126 | 75.6 | 31.6684
997 | 997 | CL2-611 | DONEGAL | DONEGAL | SS-686 | Dungloe 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.191 | 8 | 11.635 | 2 | 8.7263 | 105 | 105 | 2604940 | 11 | 24808.9524 | 40.308 | 16.8 | 136.7506
998 | 998 | CL2-612 | DONEGAL | DONEGAL | SS-195 | Cark 110kV Substation | EirGrid | 110000 | low | 110000 | 3.781 | 4 | 5.213 | 2 | 3.9097 | 46.2 | 46.2 | 1761700 | 11 | 38132.0346 | 26.2247 | 105 | 24.809
999 | 999 | CL2-613 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 10.545 | 11 | 1.356 | 2 | 1.017 | 12.6 | 12.6 | 1996170 | 7 | 158426.1905 | 6.3121 | 46.2 | 38.132
1000 | 1000 | CL2-614 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 3.183 | 4 | 1.82 | 2 | 1.365 | 16.8 | 16.8 | 1875790 | 8 | 111654.1667 | 8.9562 | 12.6 | 158.4262
1001 | 1001 | CL2-615 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 7.154 | 8 | 5.444 | 2 | 4.083 | 50.4 | 50.4 | 2604940 | 11 | 51685.3175 | 19.3479 | 16.8 | 111.6542
1002 | 1002 | CL2-616 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.009 | 11 | 21.5 | 2 | 16.125 | 197.4 | 197.4 | 9068760 | 13 | 45941.0334 | 21.767 | 50.4 | 51.6853
1003 | 1003 | CL2-617 | CAVAN | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.397 | 9 | 25.306 | 2 | 18.9795 | 235.2 | 235.2 | 8678360 | 12 | 36897.7891 | 27.1019 | 197.4 | 45.941
1004 | 1004 | CL2-618 | CAVAN | LEITRIM | SS-110 | Corraclassy 110kV Substation | EirGrid | 110000 |  |  | 8.632 | 9 | 22.242 | 2 | 16.6815 | 205.8 | 205.8 | 8678360 | 12 | 42168.9018 | 23.7142 | 235.2 | 36.8978
1005 | 1005 | CL2-619 | LEITRIM | LEITRIM | SS-304 | Arigna 110kV Substation | EirGrid | 110000 | 110000 | 20000 | 7.203 | 8 | 13.323 | 2 | 9.9923 | 121.8 | 121.8 | 2604940 | 11 | 21387.0279 | 46.7573 | 205.8 | 42.1689
1006 | 1006 | CL2-620 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.872 | 7 | 3.573 | 2 | 2.6797 | 29.4 | 29.4 | 969600 | 5 | 32979.5918 | 30.3218 | 121.8 | 21.387
1007 | 1007 | CL2-621 | SLIGO | MAYO | SS-078 | Glenree 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.174 | 6 | 9.971 | 2 | 7.4783 | 92.4 | 92.4 | 2183320 | 11 | 23629.0043 | 42.3209 | 29.4 | 32.9796
1008 | 1008 | CL2-622 | MAYO | MAYO | SS-078 | Glenree 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 2.542 | 3 | 4.992 | 2 | 3.744 | 46.2 | 46.2 | 1550890 | 11 | 33569.0476 | 29.7893 | 92.4 | 23.629
1009 | 1009 | CL2-623 | MAYO | MAYO | SS-170 | Derrynadivva 38kV Substation | ESB Networks | 38000 | low | 38000 | 9.179 | 10 | 0.477 | 2 | 0.477 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 46.2 | 33.569
1010 | 1010 | CL2-624 | MAYO | MAYO | SS-170 | Derrynadivva 38kV Substation | ESB Networks | 38000 | low | 38000 | 6.597 | 7 | 3.673 | 2 | 2.7548 | 33.6 | 33.6 | 1126610 | 6 | 33530.0595 | 29.824 | 4.2 | 330.2714
1011 | 1011 | CL2-625 | MAYO | MAYO | SS-234 | Crossmolina 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.711 | 11 | 0.922 | 2 | 0.6915 | 8.4 | 8.4 | 1485200 | 2 | 176809.5238 | 5.6558 | 33.6 | 33.5301
1012 | 1012 | CL2-626 | MAYO | MAYO | SS-170 | Derrynadivva 38kV Substation | ESB Networks | 38000 | low | 38000 | 10.969 | 11 | 2.295 | 2 | 1.7212 | 21 | 21 | 1120760 | 4 | 53369.5238 | 18.7373 | 8.4 | 176.8095
1013 | 1013 | CL2-627 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.839 | 9 | 7.082 | 2 | 5.3115 | 63 | 63 | 2815750 | 11 | 44694.4444 | 22.3741 | 21 | 53.3695
1014 | 1014 | CL2-628 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.294 | 6 | 0.971 | 2 | 0.72825 | 8.4 | 8.4 | 1732670 | 7 | 206270.2381 | 4.848 | 63 | 44.6944
1015 | 1015 | CL2-629 | DONEGAL | DONEGAL | SS-196 | Culliagh 110kV Substation | EirGrid | 110000 | low | 110000 | 2.449 | 3 | 10.191 | 2 | 7.6433 | 92.4 | 92.4 | 1550890 | 11 | 16784.5238 | 59.5787 | 8.4 | 206.2702
1016 | 1016 | CL2-630 | DONEGAL | DONEGAL | SS-196 | Culliagh 110kV Substation | EirGrid | 110000 | low | 110000 | 6.576 | 7 | 6.468 | 2 | 4.851 | 58.8 | 58.8 | 2394130 | 11 | 40716.4966 | 24.5601 | 92.4 | 16.7845
1017 | 1017 | CL2-631 | DONEGAL | DONEGAL | SS-688 | Clogher 110kV Substation | EirGrid | 110000 |  |  | 7.89 | 8 | 49.464 | 2 | 37.098 | 457.8 | 457.8 | 11877300 | 12 | 25944.2988 | 38.5441 | 58.8 | 40.7165
1018 | 1018 | CL2-632 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 10.091 | 11 | 0.994 | 2 | 0.7455 | 8.4 | 8.4 | 1996170 | 7 | 237639.2857 | 4.2081 | 457.8 | 25.9443
1019 | 1019 | CL2-633 | DONEGAL | DONEGAL | SS-102 | Binbane 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 6.975 | 7 | 1.135 | 2 | 0.85125 | 8.4 | 8.4 | 1785370 | 7 | 212544.0476 | 4.7049 | 8.4 | 237.6393
1020 | 1020 | CL2-634 | DONEGAL | DONEGAL | SS-102 | Binbane 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 3.704 | 4 | 2.873 | 2 | 2.1547 | 25.2 | 25.2 | 2309170 | 9 | 91633.7302 | 10.913 | 8.4 | 212.544
1021 | 1021 | CL2-635 | DONEGAL | DONEGAL | SS-102 | Binbane 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 3.209 | 4 | 2.118 | 2 | 1.5885 | 16.8 | 16.8 | 1875790 | 8 | 111654.1667 | 8.9562 | 25.2 | 91.6337
1022 | 1022 | CL2-636 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.028 | 6 | 3.464 | 2 | 2.598 | 29.4 | 29.4 | 2486830 | 9 | 84586.0544 | 11.8223 | 16.8 | 111.6542
1023 | 1023 | CL2-637 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.277 | 9 | 1.055 | 2 | 0.79125 | 8.4 | 8.4 | 1890770 | 7 | 225091.6667 | 4.4426 | 29.4 | 84.5861
1024 | 1024 | CL2-638 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 7.449 | 8 | 3.654 | 2 | 2.7405 | 33.6 | 33.6 | 2843930 | 10 | 84640.7738 | 11.8146 | 8.4 | 225.0917
1025 | 1025 | CL2-639 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 10.709 | 11 | 2.414 | 2 | 1.8105 | 21 | 21 | 2367680 | 8 | 112746.6667 | 8.8694 | 33.6 | 84.6408
1026 | 1026 | CL2-640 | DONEGAL | DONEGAL | SS-196 | Culliagh 110kV Substation | EirGrid | 110000 | low | 110000 | 10.584 | 11 | 0.63 | 2 | 0.4725 | 4.2 | 4.2 | 1996170 | 7 | 475278.5714 | 2.104 | 21 | 112.7467
1027 | 1027 | CL2-641 | DONEGAL | DONEGAL | SS-572 | Glenties 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.042 | 4 | 0.771 | 2 | 0.57825 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 475.2786
1028 | 1028 | CL2-642 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 3.522 | 4 | 0.721 | 2 | 0.54075 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581 | 4.2 | 149.731
1029 | 1029 | CL2-643 | DONEGAL | DONEGAL | SS-196 | Culliagh 110kV Substation | EirGrid | 110000 | low | 110000 | 8.903 | 9 | 3.074 | 2 | 2.3055 | 25.2 | 25.2 | 2753320 | 9 | 109258.7302 | 9.1526 | 4.2 | 387.4452
1030 | 1030 | CL2-644 | DONEGAL | DONEGAL | SS-196 | Culliagh 110kV Substation | EirGrid | 110000 | low | 110000 | 10.583 | 11 | 2.154 | 2 | 1.6155 | 16.8 | 16.8 | 2367680 | 8 | 140933.3333 | 7.0956 | 25.2 | 109.2587
1031 | 1031 | CL2-645 | DONEGAL | DONEGAL | SS-690 | Stranrolar 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.448 | 9 | 2.303 | 2 | 1.7272 | 21 | 21 | 980220 | 4 | 46677.1429 | 21.4238 | 16.8 | 140.9333
1032 | 1032 | CL2-646 | DONEGAL | DONEGAL | SS-015 | Letterkenny 110kV Station | EirGrid | 110000 | 110000 | 38000 | 3.357 | 4 | 0.839 | 2 | 0.62925 | 8.4 | 8.4 | 1627270 | 7 | 193722.619 | 5.162 | 21 | 46.6771
1033 | 1033 | CL2-647 | GALWAY | GALWAY | SS-131 | Ros a Mh├¡l 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.701 | 3 | 19.051 | 2 | 14.2882 | 176.4 | 176.4 | 4117400 | 12 | 23341.2698 | 42.8426 | 8.4 | 193.7226
1034 | 1034 | CL2-648 | GALWAY | GALWAY | SS-131 | Ros a Mh├¡l 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.584 | 5 | 1.251 | 2 | 0.93825 | 8.4 | 8.4 | 699140 | 4 | 83230.9524 | 12.0148 | 176.4 | 23.3413
1035 | 1035 | CL2-649 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 4.45 | 5 | 1.682 | 2 | 1.2615 | 12.6 | 12.6 | 1679970 | 7 | 133330.9524 | 7.5001 | 8.4 | 83.231
1036 | 1036 | CL2-650 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 8.667 | 9 | 22.649 | 2 | 16.9868 | 210 | 210 | 8678360 | 12 | 41325.5238 | 24.1981 | 12.6 | 133.331
1037 | 1037 | CL2-651 | GALWAY | GALWAY | SS-662 | Cloosh 110kV Substation | EirGrid | 110000 | low | 110000 | 7.89 | 8 | 1.696 | 2 | 1.272 | 12.6 | 12.6 | 1838070 | 7 | 145878.5714 | 6.855 | 210 | 41.3255
1038 | 1038 | CL2-652 | GALWAY | GALWAY | SS-623 | Uggool 110kV Substation | EirGrid | 110000 | 33000 | 110000 | 3.519 | 4 | 0.834 | 2 | 0.6255 | 8.4 | 8.4 | 1627270 | 7 | 193722.619 | 5.162 | 12.6 | 145.8786
1039 | 1039 | CL2-653 | GALWAY | GALWAY | SS-662 | Cloosh 110kV Substation | EirGrid | 110000 | low | 110000 | 2.589 | 3 | 25.74 | 2 | 19.305 | 239.4 | 239.4 | 4117400 | 12 | 17198.8304 | 58.1435 | 8.4 | 193.7226
1040 | 1040 | CL2-654 | GALWAY | GALWAY | SS-638 | Oughterard 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 3.329 | 4 | 1.197 | 2 | 0.89775 | 8.4 | 8.4 | 628870 | 4 | 74865.4762 | 13.3573 | 239.4 | 17.1988
1041 | 1041 | CL2-655 | GALWAY | GALWAY | SS-130 | An Spid├®al 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.846 | 3 | 1.075 | 2 | 0.80625 | 8.4 | 8.4 | 558600 | 4 | 66500 | 15.0376 | 8.4 | 74.8655
1042 | 1042 | CL2-656 | GALWAY | GALWAY | SS-130 | An Spid├®al 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.276 | 7 | 1.671 | 2 | 1.2532 | 12.6 | 12.6 | 839680 | 4 | 66641.2698 | 15.0057 | 8.4 | 66.5
1043 | 1043 | CL2-657 | GALWAY | GALWAY | SS-623 | Uggool 110kV Substation | EirGrid | 110000 | 33000 | 110000 | 3.961 | 4 | 1.133 | 2 | 0.84975 | 8.4 | 8.4 | 1627270 | 7 | 193722.619 | 5.162 | 12.6 | 66.6413
1044 | 1044 | CL2-658 | GALWAY | GALWAY | SS-638 | Oughterard 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 4.181 | 5 | 1.274 | 2 | 0.9555 | 8.4 | 8.4 | 699140 | 4 | 83230.9524 | 12.0148 | 8.4 | 193.7226
1045 | 1045 | CL2-659 | GALWAY | GALWAY | SS-638 | Oughterard 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 5.738 | 6 | 1.018 | 2 | 0.7635 | 8.4 | 8.4 | 769410 | 4 | 91596.4286 | 10.9175 | 8.4 | 83.231
1046 | 1046 | CL2-660 | GALWAY | GALWAY | SS-661 | Knockranny 110kV Substation | EirGrid | 110000 | low | 110000 | 5.111 | 6 | 0.555 | 2 | 0.555 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424 | 8.4 | 91.5964
1047 | 1047 | CL2-661 | GALWAY | GALWAY | SS-038 | Salthill 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 7.797 | 8 | 3.942 | 2 | 2.9565 | 33.6 | 33.6 | 2843930 | 10 | 84640.7738 | 11.8146 | 4.2 | 412.5405
1048 | 1048 | CL2-662 | GALWAY | GALWAY | SS-130 | An Spid├®al 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.215 | 5 | 1.224 | 2 | 0.918 | 8.4 | 8.4 | 699140 | 4 | 83230.9524 | 12.0148 | 33.6 | 84.6408
1049 | 1049 | CL2-663 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.757 | 7 | 7.728 | 2 | 5.796 | 71.4 | 71.4 | 2394130 | 11 | 33531.2325 | 29.8229 | 8.4 | 83.231
1050 | 1050 | CL2-664 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 4.095 | 5 | 13.209 | 2 | 9.9067 | 121.8 | 121.8 | 1972510 | 11 | 16194.6634 | 61.7487 | 71.4 | 33.5312
1051 | 1051 | CL2-665 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 7.269 | 8 | 0.419 | 2 | 0.419 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285 | 121.8 | 16.1947
1052 | 1052 | CL2-666 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 10.046 | 11 | 0.154 | 2 | 0.154 | 4.2 | 4.2 | 1996170 | 7 | 475278.5714 | 2.104 | 4.2 | 437.6357
1053 | 1053 | CL2-667 | MAYO | MAYO | SS-203 | Foxford 38kV Substation | ESB Networks | 38000 |  |  | 4.781 | 5 | 0.473 | 2 | 0.473 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 475.2786
1054 | 1054 | CL2-668 | KERRY | KERRY | SS-636 | Garranebane 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.964 | 5 | 1.081 | 2 | 0.81075 | 8.4 | 8.4 | 699140 | 4 | 83230.9524 | 12.0148 | 4.2 | 166.4619
1055 | 1055 | CL2-669 | CORK | CORK | SS-192 | Ballylickey 110kV Station | EirGrid | 110000 | 110000 | 38000 | 7.155 | 8 | 0.423 | 2 | 0.423 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285 | 8.4 | 83.231
1056 | 1056 | CL2-670 | WATERFORD | WATERFORD | SS-507 | Kilcloher 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.327 | 10 | 1.745 | 2 | 1.3088 | 12.6 | 12.6 | 1469550 | 3 | 116630.9524 | 8.5741 | 4.2 | 437.6357
1057 | 1057 | CL2-671 | TIPPERARY | WATERFORD | SS-455 | Ardfinnan 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.656 | 9 | 15.997 | 2 | 11.9977 | 147 | 147 | 4339180 | 12 | 29518.2313 | 33.8774 | 12.6 | 116.631
1058 | 1058 | CL2-672 | TIPPERARY | WATERFORD | SS-622 | Barranafaddock 38kV Substation | ESB Networks | 38000 | low | 38000 | 9.054 | 10 | 14.646 | 2 | 10.9845 | 134.4 | 134.4 | 4719260 | 12 | 35113.5417 | 28.479 | 147 | 29.5182
1059 | 1059 | CL2-673 | WATERFORD | WATERFORD | SS-659 | Spa Road 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 9.227 | 10 | 27.254 | 2 | 20.4405 | 252 | 252 | 9438520 | 12 | 37454.4444 | 26.6991 | 134.4 | 35.1135
1060 | 1060 | CL2-674 | WATERFORD | WATERFORD | SS-505 | Kilmacthomas 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.714 | 11 | 9.238 | 2 | 6.9285 | 84 | 84 | 3237370 | 11 | 38540.119 | 25.947 | 252 | 37.4544
1061 | 1061 | CL2-675 | WATERFORD | WATERFORD | SS-205 | Dungarvan 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.189 | 9 | 2.043 | 2 | 1.5323 | 16.8 | 16.8 | 2227140 | 8 | 132567.8571 | 7.5433 | 84 | 38.5401
1062 | 1062 | CL2-676 | WATERFORD | WATERFORD | SS-354 | Twomilebridge 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.045 | 5 | 0.938 | 2 | 0.7035 | 8.4 | 8.4 | 699140 | 4 | 83230.9524 | 12.0148 | 16.8 | 132.5679
1063 | 1063 | CL2-677 | WATERFORD | WATERFORD | SS-205 | Dungarvan 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.544 | 6 | 1.893 | 2 | 1.4198 | 16.8 | 16.8 | 2016330 | 8 | 120019.6429 | 8.332 | 8.4 | 83.231
1064 | 1064 | CL2-678 | CORK | LIMERICK | SS-695 | Castlepook 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 2.769 | 3 | 3.638 | 2 | 2.7285 | 33.6 | 33.6 | 681570 | 6 | 20284.8214 | 49.2979 | 16.8 | 120.0196
1065 | 1065 | CL2-679 | LIMERICK | LIMERICK | SS-695 | Castlepook 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 3.413 | 4 | 5.623 | 2 | 4.2172 | 50.4 | 50.4 | 1761700 | 11 | 34954.3651 | 28.6087 | 33.6 | 20.2848
1066 | 1066 | CL2-680 | LIMERICK | LIMERICK | SS-257 | Kilshanny 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.997 | 9 | 0.988 | 2 | 0.741 | 8.4 | 8.4 | 1379800 | 2 | 164261.9048 | 6.0878 | 50.4 | 34.9544
1067 | 1067 | CL2-681 | TIPPERARY | LIMERICK | SS-585 | Kilross Road 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.774 | 12 | 34.698 | 2 | 26.0235 | 323.4 | 323.4 | 9726200 | 13 | 30074.8299 | 33.2504 | 8.4 | 164.2619
1068 | 1068 | CL2-682 | CORK | CORK | SS-583 | Castletownroche 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.658 | 6 | 8.344 | 2 | 6.258 | 75.6 | 75.6 | 2183320 | 11 | 28879.8942 | 34.6262 | 323.4 | 30.0748
1069 | 1069 | CL2-683 | CARLOW | WEXFORD | SS-492 | Graigue 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.1 | 11 | 8.837 | 2 | 6.6277 | 79.8 | 79.8 | 3237370 | 11 | 40568.5464 | 24.6496 | 75.6 | 28.8799
1070 | 1070 | CL2-684 | TIPPERARY | TIPPERARY | SS-645 | Toomevara 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.419 | 9 | 1.49 | 2 | 1.1175 | 12.6 | 12.6 | 1416850 | 3 | 112448.4127 | 8.893 | 79.8 | 40.5685
1071 | 1071 | CL2-685 | CORK | CORK | SS-263 | Lake 38kV Station | ESB Networks | 38000 | 38000 | low | 9.744 | 10 | 0.921 | 2 | 0.69075 | 8.4 | 8.4 | 1432500 | 2 | 170535.7143 | 5.8639 | 12.6 | 112.4484
1072 | 1072 | CL2-686 | KILKENNY | KILKENNY | SS-016 | Portlaw 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.135 | 10 | 1.193 | 2 | 0.89475 | 8.4 | 8.4 | 1432500 | 2 | 170535.7143 | 5.8639 | 8.4 | 170.5357
1073 | 1073 | CL2-687 | CORK | CORK | SS-355 | Carrigcannon 38kV Substation | ESB Networks | 38000 | low | 38000 | 7.44 | 8 | 6.798 | 2 | 5.0985 | 63 | 63 | 2604940 | 11 | 41348.254 | 24.1848 | 8.4 | 170.5357
1074 | 1074 | CL2-688 | KERRY | KERRY | SS-555 | Ballybunion 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.158 | 8 | 0.47 | 2 | 0.47 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 63 | 41.3483
1075 | 1075 | CL2-689 | KERRY | KERRY | SS-555 | Ballybunion 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.436 | 7 | 0.55 | 2 | 0.55 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 216.6548
1076 | 1076 | CL2-690 | TIPPERARY | TIPPERARY | SS-295 | Doon 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.204 | 9 | 8.931 | 2 | 6.6982 | 79.8 | 79.8 | 2815750 | 11 | 35285.0877 | 28.3406 | 4.2 | 199.9238
1077 | 1077 | CL2-691 | WICKLOW | WICKLOW | SS-037 | Ballybeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.761 | 6 | 0.362 | 2 | 0.362 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424 | 79.8 | 35.2851
1078 | 1078 | CL2-692 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 17.052 | 18 | 6.733 | 2 | 5.0497 | 58.8 | 58.8 | 4713040 | 11 | 80153.7415 | 12.476 | 4.2 | 412.5405
1079 | 1079 | CL2-693 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.556 | 16 | 2.749 | 2 | 2.0617 | 25.2 | 25.2 | 1769070 | 5 | 70201.1905 | 14.2448 | 58.8 | 80.1537
1080 | 1080 | CL2-694 | CORK | CORK | SS-668 | Coomataggart 110 kV Substation | EirGrid | 110000 | low | 110000 | 10.289 | 11 | 1.232 | 2 | 0.924 | 8.4 | 8.4 | 1996170 | 7 | 237639.2857 | 4.2081 | 25.2 | 70.2012
1081 | 1081 | CL2-695 | CORK | CORK | SS-433 | Lee Bridge 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.377 | 13 | 0.49 | 2 | 0.49 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718 | 8.4 | 237.6393
1082 | 1082 | CL2-696 | KILKENNY | KILKENNY | SS-538 | Galmoy 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.689 | 10 | 2.129 | 2 | 1.5968 | 16.8 | 16.8 | 1050490 | 4 | 62529.1667 | 15.9925 | 4.2 | 367.9143
1083 | 1083 | CL2-697 | WICKLOW | WICKLOW | SS-699 | Ballycumber 38kV Substation | ESB Networks | 38000 | low | 38000 | 5.519 | 6 | 1.628 | 2 | 1.221 | 12.6 | 12.6 | 769410 | 4 | 61064.2857 | 16.3762 | 16.8 | 62.5292
1084 | 1084 | CL2-698 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 3.63 | 4 | 1.1 | 2 | 0.825 | 8.4 | 8.4 | 628870 | 4 | 74865.4762 | 13.3573 | 12.6 | 61.0643
1085 | 1085 | CL2-699 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.717 | 6 | 0.573 | 2 | 0.573 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 8.4 | 74.8655
1086 | 1086 | CL2-700 | CLARE | CLARE | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.867 | 15 | 0.84 | 2 | 0.63 | 8.4 | 8.4 | 1696000 | 2 | 201904.7619 | 4.9528 | 4.2 | 183.1929
1087 | 1087 | CL2-701 | GALWAY | GALWAY | SS-103 | Claregalway 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.009 | 7 | 0.541 | 2 | 0.541 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 8.4 | 201.9048
1088 | 1088 | CL2-702 | KERRY | KERRY | SS-189 | Knockearagh 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.998 | 6 | 0.826 | 2 | 0.6195 | 8.4 | 8.4 | 1732670 | 7 | 206270.2381 | 4.848 | 4.2 | 199.9238
1089 | 1089 | CL2-703 | WEXFORD | WEXFORD | SS-616 | Ballinvally 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 7.37 | 8 | 0.574 | 2 | 0.574 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 8.4 | 206.2702
1090 | 1090 | CL2-704 | CORK | CORK | SS-261 | Milane Hill 38kV Station | ESB Networks | 38000 |  |  | 6.406 | 7 | 3.164 | 2 | 2.373 | 29.4 | 29.4 | 969600 | 5 | 32979.5918 | 30.3218 | 4.2 | 216.6548
1091 | 1091 | CL2-705 | CORK | CORK | SS-261 | Milane Hill 38kV Station | ESB Networks | 38000 |  |  | 5.394 | 6 | 1.154 | 2 | 0.8655 | 8.4 | 8.4 | 769410 | 4 | 91596.4286 | 10.9175 | 29.4 | 32.9796
1092 | 1092 | CL2-706 | CLARE | CLARE | SS-155 | Booltiagh 110kV Substation | EirGrid | 110000 | low | 110000 | 7.941 | 8 | 0.66 | 2 | 0.495 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285 | 8.4 | 91.5964
1093 | 1093 | CL2-707 | CLARE | CLARE | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.93 | 11 | 2.713 | 2 | 2.0347 | 25.2 | 25.2 | 1324920 | 5 | 52576.1905 | 19.02 | 4.2 | 437.6357
1094 | 1094 | CL2-708 | GALWAY | CLARE | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.833 | 14 | 10.364 | 2 | 7.773 | 96.6 | 96.6 | 3869800 | 11 | 40060.0414 | 24.9625 | 25.2 | 52.5762
1095 | 1095 | CL2-709 | CLARE | CLARE | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.536 | 15 | 1.257 | 2 | 0.94275 | 8.4 | 8.4 | 1696000 | 2 | 201904.7619 | 4.9528 | 96.6 | 40.06
1096 | 1096 | CL2-710 | CLARE | CLARE | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.802 | 15 | 0.588 | 2 | 0.588 | 4.2 | 4.2 | 1650640 | 1 | 393009.5238 | 2.5445 | 8.4 | 201.9048
1097 | 1097 | CL2-711 | CLARE | CLARE | SS-595 | Kilkee 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.438 | 7 | 0.956 | 2 | 0.717 | 8.4 | 8.4 | 839680 | 4 | 99961.9048 | 10.0038 | 4.2 | 393.0095
1098 | 1098 | CL2-712 | CORK | CORK | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.471 | 5 | 0.35 | 2 | 0.35 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 8.4 | 99.9619
1099 | 1099 | CL2-713 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 16.505 | 17 | 0.648 | 2 | 0.486 | 4.2 | 4.2 | 1756040 | 1 | 418104.7619 | 2.3917 | 4.2 | 166.4619
1100 | 1100 | CL2-714 | KILKENNY | KILKENNY | SS-489 | Ballyhale 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.31 | 7 | 2.014 | 2 | 1.5105 | 16.8 | 16.8 | 839680 | 4 | 49980.9524 | 20.0076 | 4.2 | 418.1048
1101 | 1101 | CL2-715 | KILKENNY | KILKENNY | SS-492 | Graigue 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.463 | 5 | 6.231 | 2 | 4.6732 | 54.6 | 54.6 | 1972510 | 11 | 36126.5568 | 27.6805 | 16.8 | 49.981
1102 | 1102 | CL2-716 | TIPPERARY | TIPPERARY | SS-692 | Hollyford 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.453 | 4 | 1.807 | 2 | 1.3552 | 16.8 | 16.8 | 628870 | 4 | 37432.7381 | 26.7146 | 54.6 | 36.1266
1103 | 1103 | CL2-717 | WICKLOW | WICKLOW | SS-591 | Shillelagh 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.626 | 4 | 0.83 | 2 | 0.6225 | 8.4 | 8.4 | 628870 | 4 | 74865.4762 | 13.3573 | 16.8 | 37.4327
1104 | 1104 | CL2-718 | CLARE | CLARE | SS-503 | Scariff 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.134 | 9 | 11.769 | 2 | 8.8268 | 109.2 | 109.2 | 2815750 | 11 | 25785.2564 | 38.7819 | 8.4 | 74.8655
1105 | 1105 | CL2-719 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 19.151 | 20 | 0.572 | 2 | 0.572 | 4.2 | 4.2 | 1914140 | 1 | 455747.619 | 2.1942 | 109.2 | 25.7853
1106 | 1106 | CL2-720 | WICKLOW | WICKLOW | SS-699 | Ballycumber 38kV Substation | ESB Networks | 38000 | low | 38000 | 5.256 | 6 | 1.15 | 2 | 0.8625 | 8.4 | 8.4 | 769410 | 4 | 91596.4286 | 10.9175 | 4.2 | 455.7476
1107 | 1107 | CL2-721 | WICKLOW | WICKLOW | SS-699 | Ballycumber 38kV Substation | ESB Networks | 38000 | low | 38000 | 7.51 | 8 | 1.344 | 2 | 1.008 | 8.4 | 8.4 | 909950 | 4 | 108327.381 | 9.2313 | 8.4 | 91.5964
1108 | 1108 | CL2-722 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.758 | 9 | 0.803 | 2 | 0.60225 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 8.4 | 108.3274
1109 | 1109 | CL2-723 | CORK | CORK | SS-032 | Mallow 110kV Substation | EirGrid | 110000 |  |  | 5.929 | 6 | 0.979 | 2 | 0.73425 | 8.4 | 8.4 | 1732670 | 7 | 206270.2381 | 4.848 | 4.2 | 317.7238
1110 | 1110 | CL2-724 | LAOIS | LAOIS | SS-034 | Athy 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 9.25 | 10 | 0.67 | 2 | 0.5025 | 4.2 | 4.2 | 1943470 | 7 | 462730.9524 | 2.1611 | 8.4 | 206.2702
1111 | 1111 | CL2-725 | TIPPERARY | TIPPERARY | SS-483 | Birdhill 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.118 | 9 | 2.535 | 2 | 1.9013 | 21 | 21 | 980220 | 4 | 46677.1429 | 21.4238 | 4.2 | 462.731
1112 | 1112 | CL2-726 | WICKLOW | WICKLOW | SS-602 | Avoca 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.08 | 8 | 1.021 | 2 | 0.76575 | 8.4 | 8.4 | 909950 | 4 | 108327.381 | 9.2313 | 21 | 46.6771
1113 | 1113 | CL2-727 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.398 | 12 | 1.42 | 2 | 1.065 | 12.6 | 12.6 | 1574950 | 3 | 124996.0317 | 8.0003 | 8.4 | 108.3274
1114 | 1114 | CL2-728 | CORK | CORK | SS-192 | Ballylickey 110kV Station | EirGrid | 110000 | 110000 | 38000 | 6.624 | 7 | 1.049 | 2 | 0.78675 | 8.4 | 8.4 | 1785370 | 7 | 212544.0476 | 4.7049 | 12.6 | 124.996
1115 | 1115 | CL2-729 | DONEGAL | DONEGAL | SS-087 | Cliff 110kV Substation | EirGrid | 110000 | low | 110000 | 8.224 | 9 | 0.9 | 2 | 0.675 | 8.4 | 8.4 | 1890770 | 7 | 225091.6667 | 4.4426 | 8.4 | 212.544
1116 | 1116 | CL2-730 | CLARE | CLARE | SS-669 | 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.823 | 4 | 0.771 | 2 | 0.57825 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 8.4 | 225.0917
1117 | 1117 | CL2-731 | DONEGAL | DONEGAL | SS-138 | Creeslough 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.05 | 8 | 5.658 | 2 | 4.2435 | 50.4 | 50.4 | 2604940 | 11 | 51685.3175 | 19.3479 | 4.2 | 149.731
1118 | 1118 | CL2-732 | DONEGAL | DONEGAL | SS-610 | Milford (North) 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.318 | 7 | 4.809 | 2 | 3.6067 | 42 | 42 | 1126610 | 6 | 26824.0476 | 37.28 | 50.4 | 51.6853
1119 | 1119 | CL2-733 | DONEGAL | DONEGAL | SS-610 | Milford (North) 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.616 | 9 | 0.667 | 2 | 0.50025 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 42 | 26.824
1120 | 1120 | CL2-734 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.84 | 9 | 7.362 | 2 | 5.5215 | 67.2 | 67.2 | 2815750 | 11 | 41901.0417 | 23.8658 | 4.2 | 317.7238
1121 | 1121 | CL2-735 | GALWAY | GALWAY | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 9.976 | 10 | 0.556 | 2 | 0.556 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 67.2 | 41.901
1122 | 1122 | CL2-736 | MAYO | MAYO | SS-234 | Crossmolina 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.066 | 11 | 2.484 | 2 | 1.863 | 21 | 21 | 1120760 | 4 | 53369.5238 | 18.7373 | 4.2 | 330.2714
1123 | 1123 | CL2-737 | DONEGAL | DONEGAL | SS-272 | Carndonagh 38kV | ESB Networks | 38000 | 38000 | low | 9.683 | 10 | 0.416 | 2 | 0.416 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 21 | 53.3695
1124 | 1124 | CL2-738 | MAYO | MAYO | SS-710 | Tawnaghmore 110kV Substation | EirGrid | 110000 | low | 110000 | 9.218 | 10 | 1.607 | 2 | 1.2052 | 12.6 | 12.6 | 1943470 | 7 | 154243.6508 | 6.4832 | 4.2 | 330.2714
1125 | 1125 | CL2-739 | MAYO | MAYO | SS-317 | Newport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.382 | 6 | 1.657 | 2 | 1.2428 | 12.6 | 12.6 | 769410 | 4 | 61064.2857 | 16.3762 | 12.6 | 154.2437
1126 | 1126 | CL2-740 | MAYO | MAYO | SS-710 | Tawnaghmore 110kV Substation | EirGrid | 110000 | low | 110000 | 9.807 | 10 | 0.62 | 2 | 0.465 | 4.2 | 4.2 | 1943470 | 7 | 462730.9524 | 2.1611 | 12.6 | 61.0643
1127 | 1127 | CL2-741 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.17 | 10 | 3.564 | 2 | 2.673 | 29.4 | 29.4 | 1236090 | 5 | 42043.8776 | 23.7847 | 4.2 | 462.731
1128 | 1128 | CL2-742 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 2.84 | 3 | 2.34 | 2 | 1.755 | 21 | 21 | 558600 | 4 | 26600 | 37.594 | 29.4 | 42.0439
1129 | 1129 | CL2-743 | MAYO | MAYO | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 11.439 | 12 | 0.471 | 2 | 0.471 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 21 | 26.6
1130 | 1130 | CL2-744 | MAYO | MAYO | SS-431 | Knockaphunta 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.177 | 11 | 0.772 | 2 | 0.579 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 355.3667
1131 | 1131 | CL2-745 | SLIGO | SLIGO | SS-206 | Boyle 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 9.975 | 10 | 1.502 | 2 | 1.1265 | 12.6 | 12.6 | 1469550 | 3 | 116630.9524 | 8.5741 | 4.2 | 342.819
1132 | 1132 | CL2-746 | SLIGO | SLIGO | SS-068 | Ballymote 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.068 | 9 | 1.061 | 2 | 0.79575 | 8.4 | 8.4 | 1379800 | 2 | 164261.9048 | 6.0878 | 12.6 | 116.631
1133 | 1133 | CL2-747 | MAYO | MAYO | SS-203 | Foxford 38kV Substation | ESB Networks | 38000 |  |  | 6.805 | 7 | 1.252 | 2 | 0.939 | 8.4 | 8.4 | 839680 | 4 | 99961.9048 | 10.0038 | 8.4 | 164.2619
1134 | 1134 | CL2-748 | ROSCOMMON | SLIGO | SS-206 | Boyle 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 4.797 | 5 | 0.311 | 2 | 0.311 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 8.4 | 99.9619
1135 | 1135 | CL2-749 | SLIGO | LEITRIM | SS-042 | Ballytivnan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.937 | 9 | 8.012 | 2 | 6.009 | 71.4 | 71.4 | 2815750 | 11 | 39436.2745 | 25.3574 | 4.2 | 166.4619
1136 | 1136 | CL2-750 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.145 | 5 | 1.036 | 2 | 0.777 | 8.4 | 8.4 | 699140 | 4 | 83230.9524 | 12.0148 | 71.4 | 39.4363
1137 | 1137 | CL2-751 | SLIGO | SLIGO | SS-031 | Sligo 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.786 | 6 | 2.057 | 2 | 1.5427 | 16.8 | 16.8 | 2016330 | 8 | 120019.6429 | 8.332 | 8.4 | 83.231
1138 | 1138 | CL2-752 | MAYO | MAYO | SS-173 | Charlestown 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.582 | 4 | 0.339 | 2 | 0.339 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 16.8 | 120.0196
1139 | 1139 | CL2-753 | GALWAY | GALWAY | SS-109 | Cloon 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 12.167 | 13 | 0.426 | 2 | 0.426 | 4.2 | 4.2 | 2101570 | 7 | 500373.8095 | 1.9985 | 4.2 | 149.731
1140 | 1140 | CL2-754 | WESTMEATH | WESTMEATH | SS-246 | Loughanalla 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.019 | 9 | 0.8 | 2 | 0.6 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 500.3738
1141 | 1141 | CL2-755 | GALWAY | GALWAY | SS-598 | Glennamaddy 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.377 | 6 | 1.208 | 2 | 0.906 | 8.4 | 8.4 | 769410 | 4 | 91596.4286 | 10.9175 | 4.2 | 317.7238
1142 | 1142 | CL2-756 | GALWAY | GALWAY | SS-598 | Glennamaddy 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.704 | 9 | 1.645 | 2 | 1.2338 | 12.6 | 12.6 | 1416850 | 3 | 112448.4127 | 8.893 | 8.4 | 91.5964
1143 | 1143 | CL2-757 | GALWAY | GALWAY | SS-549 | Tuam North 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.078 | 9 | 0.562 | 2 | 0.562 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 12.6 | 112.4484
1144 | 1144 | CL2-758 | MAYO | MAYO | SS-431 | Knockaphunta 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.1 | 13 | 0.475 | 2 | 0.475 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718 | 4.2 | 317.7238
1145 | 1145 | CL2-759 | MAYO | MAYO | SS-640 | Ballinrobe 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.264 | 12 | 0.182 | 2 | 0.182 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 367.9143
1146 | 1146 | CL2-760 | DONEGAL | DONEGAL | SS-574 | Convoy 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.32 | 6 | 0.995 | 2 | 0.74625 | 8.4 | 8.4 | 769410 | 4 | 91596.4286 | 10.9175 | 4.2 | 355.3667
1147 | 1147 | CL2-761 | DONEGAL | DONEGAL | SS-686 | Dungloe 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.467 | 4 | 0.775 | 2 | 0.58125 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 8.4 | 91.5964
1148 | 1148 | CL2-762 | DONEGAL | DONEGAL | SS-139 | Gortlee 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.034 | 7 | 0.65 | 2 | 0.4875 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 149.731
1149 | 1149 | CL2-763 | DONEGAL | DONEGAL | SS-272 | Carndonagh 38kV | ESB Networks | 38000 | 38000 | low | 7.54 | 8 | 18.38 | 2 | 13.785 | 168 | 168 | 3959100 | 12 | 23566.0714 | 42.4339 | 4.2 | 199.9238
1150 | 1150 | CL2-764 | DONEGAL | DONEGAL | SS-239 | Moville 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.28 | 9 | 0.229 | 2 | 0.229 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 168 | 23.5661
1151 | 1151 | CL2-765 | DONEGAL | DONEGAL | SS-138 | Creeslough 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.879 | 4 | 0.765 | 2 | 0.57375 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 317.7238
1152 | 1152 | CL2-766 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.391 | 3 | 0.399 | 2 | 0.399 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 149.731
1153 | 1153 | CL2-767 | MAYO | MAYO | SS-317 | Newport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.382 | 12 | 0.148 | 2 | 0.148 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 133
1154 | 1154 | CL3-001 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 13.336 | 14 | 0.147 | 3 | 0.147 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284 | 4.2 | 355.3667
1155 | 1155 | CL3-002 | WICKLOW | WICKLOW | SS-597 | Kilmartin 38kV Substation | ESB Networks | 38000 | 38000 | low | 1.523 | 2 | 0.299 | 3 | 0.299 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007 | 4.2 | 380.4619
1156 | 1156 | CL3-003 | WEXFORD | WEXFORD | SS-493 | Enniscorthy 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.388 | 7 | 0.165 | 3 | 0.165 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 116.269
1158 | 1158 | CL3-005 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 8.094 | 9 | 0.146 | 3 | 0.146 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 199.9238
1159 | 1159 | CL3-006 | KERRY | KERRY | SS-321 | Milltown 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.111 | 8 | 0.202 | 3 | 0.202 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 317.7238
1160 | 1160 | CL3-007 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.183 | 7 | 0.101 | 3 | 0.101 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 216.6548
1161 | 1161 | CL3-008 | LIMERICK | LIMERICK | SS-144 | Monateen 110kV Substation | EirGrid | 110000 |  |  | 7.154 | 8 | 0.267 | 3 | 0.267 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285 | 4.2 | 199.9238
1162 | 1162 | CL3-009 | CLARE | CLARE | SS-176 | Shannon 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.112 | 8 | 0.1 | 3 | 0.1 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 437.6357
1163 | 1163 | CL3-010 | CLARE | CLARE | SS-673 | Drumquin 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 1.467 | 2 | 0.116 | 3 | 0.116 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007 | 4.2 | 216.6548
1164 | 1164 | CL3-011 | ROSCOMMON | ROSCOMMON | SS-206 | Boyle 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.361 | 9 | 0.099 | 3 | 0.099 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 116.269
1165 | 1165 | CL3-012 | TIPPERARY | TIPPERARY | SS-300 | Lisheen 110kV Substation | EirGrid | 110000 | 110000 | low | 4.105 | 5 | 0.204 | 3 | 0.204 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5 | 4.2 | 317.7238
1166 | 1166 | CL3-013 | KILKENNY | KILKENNY | SS-300 | Lisheen 110kV Substation | EirGrid | 110000 | 110000 | low | 4.596 | 5 | 0.181 | 3 | 0.181 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5 | 4.2 | 399.9929
1167 | 1167 | CL3-014 | WATERFORD | WATERFORD | SS-016 | Portlaw 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.186 | 3 | 0.22 | 3 | 0.22 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 399.9929
1168 | 1168 | CL3-015 | LIMERICK | LIMERICK | SS-590 | Bruff 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.331 | 6 | 0.354 | 3 | 0.354 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 133
1169 | 1169 | CL3-016 | CLARE | CLARE | SS-116 | Ardnacrusha 110kV Substation | EirGrid | 110000 | low | 110000 | 6.578 | 7 | 0.134 | 3 | 0.134 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525 | 4.2 | 183.1929
1170 | 1170 | CL3-017 | CLARE | CLARE | SS-141 | Ennis North 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 6.296 | 7 | 0.096 | 3 | 0.096 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 425.0881
1171 | 1171 | CL3-018 | CLARE | CLARE | SS-012 | Ennis 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 10.652 | 11 | 0.113 | 3 | 0.113 | 4.2 | 4.2 | 1996170 | 7 | 475278.5714 | 2.104 | 4.2 | 199.9238
1172 | 1172 | CL3-019 | CLARE | CLARE | SS-483 | Birdhill 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.435 | 8 | 0.207 | 3 | 0.207 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 475.2786
1173 | 1173 | CL3-020 | GALWAY | GALWAY | SS-439 | Loughrea 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.188 | 7 | 0.306 | 3 | 0.306 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 216.6548
1174 | 1174 | CL3-021 | ROSCOMMON | ROSCOMMON | SS-502 | Ballinasloe 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 4.33 | 5 | 0.113 | 3 | 0.113 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 199.9238
1175 | 1175 | CL3-022 | GALWAY | GALWAY | SS-269 | Shannonbridge 110kV Substation | EirGrid | 110000 | low | 110000 | 4.203 | 5 | 0.103 | 3 | 0.103 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5 | 4.2 | 166.4619
1176 | 1176 | CL3-023 | OFFALY | OFFALY | SS-269 | Shannonbridge 110kV Substation | EirGrid | 110000 | low | 110000 | 4.168 | 5 | 0.148 | 3 | 0.148 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5 | 4.2 | 399.9929
1177 | 1177 | CL3-024 | ROSCOMMON | ROSCOMMON | SS-269 | Shannonbridge 110kV Substation | EirGrid | 110000 | low | 110000 | 1.979 | 2 | 0.121 | 3 | 0.121 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341 | 4.2 | 399.9929
1178 | 1178 | CL3-025 | OFFALY | OFFALY | SS-269 | Shannonbridge 110kV Substation | EirGrid | 110000 | low | 110000 | 3.874 | 4 | 0.333 | 3 | 0.333 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581 | 4.2 | 319.0667
1179 | 1179 | CL3-026 | OFFALY | OFFALY | SS-269 | Shannonbridge 110kV Substation | EirGrid | 110000 | low | 110000 | 10.09 | 11 | 0.146 | 3 | 0.146 | 4.2 | 4.2 | 1996170 | 7 | 475278.5714 | 2.104 | 4.2 | 387.4452
1180 | 1180 | CL3-027 | MEATH | MEATH | SS-701 | Clarkstown 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.228 | 5 | 0.11 | 3 | 0.11 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 475.2786
1181 | 1181 | CL3-028 | LONGFORD | LONGFORD | SS-575 | Aghamore 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.431 | 5 | 0.117 | 3 | 0.117 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 166.4619
1182 | 1182 | CL3-029 | OFFALY | OFFALY | SS-084 | Birr 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.398 | 4 | 0.097 | 3 | 0.097 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 166.4619
1183 | 1183 | CL3-030 | KILDARE | OFFALY | SS-657 | Edenderry 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.316 | 3 | 0.121 | 3 | 0.121 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 149.731
1184 | 1184 | CL3-031 | KILDARE | KILDARE | SS-216 | Blake 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 6.153 | 7 | 0.244 | 3 | 0.244 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525 | 4.2 | 133
1185 | 1185 | CL3-032 | OFFALY | OFFALY | SS-657 | Edenderry 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.141 | 5 | 0.274 | 3 | 0.274 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 425.0881
1186 | 1186 | CL3-033 | OFFALY | OFFALY | SS-530 | Esker 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 2.329 | 3 | 0.246 | 3 | 0.246 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674 | 4.2 | 166.4619
1187 | 1187 | CL3-034 | OFFALY | OFFALY | SS-168 | Derryiron 110kV Substation | EirGrid | 110000 |  |  | 4.344 | 5 | 0.23 | 3 | 0.23 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5 | 4.2 | 374.8976
1188 | 1188 | CL3-035 | OFFALY | OFFALY | SS-168 | Derryiron 110kV Substation | EirGrid | 110000 |  |  | 4.892 | 5 | 0.249 | 3 | 0.249 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5 | 4.2 | 399.9929
1189 | 1189 | CL3-036 | OFFALY | OFFALY | SS-530 | Esker 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 5.568 | 6 | 0.129 | 3 | 0.129 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424 | 4.2 | 399.9929
1190 | 1190 | CL3-037 | TIPPERARY | TIPPERARY | SS-053 | Ikerrin 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 1.101 | 2 | 0.225 | 3 | 0.225 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341 | 4.2 | 412.5405
1191 | 1191 | CL3-038 | KILDARE | MEATH | SS-228 | Dunfierth 110kV Substation | EirGrid | 110000 | 110000 | 20000 | 1.976 | 2 | 0.121 | 3 | 0.121 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341 | 4.2 | 319.0667
1192 | 1192 | CL3-039 | MEATH | MEATH | SS-701 | Clarkstown 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.488 | 6 | 0.202 | 3 | 0.202 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 319.0667
1193 | 1193 | CL3-040 | LOUTH | LOUTH | SS-544 | Ballybailie 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.062 | 4 | 0.404 | 3 | 0.404 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 183.1929
1194 | 1194 | CL3-041 | DONEGAL | DONEGAL | SS-289 | Gweedore 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.141 | 6 | 0.181 | 3 | 0.181 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 149.731
1195 | 1195 | CL3-042 | DONEGAL | DONEGAL | SS-689 |  | ESB Networks | 38000 |  |  | 9.314 | 10 | 0.125 | 3 | 0.125 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 4.2 | 183.1929
1196 | 1196 | CL3-043 | GALWAY | GALWAY | SS-175 | Ballygar 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.664 | 7 | 0.222 | 3 | 0.222 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 330.2714
1197 | 1197 | CL3-044 | WESTMEATH | WESTMEATH | SS-229 | Mullingar 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.615 | 6 | 0.196 | 3 | 0.196 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424 | 4.2 | 199.9238
1198 | 1198 | CL3-045 | SLIGO | SLIGO | SS-095 | Collooney 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 2.349 | 3 | 0.134 | 3 | 0.134 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 412.5405
1199 | 1199 | CL3-046 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 7.184 | 8 | 0.142 | 3 | 0.142 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 133
1200 | 1200 | CL3-047 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 7.082 | 8 | 0.145 | 3 | 0.145 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 216.6548
1201 | 1201 | CL3-048 | WATERFORD | WATERFORD | SS-064 | Ballydine 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 3.259 | 4 | 0.262 | 3 | 0.262 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581 | 4.2 | 216.6548
1202 | 1202 | CL3-049 | TIPPERARY | TIPPERARY | SS-347 | Glengoole 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.042 | 6 | 0.193 | 3 | 0.193 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 387.4452
1203 | 1203 | CL3-050 | OFFALY | OFFALY | SS-551 | Dallow 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 2.951 | 3 | 0.292 | 3 | 0.292 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674 | 4.2 | 183.1929
1204 | 1204 | CL3-051 | OFFALY | OFFALY | SS-551 | Dallow 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 3.801 | 4 | 0.203 | 3 | 0.203 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581 | 4.2 | 374.8976
1205 | 1205 | CL3-052 | WESTMEATH | WESTMEATH | SS-652 | Garrycastle 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 5.346 | 6 | 0.091 | 3 | 0.091 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 387.4452
1206 | 1206 | CL3-053 | CLARE | CLARE | SS-141 | Ennis North 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 12.035 | 13 | 0.113 | 3 | 0.113 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718 | 4.2 | 183.1929
1207 | 1207 | CL3-054 | CLARE | CLARE | SS-141 | Ennis North 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 5.235 | 6 | 0.366 | 3 | 0.366 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 367.9143
1208 | 1208 | CL3-055 | KILDARE | KILDARE | SS-034 | Athy 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.505 | 6 | 0.113 | 3 | 0.113 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424 | 4.2 | 183.1929
1209 | 1209 | CL3-056 | KILDARE | KILDARE | SS-034 | Athy 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.41 | 6 | 0.223 | 3 | 0.223 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424 | 4.2 | 412.5405
1210 | 1210 | CL3-057 | WATERFORD | WATERFORD | SS-532 | Woodhouse 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 6.67 | 7 | 0.1 | 3 | 0.1 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525 | 4.2 | 412.5405
1211 | 1211 | CL3-058 | KILKENNY | KILKENNY | SS-098 | Callan 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.394 | 4 | 0.288 | 3 | 0.288 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 425.0881
1212 | 1212 | CL3-059 | LAOIS | LAOIS | SS-486 | Castlecomer 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.864 | 8 | 0.326 | 3 | 0.326 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 149.731
1213 | 1213 | CL3-060 | TIPPERARY | TIPPERARY | SS-459 | Ballycrossaun 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.053 | 14 | 0.31 | 3 | 0.31 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284 | 4.2 | 216.6548
1214 | 1214 | CL3-061 | TIPPERARY | TIPPERARY | SS-325 | Kyleeragh 38kV Substation | ESB Networks | 38000 | 38000 | low | 16.259 | 17 | 0.114 | 3 | 0.114 | 4.2 | 4.2 | 1756040 | 1 | 418104.7619 | 2.3917 | 4.2 | 380.4619
1215 | 1215 | CL3-062 | CLARE | CLARE | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.444 | 12 | 0.372 | 3 | 0.372 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 418.1048
1216 | 1216 | CL3-063 | TIPPERARY | TIPPERARY | SS-325 | Kyleeragh 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.841 | 11 | 0.12 | 3 | 0.12 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 355.3667
1217 | 1217 | CL3-064 | KILDARE | KILDARE | SS-216 | Blake 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 4.437 | 5 | 0.119 | 3 | 0.119 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5 | 4.2 | 342.819
1218 | 1218 | CL3-065 | KILDARE | KILDARE | SS-216 | Blake 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 2.978 | 3 | 0.164 | 3 | 0.164 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674 | 4.2 | 399.9929
1219 | 1219 | CL3-066 | GALWAY | GALWAY | SS-236 | Creagh 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.488 | 11 | 0.092 | 3 | 0.092 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 374.8976
1220 | 1220 | CL3-067 | TIPPERARY | TIPPERARY | SS-594 | Kill Hill 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 6.45 | 7 | 0.238 | 3 | 0.238 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525 | 4.2 | 342.819
1221 | 1221 | CL3-068 | LAOIS | LAOIS | SS-372 | Ballyconra 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.53 | 9 | 0.123 | 3 | 0.123 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 425.0881
1222 | 1222 | CL3-069 | LAOIS | LAOIS | SS-372 | Ballyconra 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.216 | 9 | 0.093 | 3 | 0.093 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 317.7238
1223 | 1223 | CL3-070 | LAOIS | LAOIS | SS-464 | Rathdowney 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.529 | 9 | 0.405 | 3 | 0.405 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 317.7238
1224 | 1224 | CL3-071 | CLARE | CLARE | SS-141 | Ennis North 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 11.773 | 12 | 0.2 | 3 | 0.2 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 317.7238
1225 | 1225 | CL3-072 | GALWAY | GALWAY | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.114 | 5 | 0.18 | 3 | 0.18 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 355.3667
1226 | 1226 | CL3-073 | OFFALY | OFFALY | SS-231 | Lumcloon 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.559 | 11 | 0.157 | 3 | 0.157 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 166.4619
1227 | 1227 | CL3-074 | OFFALY | OFFALY | SS-231 | Lumcloon 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.69 | 11 | 0.135 | 3 | 0.135 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 342.819
1228 | 1228 | CL3-075 | GALWAY | GALWAY | SS-104 | Athenry 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.999 | 16 | 0.142 | 3 | 0.142 | 4.2 | 4.2 | 1703340 | 1 | 405557.1429 | 2.4657 | 4.2 | 342.819
1229 | 1229 | CL3-076 | GALWAY | GALWAY | SS-104 | Athenry 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.184 | 16 | 0.161 | 3 | 0.161 | 4.2 | 4.2 | 1703340 | 1 | 405557.1429 | 2.4657 | 4.2 | 405.5571
1230 | 1230 | CL3-077 | LIMERICK | LIMERICK | SS-402 | Rathgoggan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 6.449 | 7 | 0.43 | 3 | 0.43 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 405.5571
1231 | 1231 | CL3-078 | ROSCOMMON | ROSCOMMON | SS-269 | Shannonbridge 110kV Substation | EirGrid | 110000 | low | 110000 | 6.415 | 7 | 0.112 | 3 | 0.112 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525 | 4.2 | 199.9238
1232 | 1232 | CL3-079 | TIPPERARY | TIPPERARY | SS-645 | Toomevara 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.234 | 7 | 0.248 | 3 | 0.248 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 425.0881
1233 | 1233 | CL3-080 | OFFALY | OFFALY | SS-084 | Birr 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.054 | 7 | 0.109 | 3 | 0.109 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 199.9238
1234 | 1234 | CL3-081 | GALWAY | GALWAY | SS-235 | Lisheeny 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.8 | 3 | 0.096 | 3 | 0.096 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 199.9238
1235 | 1235 | CL3-082 | WESTMEATH | WESTMEATH | SS-052 | Moate 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 4.841 | 5 | 0.198 | 3 | 0.198 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 133
1236 | 1236 | CL3-083 | ROSCOMMON | ROSCOMMON | SS-236 | Creagh 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.018 | 7 | 0.305 | 3 | 0.305 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 166.4619
1237 | 1237 | CL3-084 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.618 | 12 | 0.097 | 3 | 0.097 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 199.9238
1238 | 1238 | CL3-085 | CORK | CORK | SS-032 | Mallow 110kV Substation | EirGrid | 110000 |  |  | 2.048 | 3 | 0.13 | 3 | 0.13 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674 | 4.2 | 355.3667
1239 | 1239 | CL3-086 | CLARE | CLARE | SS-149 | Tulla 38kV Substation | ESB Networks | 38000 |  |  | 6.536 | 7 | 0.221 | 3 | 0.221 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 374.8976
1240 | 1240 | CL3-087 | GALWAY | GALWAY | SS-439 | Loughrea 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.561 | 9 | 0.156 | 3 | 0.156 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 199.9238
1241 | 1241 | CL3-088 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.895 | 10 | 0.235 | 3 | 0.235 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 4.2 | 317.7238
1242 | 1242 | CL3-089 | CORK | CORK | SS-581 | Coolcarron 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.74 | 5 | 0.117 | 3 | 0.117 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 330.2714
1243 | 1243 | CL3-090 | KILKENNY | KILKENNY | SS-098 | Callan 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.899 | 8 | 0.356 | 3 | 0.356 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 166.4619
1244 | 1244 | CL3-091 | OFFALY | OFFALY | SS-541 | Roscrea 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.025 | 7 | 0.144 | 3 | 0.144 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 216.6548
1245 | 1245 | CL3-092 | TIPPERARY | TIPPERARY | SS-098 | Callan 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.028 | 11 | 0.184 | 3 | 0.184 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 199.9238
1246 | 1246 | CL3-093 | OFFALY | OFFALY | SS-468 | Clara 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.664 | 5 | 0.255 | 3 | 0.255 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 342.819
1247 | 1247 | CL3-094 | CORK | CORK | SS-606 | Castlelyons 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.353 | 6 | 0.113 | 3 | 0.113 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 166.4619
1248 | 1248 | CL3-095 | CORK | CORK | SS-583 | Castletownroche 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.325 | 10 | 0.221 | 3 | 0.221 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 4.2 | 183.1929
1249 | 1249 | CL3-096 | TIPPERARY | LAOIS | SS-666 | 38kV Substation | ESB Networks | 38000 | low | 38000 | 6.79 | 7 | 0.154 | 3 | 0.154 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 330.2714
1250 | 1250 | CL3-097 | WICKLOW | WICKLOW | SS-699 | Ballycumber 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.057 | 4 | 0.201 | 3 | 0.201 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 199.9238
1251 | 1251 | CL3-098 | OFFALY | OFFALY | SS-469 | Portarlington 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.033 | 3 | 0.125 | 3 | 0.125 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 149.731
1252 | 1252 | CL3-099 | KILDARE | KILDARE | SS-228 | Dunfierth 110kV Substation | EirGrid | 110000 | 110000 | 20000 | 2.799 | 3 | 0.209 | 3 | 0.209 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674 | 4.2 | 133
1253 | 1253 | CL3-100 | LAOIS | LAOIS | SS-035 | Athy South 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.602 | 9 | 0.115 | 3 | 0.115 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 374.8976
1254 | 1254 | CL3-101 | LAOIS | LAOIS | SS-034 | Athy 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.048 | 9 | 0.325 | 3 | 0.325 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213 | 4.2 | 317.7238
1255 | 1255 | CL3-102 | OFFALY | OFFALY | SS-231 | Lumcloon 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.115 | 14 | 0.195 | 3 | 0.195 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284 | 4.2 | 450.1833
1256 | 1256 | CL3-103 | OFFALY | LAOIS | SS-311 | Clonminch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 12.322 | 13 | 0.183 | 3 | 0.183 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718 | 4.2 | 380.4619
1257 | 1257 | CL3-104 | GALWAY | GALWAY | SS-236 | Creagh 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.69 | 7 | 0.262 | 3 | 0.262 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 367.9143
1258 | 1258 | CL3-105 | CLARE | CLARE | SS-149 | Tulla 38kV Substation | ESB Networks | 38000 |  |  | 4.44 | 5 | 0.326 | 3 | 0.326 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 199.9238
1259 | 1259 | CL3-106 | WICKLOW | WICKLOW | SS-699 | Ballycumber 38kV Substation | ESB Networks | 38000 | low | 38000 | 8.256 | 9 | 0.108 | 3 | 0.108 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 166.4619
1260 | 1260 | CL3-107 | KILDARE | LAOIS | SS-469 | Portarlington 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.83 | 10 | 0.122 | 3 | 0.122 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 4.2 | 317.7238
1261 | 1261 | CL3-108 | OFFALY | OFFALY | SS-311 | Clonminch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.463 | 8 | 0.149 | 3 | 0.149 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 330.2714
1262 | 1262 | CL3-109 | CORK | CORK | SS-255 | Cloonlough 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.688 | 7 | 0.12 | 3 | 0.12 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 216.6548
1263 | 1263 | CL3-110 | WICKLOW | WICKLOW | SS-320 |  | EirGrid | 110000 | 110000 | low | 2.265 | 3 | 0.149 | 3 | 0.149 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674 | 4.2 | 199.9238
1264 | 1264 | CL3-111 | TIPPERARY | TIPPERARY | SS-325 | Kyleeragh 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.48 | 13 | 0.117 | 3 | 0.117 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718 | 4.2 | 374.8976
1265 | 1265 | CL3-112 | GALWAY | GALWAY | SS-175 | Ballygar 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.942 | 13 | 0.125 | 3 | 0.125 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718 | 4.2 | 367.9143
1266 | 1266 | CL3-113 | TIPPERARY | TIPPERARY | SS-459 | Ballycrossaun 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.285 | 15 | 0.095 | 3 | 0.095 | 4.2 | 4.2 | 1650640 | 1 | 393009.5238 | 2.5445 | 4.2 | 367.9143
1267 | 1267 | CL3-114 | OFFALY | OFFALY | SS-468 | Clara 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.286 | 3 | 0.25 | 3 | 0.25 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 393.0095
1268 | 1268 | CL3-115 | TIPPERARY | TIPPERARY | SS-540 | Templemore 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 2.651 | 3 | 0.261 | 3 | 0.261 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 133
1269 | 1269 | CL3-116 | LAOIS | LAOIS | SS-372 | Ballyconra 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.306 | 11 | 0.263 | 3 | 0.263 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 133
1270 | 1270 | CL3-117 | OFFALY | OFFALY | SS-541 | Roscrea 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.204 | 9 | 0.238 | 3 | 0.238 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 342.819
1271 | 1271 | CL3-118 | ROSCOMMON | ROSCOMMON | SS-683 | Monksland 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.976 | 3 | 0.175 | 3 | 0.175 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 317.7238
1272 | 1272 | CL3-119 | WESTMEATH | WESTMEATH | SS-066 | Thornsberry 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 11.121 | 12 | 0.199 | 3 | 0.199 | 4.2 | 4.2 | 2048870 | 7 | 487826.1905 | 2.0499 | 4.2 | 133
1273 | 1273 | CL3-120 | WEXFORD | WEXFORD | SS-495 | New Ross (West) 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.339 | 6 | 0.151 | 3 | 0.151 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 487.8262
1274 | 1274 | CL3-121 | LIMERICK | LIMERICK | SS-402 | Rathgoggan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 13.118 | 14 | 0.154 | 3 | 0.154 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284 | 4.2 | 183.1929
1275 | 1275 | CL3-122 | ROSCOMMON | ROSCOMMON | SS-236 | Creagh 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 3.877 | 4 | 0.148 | 3 | 0.148 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 380.4619
1276 | 1276 | CL3-123 | LAOIS | LAOIS | SS-217 | Port Laoise 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.646 | 9 | 0.292 | 3 | 0.292 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213 | 4.2 | 149.731
1277 | 1277 | CL3-124 | LAOIS | LAOIS | SS-275 | Mountrath ESB Telecoms 38kV Radio Site | ESB Networks | 38000 | 38000 | low | 6.611 | 7 | 0.109 | 3 | 0.109 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 450.1833
1278 | 1278 | CL3-125 | OFFALY | OFFALY | SS-084 | Birr 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.984 | 5 | 0.32 | 3 | 0.32 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 199.9238
1279 | 1279 | CL3-126 | OFFALY | OFFALY | SS-244 | Cartrontroy 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.739 | 8 | 0.161 | 3 | 0.161 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 166.4619
1280 | 1280 | CL3-127 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.053 | 5 | 0.11 | 3 | 0.11 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 216.6548
1281 | 1281 | CL3-128 | CARLOW | CARLOW | SS-368 | Gortahile 38kV Substation | ESB Networks | 38000 | low | 38000 | 6.399 | 7 | 0.17 | 3 | 0.17 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 166.4619
1282 | 1282 | CL3-129 | CLARE | CLARE | SS-503 | Scariff 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 5.043 | 6 | 0.162 | 3 | 0.162 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 199.9238
1283 | 1283 | CL3-130 | LAOIS | LAOIS | SS-469 | Portarlington 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.711 | 12 | 0.235 | 3 | 0.235 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 183.1929
1284 | 1284 | CL3-131 | CORK | LIMERICK | SS-340 | Milford 38kV Substation | ESB Networks | 38000 | 38000 | low | 1.659 | 2 | 0.109 | 3 | 0.109 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007 | 4.2 | 355.3667
1285 | 1285 | CL3-132 | WATERFORD | LAOIS | SS-537 | Monaincha 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 3.572 | 4 | 0.121 | 3 | 0.121 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 116.269
1286 | 1286 | CL3-133 | LAOIS | LAOIS | SS-275 | Mountrath ESB Telecoms 38kV Radio Site | ESB Networks | 38000 | 38000 | low | 8.995 | 9 | 0.156 | 3 | 0.156 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 149.731
1287 | 1287 | CL3-134 | CORK | CORK | SS-433 | Lee Bridge 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.297 | 11 | 0.11 | 3 | 0.11 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 317.7238
1288 | 1288 | CL3-135 | TIPPERARY | TIPPERARY | SS-348 | Furle 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.478 | 9 | 0.202 | 3 | 0.202 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 342.819
1289 | 1289 | CL3-136 | TIPPERARY | TIPPERARY | SS-040 | Deerpark 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.171 | 11 | 0.096 | 3 | 0.096 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 317.7238
1290 | 1290 | CL3-137 | KILKENNY | KILKENNY | SS-489 | Ballyhale 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.892 | 9 | 0.251 | 3 | 0.251 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 342.819
1291 | 1291 | CL3-138 | LAOIS | LAOIS | SS-486 | Castlecomer 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.951 | 11 | 0.135 | 3 | 0.135 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 317.7238
1292 | 1292 | CL3-139 | TIPPERARY | TIPPERARY | SS-594 | Kill Hill 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 2.688 | 3 | 0.113 | 3 | 0.113 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674 | 4.2 | 342.819
1293 | 1293 | CL3-140 | LAOIS | LAOIS | SS-537 | Monaincha 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 8.657 | 9 | 0.203 | 3 | 0.203 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 374.8976
1294 | 1294 | CL3-141 | KERRY | KERRY | SS-706 | Scartaglin 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.845 | 2 | 0.153 | 3 | 0.153 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007 | 4.2 | 317.7238
1295 | 1295 | CL3-142 | KERRY | KERRY | SS-189 | Knockearagh 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 4.5 | 5 | 0.109 | 3 | 0.109 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5 | 4.2 | 116.269
1296 | 1296 | CL3-143 | CAVAN | CAVAN | SS-304 | Arigna 110kV Substation | EirGrid | 110000 | 110000 | 20000 | 12.611 | 13 | 0.181 | 3 | 0.181 | 4.2 | 4.2 | 2101570 | 7 | 500373.8095 | 1.9985 | 4.2 | 399.9929
1297 | 1297 | CL3-144 | CAVAN | CAVAN | SS-110 | Corraclassy 110kV Substation | EirGrid | 110000 |  |  | 15.879 | 16 | 0.305 | 3 | 0.305 | 4.2 | 4.2 | 2259670 | 7 | 538016.6667 | 1.8587 | 4.2 | 500.3738
1298 | 1298 | CL3-145 | GALWAY | GALWAY | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 6.137 | 7 | 0.107 | 3 | 0.107 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 538.0167
1299 | 1299 | CL3-146 | GALWAY | GALWAY | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 6.923 | 7 | 0.14 | 3 | 0.14 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 199.9238
1300 | 1300 | CL3-147 | LEITRIM | LEITRIM | SS-304 | Arigna 110kV Substation | EirGrid | 110000 | 110000 | 20000 | 7.277 | 8 | 0.221 | 3 | 0.221 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285 | 4.2 | 199.9238
1301 | 1301 | CL3-148 | SLIGO | SLIGO | SS-075 | Cunghill 110kV Substation | EirGrid | 110000 | 110000 | medium | 1.907 | 2 | 0.184 | 3 | 0.184 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341 | 4.2 | 437.6357
1302 | 1302 | CL3-149 | SLIGO | SLIGO | SS-075 | Cunghill 110kV Substation | EirGrid | 110000 | 110000 | medium | 3.389 | 4 | 0.185 | 3 | 0.185 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581 | 4.2 | 319.0667
1303 | 1303 | CL3-150 | ROSCOMMON | ROSCOMMON | SS-206 | Boyle 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 13.482 | 14 | 0.137 | 3 | 0.137 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284 | 4.2 | 387.4452
1304 | 1304 | CL3-151 | ROSCOMMON | ROSCOMMON | SS-206 | Boyle 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 11.242 | 12 | 0.201 | 3 | 0.201 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 380.4619
1305 | 1305 | CL3-152 | ROSCOMMON | ROSCOMMON | SS-171 | Castlerea 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.11 | 7 | 0.132 | 3 | 0.132 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 355.3667
1306 | 1306 | CL3-153 | ROSCOMMON | ROSCOMMON | SS-171 | Castlerea 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.934 | 7 | 0.134 | 3 | 0.134 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 199.9238
1307 | 1307 | CL3-154 | LEITRIM | LEITRIM | SS-048 | Roosky 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.946 | 4 | 0.331 | 3 | 0.331 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 199.9238
1308 | 1308 | CL3-155 | ROSCOMMON | ROSCOMMON | SS-158 | Gilra 110kV Substation | EirGrid | 110000 | 110000 | low | 8.035 | 9 | 0.282 | 3 | 0.282 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213 | 4.2 | 149.731
1309 | 1309 | CL3-156 | ROSCOMMON | ROSCOMMON | SS-206 | Boyle 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 4.66 | 5 | 0.167 | 3 | 0.167 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 450.1833
1310 | 1310 | CL3-157 | SLIGO | LEITRIM | SS-031 | Sligo 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.438 | 9 | 0.174 | 3 | 0.174 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213 | 4.2 | 166.4619
1311 | 1311 | CL3-158 | MAYO | MAYO | SS-202 | Kiltimagh 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.57 | 7 | 0.234 | 3 | 0.234 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 450.1833
1312 | 1312 | CL3-159 | ROSCOMMON | ROSCOMMON | SS-171 | Castlerea 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.313 | 13 | 0.145 | 3 | 0.145 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718 | 4.2 | 199.9238
1313 | 1313 | CL3-160 | ROSCOMMON | ROSCOMMON | SS-175 | Ballygar 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.522 | 11 | 0.17 | 3 | 0.17 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 367.9143
1314 | 1314 | CL3-161 | MAYO | MAYO | SS-208 | Ballyhaunis 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.381 | 6 | 0.104 | 3 | 0.104 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 342.819
1315 | 1315 | CL3-162 | ROSCOMMON | ROSCOMMON | SS-048 | Roosky 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.486 | 4 | 0.206 | 3 | 0.206 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 183.1929
1316 | 1316 | CL3-163 | LONGFORD | LONGFORD | SS-563 | Ballymahon 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.878 | 6 | 0.102 | 3 | 0.102 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 149.731
1317 | 1317 | CL3-164 | LONGFORD | LONGFORD | SS-563 | Ballymahon 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.661 | 3 | 0.097 | 3 | 0.097 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 183.1929
1318 | 1318 | CL3-165 | LONGFORD | LONGFORD | SS-563 | Ballymahon 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.457 | 4 | 0.108 | 3 | 0.108 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 133
1319 | 1319 | CL3-166 | WESTMEATH | WESTMEATH | SS-563 | Ballymahon 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.889 | 6 | 0.141 | 3 | 0.141 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 149.731
1320 | 1320 | CL3-167 | LONGFORD | LONGFORD | SS-563 | Ballymahon 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.17 | 7 | 0.44 | 3 | 0.44 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 183.1929
1321 | 1321 | CL3-168 | ROSCOMMON | ROSCOMMON | SS-124 | Roscommon 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.464 | 7 | 0.13 | 3 | 0.13 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 199.9238
1322 | 1322 | CL3-169 | LONGFORD | LONGFORD | SS-563 | Ballymahon 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.96 | 7 | 0.166 | 3 | 0.166 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 199.9238
1323 | 1323 | CL3-170 | WEXFORD | LONGFORD | SS-247 | Edgeworthstown 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.559 | 7 | 0.168 | 3 | 0.168 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 199.9238
1324 | 1324 | CL3-171 | WESTMEATH | WESTMEATH | SS-229 | Mullingar 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 9.016 | 10 | 0.198 | 3 | 0.198 | 4.2 | 4.2 | 1943470 | 7 | 462730.9524 | 2.1611 | 4.2 | 199.9238
1325 | 1325 | CL3-172 | WESTMEATH | WESTMEATH | SS-563 | Ballymahon 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.183 | 13 | 0.103 | 3 | 0.103 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718 | 4.2 | 462.731
1326 | 1326 | CL3-173 | WESTMEATH | WESTMEATH | SS-246 | Loughanalla 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.462 | 9 | 0.091 | 3 | 0.091 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 367.9143
1327 | 1327 | CL3-174 | LONGFORD | LONGFORD | SS-067 | Finnea 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.578 | 7 | 0.272 | 3 | 0.272 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 317.7238
1328 | 1328 | CL3-175 | WESTMEATH | WESTMEATH | SS-246 | Loughanalla 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.602 | 9 | 0.154 | 3 | 0.154 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 199.9238
1329 | 1329 | CL3-176 | WESTMEATH | WESTMEATH | SS-246 | Loughanalla 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 3.665 | 4 | 0.176 | 3 | 0.176 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 317.7238
1330 | 1330 | CL3-177 | WESTMEATH | WESTMEATH | SS-067 | Finnea 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.728 | 6 | 0.109 | 3 | 0.109 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 149.731
1331 | 1331 | CL3-178 | WEXFORD | LONGFORD | SS-247 | Edgeworthstown 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.924 | 6 | 0.231 | 3 | 0.231 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 183.1929
1332 | 1332 | CL3-179 | WESTMEATH | WESTMEATH | SS-052 | Moate 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 14.539 | 15 | 0.133 | 3 | 0.133 | 4.2 | 4.2 | 1650640 | 1 | 393009.5238 | 2.5445 | 4.2 | 183.1929
1333 | 1333 | CL3-180 | LONGFORD | LONGFORD | SS-543 | Lisnamuck 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.528 | 5 | 0.144 | 3 | 0.144 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 393.0095
1334 | 1334 | CL3-181 | CAVAN | CAVAN | SS-081 | Killeshandra 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.122 | 6 | 0.116 | 3 | 0.116 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 166.4619
1335 | 1335 | CL3-182 | MONAGHAN | MONAGHAN | SS-428 | Clones 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.214 | 7 | 0.137 | 3 | 0.137 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 183.1929
1336 | 1336 | CL3-183 | WESTMEATH | WESTMEATH | SS-526 | Newbrook 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.405 | 8 | 0.139 | 3 | 0.139 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 199.9238
1337 | 1337 | CL3-184 | WESTMEATH | WESTMEATH | SS-526 | Newbrook 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 4.434 | 5 | 0.306 | 3 | 0.306 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 216.6548
1338 | 1338 | CL3-185 | WESTMEATH | WESTMEATH | SS-517 | Delvin 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.828 | 8 | 0.115 | 3 | 0.115 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 166.4619
1339 | 1339 | CL3-186 | MEATH | MEATH | SS-375 | Kells Business Park 38kV Substation | ESB Networks | 38000 | 38000 |  | 5.912 | 6 | 0.348 | 3 | 0.348 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 216.6548
1340 | 1340 | CL3-187 | MEATH | MEATH | SS-521 | Kingscourt 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.125 | 9 | 0.095 | 3 | 0.095 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 183.1929
1341 | 1341 | CL3-188 | WESTMEATH | MEATH | SS-517 | Delvin 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.032 | 8 | 0.132 | 3 | 0.132 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 317.7238
1342 | 1342 | CL3-189 | MEATH | MEATH | SS-460 | Julianstown 38kV Substation | ESB Networks | 38000 | 38000 | low | 1.865 | 2 | 0.279 | 3 | 0.279 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007 | 4.2 | 216.6548
1343 | 1343 | CL3-190 | MEATH | MEATH | SS-518 | Athboy 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.902 | 4 | 0.241 | 3 | 0.241 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 116.269
1344 | 1344 | CL3-191 | LONGFORD | LONGFORD | SS-044 | Richmond 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 4.627 | 5 | 0.107 | 3 | 0.107 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5 | 4.2 | 149.731
1345 | 1345 | CL3-192 | ROSCOMMON | ROSCOMMON | SS-175 | Ballygar 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.858 | 5 | 0.212 | 3 | 0.212 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 399.9929
1346 | 1346 | CL3-193 | KILDARE | KILDARE | SS-034 | Athy 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 6.726 | 7 | 0.113 | 3 | 0.113 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525 | 4.2 | 166.4619
1347 | 1347 | CL3-194 | KILDARE | KILDARE | SS-216 | Blake 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 6.36 | 7 | 0.106 | 3 | 0.106 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525 | 4.2 | 425.0881
1348 | 1348 | CL3-195 | GALWAY | GALWAY | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 6.469 | 7 | 0.145 | 3 | 0.145 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 425.0881
1349 | 1349 | CL3-196 | LONGFORD | LONGFORD | SS-575 | Aghamore 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.254 | 11 | 0.248 | 3 | 0.248 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 199.9238
1350 | 1350 | CL3-197 | LONGFORD | LONGFORD | SS-268 | Lanesborough 110kV Substation | EirGrid | 110000 |  |  | 6.45 | 7 | 0.203 | 3 | 0.203 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525 | 4.2 | 342.819
1351 | 1351 | CL3-198 | MONAGHAN | MONAGHAN | SS-547 | Emyvale 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.675 | 5 | 0.115 | 3 | 0.115 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 425.0881
1352 | 1352 | CL3-199 | OFFALY | OFFALY | SS-084 | Birr 38kV Substation | ESB Networks | 38000 | 38000 | low | 16.731 | 17 | 0.133 | 3 | 0.133 | 4.2 | 4.2 | 1756040 | 1 | 418104.7619 | 2.3917 | 4.2 | 166.4619
1353 | 1353 | CL3-200 | OFFALY | OFFALY | SS-084 | Birr 38kV Substation | ESB Networks | 38000 | 38000 | low | 16.649 | 17 | 0.153 | 3 | 0.153 | 4.2 | 4.2 | 1756040 | 1 | 418104.7619 | 2.3917 | 4.2 | 418.1048
1354 | 1354 | CL3-201 | LIMERICK | LIMERICK | SS-596 | Cappamore 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.426 | 8 | 0.201 | 3 | 0.201 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 418.1048
1355 | 1355 | CL3-202 | MONAGHAN | MONAGHAN | SS-428 | Clones 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.941 | 8 | 0.226 | 3 | 0.226 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 216.6548
1356 | 1356 | CL3-203 | WATERFORD | WATERFORD | SS-622 | Barranafaddock 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.898 | 2 | 0.148 | 3 | 0.148 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007 | 4.2 | 216.6548
1357 | 1357 | CL3-204 | TIPPERARY | TIPPERARY | SS-459 | Ballycrossaun 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.934 | 5 | 0.299 | 3 | 0.299 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 116.269
1358 | 1358 | CL3-205 | OFFALY | OFFALY | SS-311 | Clonminch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 3.173 | 4 | 0.392 | 3 | 0.392 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 166.4619
1359 | 1359 | CL3-206 | OFFALY | OFFALY | SS-168 | Derryiron 110kV Substation | EirGrid | 110000 |  |  | 5.659 | 6 | 0.302 | 3 | 0.302 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424 | 4.2 | 149.731
1360 | 1360 | CL3-207 | TIPPERARY | TIPPERARY | SS-537 | Monaincha 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 1.991 | 2 | 0.424 | 3 | 0.424 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007 | 4.2 | 412.5405
1361 | 1361 | CL3-208 | OFFALY | LAOIS | SS-231 | Lumcloon 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.782 | 14 | 0.422 | 3 | 0.422 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284 | 4.2 | 116.269
1362 | 1362 | CL3-209 | CORK | WATERFORD | SS-607 | Curraglass 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.633 | 8 | 0.103 | 3 | 0.103 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 380.4619
1363 | 1363 | CL3-210 | KILKENNY | KILKENNY | SS-492 | Graigue 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.244 | 6 | 0.104 | 3 | 0.104 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 216.6548
1364 | 1364 | CL3-211 | TIPPERARY | TIPPERARY | SS-347 | Glengoole 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.452 | 7 | 0.338 | 3 | 0.338 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 183.1929
1365 | 1365 | CL3-212 | ROSCOMMON | ROSCOMMON | SS-236 | Creagh 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 1.677 | 2 | 0.261 | 3 | 0.261 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007 | 4.2 | 199.9238
1366 | 1366 | CL3-213 | SLIGO | SLIGO | SS-075 | Cunghill 110kV Substation | EirGrid | 110000 | 110000 | medium | 4.558 | 5 | 0.422 | 3 | 0.422 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5 | 4.2 | 116.269
1367 | 1367 | CL3-214 | ROSCOMMON | ROSCOMMON | SS-236 | Creagh 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.334 | 12 | 0.1 | 3 | 0.1 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 399.9929
1368 | 1368 | CL3-215 | WESTMEATH | WESTMEATH | SS-232 | Bushfield 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.831 | 7 | 0.143 | 3 | 0.143 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 355.3667
1369 | 1369 | CL3-216 | WESTMEATH | WESTMEATH | SS-052 | Moate 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.363 | 8 | 0.457 | 3 | 0.457 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 199.9238
1370 | 1370 | CL3-217 | DONEGAL | DONEGAL | SS-117 | Crockahenny 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.528 | 2 | 0.529 | 3 | 0.529 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007 | 4.2 | 216.6548
1371 | 1371 | CL3-218 | DONEGAL | DONEGAL | SS-083 | Golagh 110kV Substation | EirGrid | 110000 | 38000 | 110000 | 9.304 | 10 | 0.277 | 3 | 0.277 | 4.2 | 4.2 | 1943470 | 7 | 462730.9524 | 2.1611 | 4.2 | 116.269
1372 | 1372 | CL3-219 | DONEGAL | DONEGAL | SS-690 | Stranrolar 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.66 | 11 | 0.091 | 3 | 0.091 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 462.731
1373 | 1373 | CL3-220 | DONEGAL | DONEGAL | SS-083 | Golagh 110kV Substation | EirGrid | 110000 | 38000 | 110000 | 5.41 | 6 | 0.291 | 3 | 0.291 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424 | 4.2 | 342.819
1374 | 1374 | CL3-221 | DONEGAL | DONEGAL | SS-617 | Mulreavy 110kV Substation | EirGrid | 110000 | 33000 | 110000 | 7.02 | 8 | 0.312 | 3 | 0.312 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285 | 4.2 | 412.5405
1375 | 1375 | CL3-222 | DONEGAL | DONEGAL | SS-617 | Mulreavy 110kV Substation | EirGrid | 110000 | 33000 | 110000 | 7.728 | 8 | 0.096 | 3 | 0.096 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285 | 4.2 | 437.6357
1376 | 1376 | CL3-223 | DONEGAL | DONEGAL | SS-087 | Cliff 110kV Substation | EirGrid | 110000 | low | 110000 | 13.498 | 14 | 0.125 | 3 | 0.125 | 4.2 | 4.2 | 2154270 | 7 | 512921.4286 | 1.9496 | 4.2 | 437.6357
1377 | 1377 | CL3-224 | CAVAN | CAVAN | SS-110 | Corraclassy 110kV Substation | EirGrid | 110000 |  |  | 3.382 | 4 | 0.124 | 3 | 0.124 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581 | 4.2 | 512.9214
1378 | 1378 | CL3-225 | LOUTH | LOUTH | SS-650 | Ballymascanlan 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.283 | 7 | 0.242 | 3 | 0.242 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 387.4452
1379 | 1379 | CL3-226 | CORK | CORK | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.004 | 12 | 0.226 | 3 | 0.226 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 199.9238
1380 | 1380 | CL3-227 | CORK | CORK | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 13.888 | 14 | 0.216 | 3 | 0.216 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284 | 4.2 | 355.3667
1381 | 1381 | CL3-228 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 13.213 | 14 | 0.155 | 3 | 0.155 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284 | 4.2 | 380.4619
1382 | 1382 | CL3-229 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.492 | 8 | 0.21 | 3 | 0.21 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 380.4619
1383 | 1383 | CL3-230 | CORK | CORK | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.461 | 9 | 0.268 | 3 | 0.268 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 216.6548
1384 | 1384 | CL3-231 | CORK | KERRY | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.144 | 8 | 0.66 | 3 | 0.66 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 317.7238
1385 | 1385 | CL3-232 | KERRY | KERRY | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.939 | 10 | 0.101 | 3 | 0.101 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 4.2 | 216.6548
1386 | 1386 | CL3-233 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.091 | 12 | 0.419 | 3 | 0.419 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 330.2714
1387 | 1387 | CL3-234 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.447 | 10 | 0.346 | 3 | 0.346 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 4.2 | 355.3667
1388 | 1388 | CL3-235 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.443 | 7 | 0.557 | 3 | 0.557 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 330.2714
1389 | 1389 | CL3-236 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.179 | 8 | 0.313 | 3 | 0.313 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 199.9238
1390 | 1390 | CL3-237 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.71 | 6 | 0.162 | 3 | 0.162 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 216.6548
1391 | 1391 | CL3-238 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 17.786 | 18 | 0.167 | 3 | 0.167 | 4.2 | 4.2 | 1808740 | 1 | 430652.381 | 2.3221 | 4.2 | 183.1929
1392 | 1392 | CL3-239 | KERRY | KERRY | SS-387 | Coolcorcoran 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.356 | 9 | 0.319 | 3 | 0.319 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 430.6524
1393 | 1393 | CL3-240 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.154 | 15 | 0.12 | 3 | 0.12 | 4.2 | 4.2 | 1650640 | 1 | 393009.5238 | 2.5445 | 4.2 | 317.7238
1394 | 1394 | CL3-241 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.258 | 12 | 0.29 | 3 | 0.29 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 393.0095
1395 | 1395 | CL3-242 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.096 | 12 | 0.212 | 3 | 0.212 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 355.3667
1396 | 1396 | CL3-243 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.798 | 9 | 0.129 | 3 | 0.129 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 355.3667
1397 | 1397 | CL3-244 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.896 | 15 | 0.511 | 3 | 0.511 | 4.2 | 4.2 | 1650640 | 1 | 393009.5238 | 2.5445 | 4.2 | 317.7238
1398 | 1398 | CL3-245 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 12.36 | 13 | 0.23 | 3 | 0.23 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718 | 4.2 | 393.0095
1399 | 1399 | CL3-246 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.957 | 13 | 0.276 | 3 | 0.276 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718 | 4.2 | 367.9143
1400 | 1400 | CL3-247 | KERRY | KERRY | SS-321 | Milltown 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 12.639 | 13 | 0.101 | 3 | 0.101 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718 | 4.2 | 367.9143
1401 | 1401 | CL3-248 | KERRY | KERRY | SS-157 | Oughtragh 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 13.446 | 14 | 0.392 | 3 | 0.392 | 4.2 | 4.2 | 2154270 | 7 | 512921.4286 | 1.9496 | 4.2 | 367.9143
1402 | 1402 | CL3-249 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 15.864 | 16 | 0.111 | 3 | 0.111 | 4.2 | 4.2 | 1703340 | 1 | 405557.1429 | 2.4657 | 4.2 | 512.9214
1403 | 1403 | CL3-250 | KERRY | KERRY | SS-072 | Clonkeen 110kV Substation | EirGrid | 110000 |  |  | 5.546 | 6 | 0.197 | 3 | 0.197 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424 | 4.2 | 405.5571
1404 | 1404 | CL3-251 | KERRY | KERRY | SS-071 | Coomagearlahy Substation | EirGrid | 110000 | medium-low | 110000 | 5.191 | 6 | 0.376 | 3 | 0.376 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424 | 4.2 | 412.5405
1405 | 1405 | CL3-252 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.158 | 5 | 0.344 | 3 | 0.344 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 412.5405
1406 | 1406 | CL3-253 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.165 | 16 | 0.397 | 3 | 0.397 | 4.2 | 4.2 | 1703340 | 1 | 405557.1429 | 2.4657 | 4.2 | 166.4619
1407 | 1407 | CL3-254 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 11.758 | 12 | 0.091 | 3 | 0.091 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 405.5571
1408 | 1408 | CL3-255 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 8.735 | 9 | 0.319 | 3 | 0.319 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 355.3667
1409 | 1409 | CL3-256 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.637 | 2 | 0.128 | 3 | 0.128 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007 | 4.2 | 317.7238
1410 | 1410 | CL3-257 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 6.326 | 7 | 0.444 | 3 | 0.444 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 116.269
1411 | 1411 | CL3-258 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.644 | 4 | 0.227 | 3 | 0.227 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 199.9238
1412 | 1412 | CL3-259 | CORK | CORK | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 5.364 | 6 | 0.42 | 3 | 0.42 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 149.731
1413 | 1413 | CL3-260 | CORK | CORK | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 6.022 | 7 | 0.401 | 3 | 0.401 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 183.1929
1414 | 1414 | CL3-261 | CORK | CORK | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 2.547 | 3 | 0.117 | 3 | 0.117 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 199.9238
1415 | 1415 | CL3-262 | KERRY | KERRY | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 7.907 | 8 | 0.626 | 3 | 0.626 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 133
1416 | 1416 | CL3-263 | KERRY | KERRY | SS-637 | Kilgarvan 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.44 | 6 | 0.454 | 3 | 0.454 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 216.6548
1417 | 1417 | CL3-264 | KERRY | KERRY | SS-321 | Milltown 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 3.471 | 4 | 0.387 | 3 | 0.387 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 183.1929
1418 | 1418 | CL3-265 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.78 | 5 | 0.276 | 3 | 0.276 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 149.731
1419 | 1419 | CL3-266 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.286 | 8 | 0.239 | 3 | 0.239 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 166.4619
1420 | 1420 | CL3-267 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.716 | 9 | 0.644 | 3 | 0.644 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 216.6548
1421 | 1421 | CL3-268 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.044 | 6 | 0.173 | 3 | 0.173 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 317.7238
1422 | 1422 | CL3-269 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.267 | 5 | 0.103 | 3 | 0.103 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 183.1929
1423 | 1423 | CL3-270 | KERRY | KERRY | SS-140 | Ballyard 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.087 | 8 | 0.305 | 3 | 0.305 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 166.4619
1424 | 1424 | CL3-271 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.612 | 6 | 0.2 | 3 | 0.2 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 216.6548
1425 | 1425 | CL3-272 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.93 | 8 | 0.106 | 3 | 0.106 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 183.1929
1426 | 1426 | CL3-273 | CLARE | CLARE | SS-176 | Drumquin 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 6.337 | 7 | 0.177 | 3 | 0.177 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 216.6548
1427 | 1427 | CL3-274 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.58 | 16 | 0.099 | 3 | 0.099 | 4.2 | 4.2 | 1703340 | 1 | 405557.1429 | 2.4657 | 4.2 | 199.9238
1428 | 1428 | CL3-275 | CLARE | CLARE | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 18.161 | 19 | 0.27 | 3 | 0.27 | 4.2 | 4.2 | 1861440 | 1 | 443200 | 2.2563 | 4.2 | 405.5571
1429 | 1429 | CL3-276 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 18.143 | 19 | 0.115 | 3 | 0.115 | 4.2 | 4.2 | 1861440 | 1 | 443200 | 2.2563 | 4.2 | 443.2
1430 | 1430 | CL3-277 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.266 | 13 | 0.09 | 3 | 0.09 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718 | 4.2 | 443.2
1431 | 1431 | CL3-278 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.705 | 13 | 0.148 | 3 | 0.148 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718 | 4.2 | 367.9143
1432 | 1432 | CL3-279 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.965 | 10 | 0.114 | 3 | 0.114 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 4.2 | 367.9143
1433 | 1433 | CL3-280 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.948 | 12 | 0.156 | 3 | 0.156 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 330.2714
1434 | 1434 | CL3-281 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.137 | 11 | 0.497 | 3 | 0.497 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 355.3667
1435 | 1435 | CL3-282 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.583 | 3 | 0.148 | 3 | 0.148 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 342.819
1436 | 1436 | CL3-283 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.359 | 15 | 0.537 | 3 | 0.537 | 4.2 | 4.2 | 1650640 | 1 | 393009.5238 | 2.5445 | 4.2 | 133
1437 | 1437 | CL3-284 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.732 | 13 | 0.252 | 3 | 0.252 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718 | 4.2 | 393.0095
1438 | 1438 | CL3-285 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.105 | 14 | 0.386 | 3 | 0.386 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284 | 4.2 | 367.9143
1439 | 1439 | CL3-286 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 10.603 | 11 | 0.24 | 3 | 0.24 | 4.2 | 4.2 | 1996170 | 7 | 475278.5714 | 2.104 | 4.2 | 380.4619
1440 | 1440 | CL3-287 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 17.082 | 18 | 0.273 | 3 | 0.273 | 4.2 | 4.2 | 1808740 | 1 | 430652.381 | 2.3221 | 4.2 | 475.2786
1441 | 1441 | CL3-288 | GALWAY | GALWAY | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 17.598 | 18 | 0.119 | 3 | 0.119 | 4.2 | 4.2 | 1808740 | 1 | 430652.381 | 2.3221 | 4.2 | 430.6524
1442 | 1442 | CL3-289 | MAYO | MAYO | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 17.635 | 18 | 0.55 | 3 | 0.55 | 4.2 | 4.2 | 1808740 | 1 | 430652.381 | 2.3221 | 4.2 | 430.6524
1443 | 1443 | CL3-290 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 11.291 | 12 | 0.365 | 3 | 0.365 | 4.2 | 4.2 | 2048870 | 7 | 487826.1905 | 2.0499 | 4.2 | 430.6524
1444 | 1444 | CL3-291 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.205 | 7 | 0.344 | 3 | 0.344 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 487.8262
1445 | 1445 | CL3-292 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 18.421 | 19 | 0.093 | 3 | 0.093 | 4.2 | 4.2 | 1861440 | 1 | 443200 | 2.2563 | 4.2 | 199.9238
1446 | 1446 | CL3-293 | MAYO | MAYO | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 20.746 | 21 | 0.336 | 3 | 0.336 | 4.2 | 4.2 | 1966840 | 1 | 468295.2381 | 2.1354 | 4.2 | 443.2
1447 | 1447 | CL3-294 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 26.37 | 27 | 0.354 | 3 | 0.354 | 4.2 | 4.2 | 2839370 | 7 | 676040.4762 | 1.4792 | 4.2 | 468.2952
1448 | 1448 | CL3-295 | MAYO | MAYO | SS-317 | Newport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 13.796 | 14 | 0.593 | 3 | 0.593 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284 | 4.2 | 676.0405
1449 | 1449 | CL3-296 | MAYO | MAYO | SS-317 | Newport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 13.25 | 14 | 0.132 | 3 | 0.132 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284 | 4.2 | 380.4619
1450 | 1450 | CL3-297 | MAYO | MAYO | SS-170 | Derrynadivva 38kV Substation | ESB Networks | 38000 | low | 38000 | 9.007 | 10 | 0.408 | 3 | 0.408 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 4.2 | 380.4619
1451 | 1451 | CL3-298 | MAYO | MAYO | SS-170 | Derrynadivva 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.193 | 5 | 0.22 | 3 | 0.22 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 330.2714
1452 | 1452 | CL3-299 | SLIGO | SLIGO | SS-302 | Carrowleagh 38kV Substation | ESB Networks | 38000 | low | 38000 | 7.029 | 8 | 0.213 | 3 | 0.213 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 166.4619
1453 | 1453 | CL3-300 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.192 | 11 | 0.166 | 3 | 0.166 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 216.6548
1454 | 1454 | CL3-301 | SLIGO | SLIGO | SS-042 | Ballytivnan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.747 | 9 | 0.171 | 3 | 0.171 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 342.819
1455 | 1455 | CL3-302 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 4.011 | 5 | 0.326 | 3 | 0.326 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 317.7238
1456 | 1456 | CL3-303 | DONEGAL | DONEGAL | SS-252 | Killybegs 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 3.463 | 4 | 0.339 | 3 | 0.339 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 166.4619
1457 | 1457 | CL3-304 | DONEGAL | DONEGAL | SS-090 | Corkermore 38kV Substation | ESB Networks | 38000 | low | 38000 | 5.462 | 6 | 0.199 | 3 | 0.199 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 149.731
1458 | 1458 | CL3-305 | DONEGAL | DONEGAL | SS-090 | Corkermore 38kV Substation | ESB Networks | 38000 | low | 38000 | 5.873 | 6 | 0.361 | 3 | 0.361 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 183.1929
1459 | 1459 | CL3-306 | DONEGAL | DONEGAL | SS-119 | Drumlough Hill (1) 38kV Substation | ESB Networks | 38000 | low | 38000 | 6.548 | 7 | 0.178 | 3 | 0.178 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 183.1929
1460 | 1460 | CL3-307 | ROSCOMMON | ROSCOMMON | SS-384 | Largan Hill 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.759 | 5 | 0.497 | 3 | 0.497 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 199.9238
1461 | 1461 | CL3-308 | ROSCOMMON | SLIGO | SS-384 | Largan Hill 38kV Substation | ESB Networks | 38000 | low | 38000 | 7.588 | 8 | 0.347 | 3 | 0.347 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 166.4619
1462 | 1462 | CL3-309 | WEXFORD | WEXFORD | SS-481 | Castledockrell 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 7.617 | 8 | 0.121 | 3 | 0.121 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285 | 4.2 | 216.6548
1463 | 1463 | CL3-310 | CARLOW | CARLOW | SS-481 | Castledockrell 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 11.255 | 12 | 0.498 | 3 | 0.498 | 4.2 | 4.2 | 2048870 | 7 | 487826.1905 | 2.0499 | 4.2 | 437.6357
1464 | 1464 | CL3-311 | CARLOW | CARLOW | SS-494 | Bunclody 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.445 | 10 | 0.608 | 3 | 0.608 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 4.2 | 487.8262
1465 | 1465 | CL3-312 | WICKLOW | WICKLOW | SS-062 | Stratford 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 6.497 | 7 | 0.318 | 3 | 0.318 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525 | 4.2 | 330.2714
1466 | 1466 | CL3-313 | WICKLOW | WICKLOW | SS-062 | Stratford 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 6.941 | 7 | 0.267 | 3 | 0.267 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525 | 4.2 | 425.0881
1467 | 1467 | CL3-314 | WICKLOW | WICKLOW | SS-062 | Stratford 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.76 | 9 | 0.243 | 3 | 0.243 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213 | 4.2 | 425.0881
1468 | 1468 | CL3-315 | WICKLOW | WICKLOW | SS-699 | Ballycumber 38kV Substation | ESB Networks | 38000 | low | 38000 | 11.14 | 12 | 0.402 | 3 | 0.402 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 450.1833
1469 | 1469 | CL3-316 | WICKLOW | WICKLOW | SS-062 | Stratford 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 9.598 | 10 | 0.129 | 3 | 0.129 | 4.2 | 4.2 | 1943470 | 7 | 462730.9524 | 2.1611 | 4.2 | 355.3667
1470 | 1470 | CL3-317 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.73 | 9 | 0.091 | 3 | 0.091 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 462.731
1471 | 1471 | CL3-318 | WICKLOW | WICKLOW | SS-062 | Stratford 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 11.428 | 12 | 0.646 | 3 | 0.646 | 4.2 | 4.2 | 2048870 | 7 | 487826.1905 | 2.0499 | 4.2 | 317.7238
1472 | 1472 | CL3-319 | WICKLOW | WICKLOW | SS-209 | Blessington 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.429 | 10 | 0.555 | 3 | 0.555 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 4.2 | 487.8262
1473 | 1473 | CL3-320 | WICKLOW | WICKLOW | SS-570 | Kilcoole 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.644 | 14 | 0.346 | 3 | 0.346 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284 | 4.2 | 330.2714
1474 | 1474 | CL3-321 | WEXFORD | WICKLOW | SS-616 | Ballinvally 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 3.755 | 4 | 0.126 | 3 | 0.126 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 380.4619
1475 | 1475 | CL3-322 | KERRY | KERRY | SS-668 | Coomataggart 110 kV Substation | EirGrid | 110000 | low | 110000 | 3.933 | 4 | 0.316 | 3 | 0.316 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581 | 4.2 | 149.731
1476 | 1476 | CL3-323 | CORK | CORK | SS-668 | Coomataggart 110 kV Substation | EirGrid | 110000 | low | 110000 | 2.789 | 3 | 0.234 | 3 | 0.234 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674 | 4.2 | 387.4452
1477 | 1477 | CL3-324 | CORK | CORK | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.518 | 3 | 0.17 | 3 | 0.17 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 374.8976
1478 | 1478 | CL3-325 | CORK | CORK | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.933 | 4 | 0.224 | 3 | 0.224 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 133
1479 | 1479 | CL3-326 | CORK | CORK | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.805 | 4 | 0.119 | 3 | 0.119 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 149.731
1480 | 1480 | CL3-327 | KERRY | KERRY | SS-071 | Coomagearlahy Substation | EirGrid | 110000 | medium-low | 110000 | 1.825 | 2 | 0.585 | 3 | 0.585 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341 | 4.2 | 149.731
1481 | 1481 | CL3-328 | KERRY | KERRY | SS-070 | Glanlee 110kV Substation | EirGrid | 110000 | low | 110000 | 4.099 | 5 | 0.371 | 3 | 0.371 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5 | 4.2 | 319.0667
1482 | 1482 | CL3-329 | CORK | CORK | SS-070 | Glanlee 110kV Substation | EirGrid | 110000 | low | 110000 | 4.155 | 5 | 0.09 | 3 | 0.09 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5 | 4.2 | 399.9929
1483 | 1483 | CL3-330 | CORK | CORK | SS-615 | Knockduff 110kv Substation | EirGrid | 110000 |  |  | 3.355 | 4 | 0.144 | 3 | 0.144 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581 | 4.2 | 399.9929
1484 | 1484 | CL3-331 | CORK | CORK | SS-615 | Knockduff 110kv Substation | EirGrid | 110000 |  |  | 2.224 | 3 | 0.119 | 3 | 0.119 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674 | 4.2 | 387.4452
1485 | 1485 | CL3-332 | CORK | CORK | SS-096 | Boggeragh 110kV Substation | EirGrid | 110000 |  |  | 3.674 | 4 | 0.133 | 3 | 0.133 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581 | 4.2 | 374.8976
1486 | 1486 | CL3-333 | KILKENNY | KILKENNY | SS-495 | New Ross (West) 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.603 | 11 | 0.148 | 3 | 0.148 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 387.4452
1487 | 1487 | CL3-334 | TIPPERARY | TIPPERARY | SS-540 | Templemore 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.665 | 9 | 0.185 | 3 | 0.185 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 342.819
1488 | 1488 | CL3-335 | TIPPERARY | TIPPERARY | SS-540 | Templemore 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.728 | 8 | 0.28 | 3 | 0.28 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 317.7238
1489 | 1489 | CL3-336 | OFFALY | OFFALY | SS-168 | Derryiron 110kV Substation | EirGrid | 110000 |  |  | 6.071 | 7 | 0.536 | 3 | 0.536 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525 | 4.2 | 216.6548
1490 | 1490 | CL3-337 | CLARE | CLARE | SS-708 |  | EirGrid | 110000 | medium | 110000 | 3.067 | 4 | 0.216 | 3 | 0.216 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581 | 4.2 | 425.0881
1491 | 1491 | CL3-338 | DONEGAL | DONEGAL | SS-686 | Dungloe 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.182 | 13 | 0.113 | 3 | 0.113 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718 | 4.2 | 387.4452
1492 | 1492 | CL3-339 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 11.803 | 12 | 0.09 | 3 | 0.09 | 4.2 | 4.2 | 2048870 | 7 | 487826.1905 | 2.0499 | 4.2 | 367.9143
1493 | 1493 | CL3-340 | CAVAN | CAVAN | SS-097 | Corderry 110kV Substation | EirGrid | 110000 |  |  | 13.683 | 14 | 0.218 | 3 | 0.218 | 4.2 | 4.2 | 2154270 | 7 | 512921.4286 | 1.9496 | 4.2 | 487.8262
1494 | 1494 | CL3-341 | LEITRIM | LEITRIM | SS-097 | Corderry 110kV Substation | EirGrid | 110000 |  |  | 8.587 | 9 | 0.21 | 3 | 0.21 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213 | 4.2 | 512.9214
1495 | 1495 | CL3-342 | CAVAN | CAVAN | SS-110 | Corraclassy 110kV Substation | EirGrid | 110000 |  |  | 7.812 | 8 | 0.289 | 3 | 0.289 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285 | 4.2 | 450.1833
1496 | 1496 | CL3-343 | LEITRIM | LEITRIM | SS-304 | Arigna 110kV Substation | EirGrid | 110000 | 110000 | 20000 | 10.843 | 11 | 0.264 | 3 | 0.264 | 4.2 | 4.2 | 1996170 | 7 | 475278.5714 | 2.104 | 4.2 | 437.6357
1497 | 1497 | CL3-344 | CAVAN | CAVAN | SS-110 | Corraclassy 110kV Substation | EirGrid | 110000 |  |  | 4.169 | 5 | 0.236 | 3 | 0.236 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5 | 4.2 | 475.2786
1498 | 1498 | CL3-345 | DONEGAL | DONEGAL | SS-086 | Meentycat 110kV Substation | EirGrid | 110000 | low | 110000 | 2.675 | 3 | 0.403 | 3 | 0.403 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674 | 4.2 | 399.9929
1499 | 1499 | CL3-346 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 12.127 | 13 | 0.168 | 3 | 0.168 | 4.2 | 4.2 | 2101570 | 7 | 500373.8095 | 1.9985 | 4.2 | 374.8976
1500 | 1500 | CL3-347 | DONEGAL | DONEGAL | SS-690 | Stranrolar 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.626 | 9 | 0.092 | 3 | 0.092 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 500.3738
1501 | 1501 | CL3-348 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 10.274 | 11 | 0.334 | 3 | 0.334 | 4.2 | 4.2 | 1996170 | 7 | 475278.5714 | 2.104 | 4.2 | 317.7238
1502 | 1502 | CL3-349 | DONEGAL | DONEGAL | SS-102 | Binbane 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 3.858 | 4 | 0.446 | 3 | 0.446 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581 | 4.2 | 475.2786
1503 | 1503 | CL3-350 | GALWAY | GALWAY | SS-623 | Uggool 110kV Substation | EirGrid | 110000 | 33000 | 110000 | 1.45 | 2 | 0.22 | 3 | 0.22 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341 | 4.2 | 387.4452
1504 | 1504 | CL3-351 | WATERFORD | WATERFORD | SS-455 | Ardfinnan 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.521 | 11 | 0.502 | 3 | 0.502 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 319.0667
1505 | 1505 | CL3-352 | WATERFORD | WATERFORD | SS-659 | Spa Road 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 5.23 | 6 | 0.146 | 3 | 0.146 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 342.819
1506 | 1506 | CL3-353 | WATERFORD | WATERFORD | SS-064 | Ballydine 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 9.301 | 10 | 0.299 | 3 | 0.299 | 4.2 | 4.2 | 1943470 | 7 | 462730.9524 | 2.1611 | 4.2 | 183.1929
1507 | 1507 | CL3-354 | WATERFORD | WATERFORD | SS-064 | Ballydine 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.591 | 9 | 0.133 | 3 | 0.133 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213 | 4.2 | 462.731
1508 | 1508 | CL3-355 | WATERFORD | WATERFORD | SS-064 | Ballydine 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 9.748 | 10 | 0.364 | 3 | 0.364 | 4.2 | 4.2 | 1943470 | 7 | 462730.9524 | 2.1611 | 4.2 | 450.1833
1509 | 1509 | CL3-356 | WATERFORD | WATERFORD | SS-205 | Dungarvan 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.268 | 9 | 0.51 | 3 | 0.51 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213 | 4.2 | 462.731
1510 | 1510 | CL3-357 | WATERFORD | WATERFORD | SS-659 | Spa Road 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 12.408 | 13 | 0.167 | 3 | 0.167 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718 | 4.2 | 450.1833
1511 | 1511 | CL3-358 | WATERFORD | WATERFORD | SS-659 | Spa Road 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 11.469 | 12 | 0.133 | 3 | 0.133 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 367.9143
1512 | 1512 | CL3-359 | WATERFORD | WATERFORD | SS-505 | Kilmacthomas 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.436 | 10 | 0.217 | 3 | 0.217 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 4.2 | 355.3667
1513 | 1513 | CL3-360 | WATERFORD | WATERFORD | SS-064 | Ballydine 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.448 | 6 | 0.282 | 3 | 0.282 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424 | 4.2 | 330.2714
1514 | 1514 | CL3-361 | WATERFORD | WATERFORD | SS-205 | Dungarvan 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 4.755 | 5 | 0.16 | 3 | 0.16 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5 | 4.2 | 412.5405
1515 | 1515 | CL3-362 | CORK | LIMERICK | SS-695 | Castlepook 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 2.432 | 3 | 0.213 | 3 | 0.213 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 399.9929
1516 | 1516 | CL3-363 | LIMERICK | LIMERICK | SS-257 | Kilshanny 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.122 | 12 | 0.207 | 3 | 0.207 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 133
1517 | 1517 | CL3-364 | TIPPERARY | LIMERICK | SS-585 | Kilross Road 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.536 | 11 | 0.186 | 3 | 0.186 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 355.3667
1518 | 1518 | CL3-365 | TIPPERARY | TIPPERARY | SS-315 | Cahir 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 4.593 | 5 | 0.439 | 3 | 0.439 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 342.819
1519 | 1519 | CL3-366 | TIPPERARY | TIPPERARY | SS-257 | Kilshanny 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.753 | 10 | 0.206 | 3 | 0.206 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 4.2 | 166.4619
1520 | 1520 | CL3-367 | CORK | CORK | SS-583 | Castletownroche 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.691 | 5 | 0.359 | 3 | 0.359 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 330.2714
1521 | 1521 | CL3-368 | CORK | CORK | SS-583 | Castletownroche 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.841 | 4 | 0.1 | 3 | 0.1 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 166.4619
1522 | 1522 | CL3-369 | CARLOW | CARLOW | SS-492 | Graigue 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.958 | 9 | 0.187 | 3 | 0.187 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 149.731
1523 | 1523 | CL3-370 | CARLOW | CARLOW | SS-492 | Graigue 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.859 | 9 | 0.116 | 3 | 0.116 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 317.7238
1524 | 1524 | CL3-371 | WEXFORD | WEXFORD | SS-492 | Graigue 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.913 | 10 | 0.115 | 3 | 0.115 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 4.2 | 317.7238
1525 | 1525 | CL3-372 | TIPPERARY | TIPPERARY | SS-692 | Hollyford 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.806 | 2 | 0.182 | 3 | 0.182 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007 | 4.2 | 330.2714
1526 | 1526 | CL3-373 | TIPPERARY | TIPPERARY | SS-692 | Hollyford 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.848 | 3 | 0.497 | 3 | 0.497 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 116.269
1527 | 1527 | CL3-374 | TIPPERARY | TIPPERARY | SS-692 | Hollyford 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.929 | 3 | 0.109 | 3 | 0.109 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 133
1528 | 1528 | CL3-375 | CLARE | CLARE | SS-653 | Cranny 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 2.652 | 3 | 0.553 | 3 | 0.553 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 133
1529 | 1529 | CL3-376 | TIPPERARY | TIPPERARY | SS-551 | Dallow 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 3.595 | 4 | 0.414 | 3 | 0.414 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581 | 4.2 | 133
1530 | 1530 | CL3-377 | KILKENNY | KILKENNY | SS-016 | Portlaw 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.636 | 9 | 0.117 | 3 | 0.117 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 387.4452
1531 | 1531 | CL3-378 | TIPPERARY | TIPPERARY | SS-295 | Doon 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.135 | 6 | 0.303 | 3 | 0.303 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424 | 4.2 | 317.7238
1532 | 1532 | CL3-379 | TIPPERARY | TIPPERARY | SS-295 | Doon 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 9.363 | 10 | 0.143 | 3 | 0.143 | 4.2 | 4.2 | 1943470 | 7 | 462730.9524 | 2.1611 | 4.2 | 412.5405
1533 | 1533 | CL3-380 | TIPPERARY | TIPPERARY | SS-295 | Doon 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 10.211 | 11 | 0.127 | 3 | 0.127 | 4.2 | 4.2 | 1996170 | 7 | 475278.5714 | 2.104 | 4.2 | 462.731
1534 | 1534 | CL3-381 | TIPPERARY | TIPPERARY | SS-459 | Ballycrossaun 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.279 | 9 | 0.535 | 3 | 0.535 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 475.2786
1535 | 1535 | CL3-382 | LAOIS | LAOIS | SS-275 | Mountrath ESB Telecoms 38kV Radio Site | ESB Networks | 38000 | 38000 | low | 9.596 | 10 | 0.266 | 3 | 0.266 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 4.2 | 317.7238
1536 | 1536 | CL3-383 | LAOIS | LAOIS | SS-275 | Mountrath ESB Telecoms 38kV Radio Site | ESB Networks | 38000 | 38000 | low | 11.076 | 12 | 0.321 | 3 | 0.321 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 330.2714
1537 | 1537 | CL3-384 | OFFALY | OFFALY | SS-084 | Birr 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.522 | 12 | 0.103 | 3 | 0.103 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 355.3667
1538 | 1538 | CL3-385 | GALWAY | GALWAY | SS-175 | Ballygar 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.088 | 11 | 0.115 | 3 | 0.115 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 355.3667
1539 | 1539 | CL3-386 | GALWAY | GALWAY | SS-175 | Ballygar 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.87 | 8 | 0.43 | 3 | 0.43 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 342.819
1540 | 1540 | CL3-387 | CORK | CORK | SS-668 | Coomataggart 110 kV Substation | EirGrid | 110000 | low | 110000 | 11.217 | 12 | 0.109 | 3 | 0.109 | 4.2 | 4.2 | 2048870 | 7 | 487826.1905 | 2.0499 | 4.2 | 216.6548
1541 | 1541 | CL3-388 | KILKENNY | KILKENNY | SS-538 | Galmoy 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.085 | 11 | 0.388 | 3 | 0.388 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 487.8262
1542 | 1542 | CL3-389 | LIMERICK | LIMERICK | SS-069 | Garryspillane 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.922 | 8 | 0.255 | 3 | 0.255 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 342.819
1543 | 1543 | CL3-390 | LAOIS | LAOIS | SS-470 | Mountmellick 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.019 | 6 | 0.292 | 3 | 0.292 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 216.6548
1544 | 1544 | CL3-391 | KILDARE | KILDARE | SS-657 | Edenderry 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.097 | 5 | 0.417 | 3 | 0.417 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 183.1929
1545 | 1545 | CL3-392 | WEXFORD | WEXFORD | SS-616 | Ballinvally 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 7.429 | 8 | 0.205 | 3 | 0.205 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 166.4619
1546 | 1546 | CL3-393 | CORK | CORK | SS-197 | Midleton 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.157 | 9 | 0.279 | 3 | 0.279 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213 | 4.2 | 216.6548
1547 | 1547 | CL3-394 | CLARE | CLARE | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.397 | 11 | 0.515 | 3 | 0.515 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 450.1833
1548 | 1548 | CL3-395 | CLARE | CLARE | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.042 | 12 | 0.22 | 3 | 0.22 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 342.819
1549 | 1549 | CL3-396 | WATERFORD | WATERFORD | SS-622 | Barranafaddock 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.997 | 5 | 0.145 | 3 | 0.145 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 355.3667
1550 | 1550 | CL3-397 | KILKENNY | KILKENNY | SS-194 | Kilkenny 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.551 | 11 | 0.222 | 3 | 0.222 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 166.4619
1551 | 1551 | CL3-398 | KILKENNY | KILKENNY | SS-489 | Ballyhale 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.257 | 3 | 0.38 | 3 | 0.38 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 342.819
1552 | 1552 | CL3-399 | KILKENNY | KILKENNY | SS-489 | Ballyhale 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.835 | 8 | 0.156 | 3 | 0.156 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 133
1553 | 1553 | CL3-400 | GALWAY | GALWAY | SS-459 | Ballycrossaun 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.617 | 5 | 0.359 | 3 | 0.359 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 216.6548
1554 | 1554 | CL3-401 | CLARE | CLARE | SS-503 | Scariff 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 4.989 | 5 | 0.725 | 3 | 0.725 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 166.4619
1555 | 1555 | CL3-402 | CLARE | CLARE | SS-503 | Scariff 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.306 | 8 | 0.265 | 3 | 0.265 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 166.4619
1556 | 1556 | CL3-403 | CLARE | CLARE | SS-483 | Birdhill 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.14 | 8 | 0.239 | 3 | 0.239 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 216.6548
1557 | 1557 | CL3-404 | TIPPERARY | LIMERICK | SS-585 | Kilross Road 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.512 | 10 | 0.215 | 3 | 0.215 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 4.2 | 216.6548
1558 | 1558 | CL3-405 | LAOIS | LAOIS | SS-034 | Athy 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 12.085 | 13 | 0.214 | 3 | 0.214 | 4.2 | 4.2 | 2101570 | 7 | 500373.8095 | 1.9985 | 4.2 | 330.2714
1559 | 1559 | CL3-406 | WESTMEATH | WESTMEATH | SS-467 | Clara 38kV Substation | ESB Networks | 38000 | 38000 | 20000;10000 | 6.219 | 7 | 0.549 | 3 | 0.549 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 500.3738
1560 | 1560 | CL3-407 | KILDARE | KILDARE | SS-228 | Dunfierth 110kV Substation | EirGrid | 110000 | 110000 | 20000 | 7.812 | 8 | 0.262 | 3 | 0.262 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285 | 4.2 | 199.9238
1561 | 1561 | CL3-408 | MAYO | MAYO | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 12.217 | 13 | 0.091 | 3 | 0.091 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718 | 4.2 | 437.6357
1562 | 1562 | CL3-409 | SLIGO | SLIGO | SS-074 | Tobercurry 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.502 | 6 | 0.424 | 3 | 0.424 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 367.9143
1563 | 1563 | CL3-410 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.811 | 6 | 0.097 | 3 | 0.097 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 183.1929
1564 | 1564 | CL3-411 | GALWAY | GALWAY | SS-175 | Ballygar 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.493 | 9 | 0.211 | 3 | 0.211 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 183.1929
1565 | 1565 | CL3-412 | WESTMEATH | WESTMEATH | SS-246 | Loughanalla 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 5.828 | 6 | 0.105 | 3 | 0.105 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 317.7238
1566 | 1566 | CL3-413 | CAVAN | CAVAN | SS-081 | Killeshandra 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.7 | 4 | 0.307 | 3 | 0.307 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 183.1929
1567 | 1567 | CL3-414 | CAVAN | CAVAN | SS-081 | Killeshandra 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.527 | 5 | 0.283 | 3 | 0.283 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 149.731
1568 | 1568 | CL3-415 | MEATH | MEATH | SS-059 | Kinnegad 110kV | EirGrid | 110000 |  |  | 8.002 | 9 | 0.142 | 3 | 0.142 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213 | 4.2 | 166.4619
1569 | 1569 | CL3-416 | ROSCOMMON | ROSCOMMON | SS-457 | Cloondara 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.065 | 3 | 0.497 | 3 | 0.497 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 450.1833
1570 | 1570 | CL3-417 | WESTMEATH | WESTMEATH | SS-232 | Bushfield 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.043 | 10 | 0.536 | 3 | 0.536 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 4.2 | 133
1571 | 1571 | CL3-418 | DONEGAL | DONEGAL | SS-118 | Sorne Hill 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 3.486 | 4 | 3.659 | 3 | 2.7443 | 16.8 | 16.8 | 1875790 | 8 | 111654.1667 | 8.9562 | 4.2 | 330.2714
1572 | 1572 | CL3-419 | DONEGAL | DONEGAL | SS-690 | Stranrolar 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.945 | 9 | 1.018 | 3 | 1.018 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 16.8 | 111.6542
1573 | 1573 | CL3-420 | DONEGAL | DONEGAL | SS-690 | Stranrolar 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.768 | 9 | 0.485 | 3 | 0.485 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 317.7238
1574 | 1574 | CL3-421 | DONEGAL | DONEGAL | SS-083 | Golagh 110kV Substation | EirGrid | 110000 | 38000 | 110000 | 6.614 | 7 | 0.737 | 3 | 0.737 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525 | 4.2 | 317.7238
1575 | 1575 | CL3-422 | DONEGAL | DONEGAL | SS-083 | Golagh 110kV Substation | EirGrid | 110000 | 38000 | 110000 | 4.88 | 5 | 0.603 | 3 | 0.603 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5 | 4.2 | 425.0881
1576 | 1576 | CL3-423 | DONEGAL | DONEGAL | SS-617 | Mulreavy 110kV Substation | EirGrid | 110000 | 33000 | 110000 | 6.757 | 7 | 4.484 | 3 | 3.363 | 21 | 21 | 2086600 | 8 | 99361.9048 | 10.0642 | 4.2 | 399.9929
1577 | 1577 | CL3-424 | DONEGAL | DONEGAL | SS-617 | Mulreavy 110kV Substation | EirGrid | 110000 | 33000 | 110000 | 11.409 | 12 | 2.52 | 3 | 1.89 | 12.6 | 12.6 | 2048870 | 7 | 162608.7302 | 6.1497 | 21 | 99.3619
1578 | 1578 | CL3-425 | DONEGAL | DONEGAL | SS-087 | Cliff 110kV Substation | EirGrid | 110000 | low | 110000 | 3.306 | 4 | 1.921 | 3 | 1.4407 | 8.4 | 8.4 | 1627270 | 7 | 193722.619 | 5.162 | 12.6 | 162.6087
1579 | 1579 | CL3-426 | CAVAN | CAVAN | SS-110 | Corraclassy 110kV Substation | EirGrid | 110000 |  |  | 4.611 | 5 | 2.859 | 3 | 2.1442 | 12.6 | 12.6 | 1679970 | 7 | 133330.9524 | 7.5001 | 8.4 | 193.7226
1580 | 1580 | CL3-427 | CAVAN | CAVAN | SS-110 | Corraclassy 110kV Substation | EirGrid | 110000 |  |  | 8.743 | 9 | 2.396 | 3 | 1.797 | 12.6 | 12.6 | 1890770 | 7 | 150061.1111 | 6.664 | 12.6 | 133.331
1581 | 1581 | CL3-428 | CAVAN | CAVAN | SS-111 | Gortawee 110kV Station | EirGrid | 110000 | 110000 | low | 3.454 | 4 | 0.968 | 3 | 0.968 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581 | 12.6 | 150.0611
1582 | 1582 | CL3-429 | CAVAN | CAVAN | SS-110 | Corraclassy 110kV Substation | EirGrid | 110000 |  |  | 5.225 | 6 | 3.936 | 3 | 2.952 | 21 | 21 | 2016330 | 8 | 96015.7143 | 10.415 | 4.2 | 387.4452
1583 | 1583 | CL3-430 | LOUTH | LOUTH | SS-650 | Ballymascanlan 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.384 | 5 | 1.336 | 3 | 1.002 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 21 | 96.0157
1584 | 1584 | CL3-431 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 12.561 | 13 | 3.33 | 3 | 2.4975 | 16.8 | 16.8 | 1261300 | 4 | 75077.381 | 13.3196 | 4.2 | 166.4619
1585 | 1585 | CL3-432 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 12.402 | 13 | 2.196 | 3 | 1.647 | 8.4 | 8.4 | 1590600 | 2 | 189357.1429 | 5.281 | 16.8 | 75.0774
1586 | 1586 | CL3-433 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 13.715 | 14 | 0.983 | 3 | 0.983 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284 | 8.4 | 189.3571
1587 | 1587 | CL3-434 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.518 | 11 | 0.941 | 3 | 0.941 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 380.4619
1588 | 1588 | CL3-435 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.278 | 11 | 0.332 | 3 | 0.332 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 342.819
1589 | 1589 | CL3-436 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.018 | 8 | 0.58 | 3 | 0.58 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 342.819
1590 | 1590 | CL3-437 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.851 | 9 | 1.702 | 3 | 1.2765 | 8.4 | 8.4 | 1379800 | 2 | 164261.9048 | 6.0878 | 4.2 | 216.6548
1591 | 1591 | CL3-438 | CORK | CORK | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.711 | 9 | 1.142 | 3 | 1.142 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 8.4 | 164.2619
1592 | 1592 | CL3-439 | CORK | CORK | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.059 | 8 | 2.992 | 3 | 2.244 | 12.6 | 12.6 | 909950 | 4 | 72218.254 | 13.8469 | 4.2 | 317.7238
1593 | 1593 | CL3-440 | KERRY | KERRY | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.349 | 10 | 1.558 | 3 | 1.1685 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 12.6 | 72.2183
1594 | 1594 | CL3-441 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 12.241 | 13 | 0.768 | 3 | 0.768 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718 | 4.2 | 330.2714
1595 | 1595 | CL3-442 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.199 | 5 | 0.791 | 3 | 0.791 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 367.9143
1596 | 1596 | CL3-443 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 3.997 | 4 | 0.612 | 3 | 0.612 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 166.4619
1597 | 1597 | CL3-444 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.65 | 7 | 0.922 | 3 | 0.922 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 149.731
1598 | 1598 | CL3-445 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 9.908 | 10 | 1.197 | 3 | 1.197 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 4.2 | 199.9238
1599 | 1599 | CL3-446 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 13.387 | 14 | 4.108 | 3 | 3.081 | 21 | 21 | 1331570 | 4 | 63408.0952 | 15.7709 | 4.2 | 330.2714
1600 | 1600 | CL3-447 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 18.146 | 19 | 1.993 | 3 | 1.4948 | 8.4 | 8.4 | 1906800 | 2 | 227000 | 4.4053 | 21 | 63.4081
1601 | 1601 | CL3-448 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.718 | 16 | 3.601 | 3 | 2.7008 | 16.8 | 16.8 | 1472110 | 4 | 87625.5952 | 11.4122 | 8.4 | 227
1602 | 1602 | CL3-449 | KERRY | KERRY | SS-321 | Milltown 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 17.503 | 18 | 1.262 | 3 | 0.9465 | 4.2 | 4.2 | 1808740 | 1 | 430652.381 | 2.3221 | 16.8 | 87.6256
1603 | 1603 | CL3-450 | KERRY | KERRY | SS-321 | Milltown 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 17.597 | 18 | 1.096 | 3 | 1.096 | 4.2 | 4.2 | 1808740 | 1 | 430652.381 | 2.3221 | 4.2 | 430.6524
1604 | 1604 | CL3-451 | KERRY | KERRY | SS-387 | Coolcorcoran 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.51 | 12 | 1.123 | 3 | 1.123 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 430.6524
1605 | 1605 | CL3-452 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.58 | 14 | 0.767 | 3 | 0.767 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284 | 4.2 | 355.3667
1606 | 1606 | CL3-453 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.536 | 14 | 0.504 | 3 | 0.504 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284 | 4.2 | 380.4619
1607 | 1607 | CL3-454 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.622 | 14 | 1.884 | 3 | 1.413 | 8.4 | 8.4 | 1643300 | 2 | 195630.9524 | 5.1117 | 4.2 | 380.4619
1608 | 1608 | CL3-455 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.408 | 10 | 2.99 | 3 | 2.2425 | 12.6 | 12.6 | 1469550 | 3 | 116630.9524 | 8.5741 | 8.4 | 195.631
1609 | 1609 | CL3-456 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.75 | 13 | 0.615 | 3 | 0.615 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718 | 12.6 | 116.631
1610 | 1610 | CL3-457 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.814 | 10 | 0.858 | 3 | 0.858 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 4.2 | 367.9143
1611 | 1611 | CL3-458 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.334 | 13 | 0.337 | 3 | 0.337 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718 | 4.2 | 330.2714
1612 | 1612 | CL3-459 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 16.18 | 17 | 2.277 | 3 | 1.7078 | 8.4 | 8.4 | 1801400 | 2 | 214452.381 | 4.663 | 4.2 | 367.9143
1613 | 1613 | CL3-460 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 17.927 | 18 | 1.725 | 3 | 1.2938 | 8.4 | 8.4 | 1854100 | 2 | 220726.1905 | 4.5305 | 8.4 | 214.4524
1614 | 1614 | CL3-461 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 17.832 | 18 | 0.482 | 3 | 0.482 | 4.2 | 4.2 | 1808740 | 1 | 430652.381 | 2.3221 | 8.4 | 220.7262
1615 | 1615 | CL3-462 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 16.211 | 17 | 0.976 | 3 | 0.976 | 4.2 | 4.2 | 1756040 | 1 | 418104.7619 | 2.3917 | 4.2 | 430.6524
1616 | 1616 | CL3-463 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 15.74 | 16 | 2.156 | 3 | 1.617 | 8.4 | 8.4 | 1748700 | 2 | 208178.5714 | 4.8036 | 4.2 | 418.1048
1617 | 1617 | CL3-464 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 12.906 | 13 | 7.55 | 3 | 5.6625 | 37.8 | 37.8 | 1794170 | 6 | 47464.8148 | 21.0682 | 8.4 | 208.1786
1618 | 1618 | CL3-465 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 12.709 | 13 | 1.795 | 3 | 1.3462 | 8.4 | 8.4 | 1590600 | 2 | 189357.1429 | 5.281 | 37.8 | 47.4648
1619 | 1619 | CL3-466 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 13.119 | 14 | 1.102 | 3 | 1.102 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284 | 8.4 | 189.3571
1620 | 1620 | CL3-467 | KERRY | KERRY | SS-321 | Milltown 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 15.274 | 16 | 1.035 | 3 | 1.035 | 4.2 | 4.2 | 1703340 | 1 | 405557.1429 | 2.4657 | 4.2 | 380.4619
1621 | 1621 | CL3-468 | KERRY | KERRY | SS-157 | Oughtragh 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 14.717 | 15 | 2.795 | 3 | 2.0962 | 12.6 | 12.6 | 2206970 | 7 | 175156.3492 | 5.7092 | 4.2 | 405.5571
1622 | 1622 | CL3-469 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 13.176 | 14 | 0.502 | 3 | 0.502 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284 | 12.6 | 175.1563
1623 | 1623 | CL3-470 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 12.147 | 13 | 8.363 | 3 | 6.2722 | 42 | 42 | 1794170 | 6 | 42718.3333 | 23.4092 | 4.2 | 380.4619
1624 | 1624 | CL3-471 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 10.162 | 11 | 0.812 | 3 | 0.812 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 42 | 42.7183
1625 | 1625 | CL3-472 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 9.951 | 10 | 2.419 | 3 | 1.8142 | 12.6 | 12.6 | 1469550 | 3 | 116630.9524 | 8.5741 | 4.2 | 342.819
1626 | 1626 | CL3-473 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 9.19 | 10 | 1.219 | 3 | 0.91425 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 12.6 | 116.631
1627 | 1627 | CL3-474 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 10.49 | 11 | 5.228 | 3 | 3.921 | 25.2 | 25.2 | 1324920 | 5 | 52576.1905 | 19.02 | 4.2 | 330.2714
1628 | 1628 | CL3-475 | KERRY | KERRY | SS-072 | Clonkeen 110kV Substation | EirGrid | 110000 |  |  | 7.558 | 8 | 2.816 | 3 | 2.112 | 12.6 | 12.6 | 1838070 | 7 | 145878.5714 | 6.855 | 25.2 | 52.5762
1629 | 1629 | CL3-476 | KERRY | KERRY | SS-637 | Kilgarvan 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.399 | 7 | 1.865 | 3 | 1.3987 | 8.4 | 8.4 | 839680 | 4 | 99961.9048 | 10.0038 | 12.6 | 145.8786
1630 | 1630 | CL3-477 | KERRY | KERRY | SS-637 | Kilgarvan 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.591 | 6 | 0.913 | 3 | 0.913 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 8.4 | 99.9619
1631 | 1631 | CL3-478 | KERRY | KERRY | SS-637 | Kilgarvan 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.427 | 7 | 2.819 | 3 | 2.1143 | 12.6 | 12.6 | 839680 | 4 | 66641.2698 | 15.0057 | 4.2 | 183.1929
1632 | 1632 | CL3-479 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.489 | 5 | 1.066 | 3 | 1.066 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 12.6 | 66.6413
1633 | 1633 | CL3-480 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.458 | 6 | 1.827 | 3 | 1.3702 | 8.4 | 8.4 | 769410 | 4 | 91596.4286 | 10.9175 | 4.2 | 166.4619
1634 | 1634 | CL3-481 | KERRY | KERRY | SS-160 | Woodford 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.96 | 8 | 2.69 | 3 | 2.0175 | 12.6 | 12.6 | 909950 | 4 | 72218.254 | 13.8469 | 8.4 | 91.5964
1635 | 1635 | CL3-482 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.93 | 5 | 2.304 | 3 | 1.728 | 8.4 | 8.4 | 699140 | 4 | 83230.9524 | 12.0148 | 12.6 | 72.2183
1636 | 1636 | CL3-483 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.024 | 15 | 1.44 | 3 | 1.08 | 4.2 | 4.2 | 1650640 | 1 | 393009.5238 | 2.5445 | 8.4 | 83.231
1637 | 1637 | CL3-484 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 16.668 | 17 | 2.46 | 3 | 1.845 | 12.6 | 12.6 | 1838450 | 3 | 145908.7302 | 6.8536 | 4.2 | 393.0095
1638 | 1638 | CL3-485 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 15.478 | 16 | 1.197 | 3 | 1.197 | 4.2 | 4.2 | 1703340 | 1 | 405557.1429 | 2.4657 | 12.6 | 145.9087
1639 | 1639 | CL3-486 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 12.104 | 13 | 4.149 | 3 | 3.1117 | 21 | 21 | 1261300 | 4 | 60061.9048 | 16.6495 | 4.2 | 405.5571
1640 | 1640 | CL3-487 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 8.316 | 9 | 2.383 | 3 | 1.7873 | 12.6 | 12.6 | 1416850 | 3 | 112448.4127 | 8.893 | 21 | 60.0619
1641 | 1641 | CL3-488 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 10.915 | 11 | 1.394 | 3 | 1.0455 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 12.6 | 112.4484
1642 | 1642 | CL3-489 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 9.185 | 10 | 2.781 | 3 | 2.0857 | 12.6 | 12.6 | 1469550 | 3 | 116630.9524 | 8.5741 | 4.2 | 342.819
1643 | 1643 | CL3-490 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 9.868 | 10 | 1.379 | 3 | 1.0343 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 12.6 | 116.631
1644 | 1644 | CL3-491 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 7.454 | 8 | 0.451 | 3 | 0.451 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 330.2714
1645 | 1645 | CL3-492 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 6.495 | 7 | 1.267 | 3 | 0.95025 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 216.6548
1646 | 1646 | CL3-493 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.824 | 4 | 2.088 | 3 | 1.566 | 8.4 | 8.4 | 628870 | 4 | 74865.4762 | 13.3573 | 4.2 | 199.9238
1647 | 1647 | CL3-494 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.359 | 5 | 2.119 | 3 | 1.5893 | 8.4 | 8.4 | 699140 | 4 | 83230.9524 | 12.0148 | 8.4 | 74.8655
1648 | 1648 | CL3-495 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.577 | 2 | 1.265 | 3 | 0.94875 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007 | 8.4 | 83.231
1649 | 1649 | CL3-496 | CORK | CORK | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 7.131 | 8 | 0.595 | 3 | 0.595 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 116.269
1650 | 1650 | CL3-497 | CORK | CORK | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.166 | 5 | 1.736 | 3 | 1.302 | 8.4 | 8.4 | 699140 | 4 | 83230.9524 | 12.0148 | 4.2 | 216.6548
1651 | 1651 | CL3-498 | CORK | CORK | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 2.783 | 3 | 1.013 | 3 | 1.013 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 8.4 | 83.231
1652 | 1652 | CL3-499 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.849 | 5 | 1.557 | 3 | 1.1677 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 133
1653 | 1653 | CL3-500 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.871 | 7 | 1.557 | 3 | 1.1677 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 166.4619
1654 | 1654 | CL3-501 | KERRY | KERRY | SS-637 | Kilgarvan 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.637 | 9 | 0.897 | 3 | 0.897 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 199.9238
1655 | 1655 | CL3-502 | KERRY | KERRY | SS-637 | Kilgarvan 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.071 | 8 | 1.803 | 3 | 1.3522 | 8.4 | 8.4 | 909950 | 4 | 108327.381 | 9.2313 | 4.2 | 317.7238
1656 | 1656 | CL3-503 | KERRY | KERRY | SS-321 | Milltown 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 3.149 | 4 | 0.577 | 3 | 0.577 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 8.4 | 108.3274
1657 | 1657 | CL3-504 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.308 | 6 | 3.904 | 3 | 2.928 | 21 | 21 | 769410 | 4 | 36638.5714 | 27.2936 | 4.2 | 149.731
1658 | 1658 | CL3-505 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.163 | 8 | 3.114 | 3 | 2.3355 | 16.8 | 16.8 | 909950 | 4 | 54163.6905 | 18.4626 | 21 | 36.6386
1659 | 1659 | CL3-506 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.321 | 9 | 3.456 | 3 | 2.592 | 16.8 | 16.8 | 980220 | 4 | 58346.4286 | 17.139 | 16.8 | 54.1637
1660 | 1660 | CL3-507 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.517 | 8 | 0.884 | 3 | 0.884 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 16.8 | 58.3464
1661 | 1661 | CL3-508 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.021 | 10 | 1.764 | 3 | 1.323 | 8.4 | 8.4 | 1432500 | 2 | 170535.7143 | 5.8639 | 4.2 | 216.6548
1662 | 1662 | CL3-509 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.152 | 6 | 2.335 | 3 | 1.7512 | 8.4 | 8.4 | 769410 | 4 | 91596.4286 | 10.9175 | 8.4 | 170.5357
1663 | 1663 | CL3-510 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.852 | 10 | 2.262 | 3 | 1.6965 | 8.4 | 8.4 | 1432500 | 2 | 170535.7143 | 5.8639 | 8.4 | 91.5964
1664 | 1664 | CL3-511 | KERRY | KERRY | SS-321 | Milltown 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.104 | 9 | 1.605 | 3 | 1.2037 | 8.4 | 8.4 | 1379800 | 2 | 164261.9048 | 6.0878 | 8.4 | 170.5357
1665 | 1665 | CL3-512 | KERRY | KERRY | SS-321 | Milltown 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.488 | 10 | 0.871 | 3 | 0.871 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 8.4 | 164.2619
1666 | 1666 | CL3-513 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.965 | 9 | 1.233 | 3 | 0.92475 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 330.2714
1667 | 1667 | CL3-514 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 2.277 | 3 | 0.622 | 3 | 0.622 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 317.7238
1668 | 1668 | CL3-515 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.778 | 7 | 0.258 | 3 | 0.258 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 133
1669 | 1669 | CL3-516 | LIMERICK | LIMERICK | SS-378 | Foynes 38kV Substation | ESB Networks | 38000 | 38000 | low | 1.955 | 2 | 0.703 | 3 | 0.703 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007 | 4.2 | 199.9238
1670 | 1670 | CL3-517 | LIMERICK | LIMERICK | SS-144 | Monateen 110kV Substation | EirGrid | 110000 |  |  | 6.628 | 7 | 2.567 | 3 | 1.9253 | 12.6 | 12.6 | 1785370 | 7 | 141696.0317 | 7.0574 | 4.2 | 116.269
1671 | 1671 | CL3-518 | LIMERICK | LIMERICK | SS-283 | Mungret | EirGrid | 110000 | 110000 | low | 2.492 | 3 | 1.214 | 3 | 0.9105 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674 | 12.6 | 141.696
1672 | 1672 | CL3-519 | CLARE | CLARE | SS-673 | Drumquin 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 3.723 | 4 | 0.601 | 3 | 0.601 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 374.8976
1673 | 1673 | CL3-520 | CLARE | CLARE | SS-673 | Drumquin 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 3.032 | 4 | 1.018 | 3 | 1.018 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 149.731
1674 | 1674 | CL3-521 | CLARE | CLARE | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 17.9 | 18 | 0.612 | 3 | 0.612 | 4.2 | 4.2 | 1808740 | 1 | 430652.381 | 2.3221 | 4.2 | 149.731
1675 | 1675 | CL3-522 | CLARE | CLARE | SS-141 | Ennis North 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 13.238 | 14 | 3.107 | 3 | 2.3303 | 16.8 | 16.8 | 1331570 | 4 | 79260.119 | 12.6167 | 4.2 | 430.6524
1676 | 1676 | CL3-523 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.133 | 6 | 3.191 | 3 | 2.3933 | 16.8 | 16.8 | 769410 | 4 | 45798.2143 | 21.8349 | 16.8 | 79.2601
1677 | 1677 | CL3-524 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.455 | 8 | 2.541 | 3 | 1.9057 | 12.6 | 12.6 | 909950 | 4 | 72218.254 | 13.8469 | 16.8 | 45.7982
1678 | 1678 | CL3-525 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.995 | 6 | 8.695 | 3 | 6.5213 | 46.2 | 46.2 | 2183320 | 11 | 47258.0087 | 21.1604 | 12.6 | 72.2183
1679 | 1679 | CL3-526 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.087 | 12 | 5.519 | 3 | 4.1393 | 29.4 | 29.4 | 1413750 | 5 | 48086.7347 | 20.7958 | 46.2 | 47.258
1680 | 1680 | CL3-527 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.414 | 11 | 2.498 | 3 | 1.8735 | 12.6 | 12.6 | 1522250 | 3 | 120813.4921 | 8.2772 | 29.4 | 48.0867
1681 | 1681 | CL3-528 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 12.726 | 13 | 1.094 | 3 | 1.094 | 4.2 | 4.2 | 2101570 | 7 | 500373.8095 | 1.9985 | 12.6 | 120.8135
1682 | 1682 | CL3-529 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.096 | 11 | 1.141 | 3 | 1.141 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 500.3738
1683 | 1683 | CL3-530 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.72 | 7 | 3.529 | 3 | 2.6467 | 16.8 | 16.8 | 839680 | 4 | 49980.9524 | 20.0076 | 4.2 | 342.819
1684 | 1684 | CL3-531 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.647 | 10 | 3.963 | 3 | 2.9722 | 21 | 21 | 1050490 | 4 | 50023.3333 | 19.9907 | 16.8 | 49.981
1685 | 1685 | CL3-532 | MAYO | MAYO | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 20.501 | 21 | 3.887 | 3 | 2.9152 | 21 | 21 | 1823460 | 4 | 86831.4286 | 11.5166 | 21 | 50.0233
1686 | 1686 | CL3-533 | MAYO | GALWAY | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 19.671 | 20 | 0.941 | 3 | 0.941 | 4.2 | 4.2 | 1914140 | 1 | 455747.619 | 2.1942 | 21 | 86.8314
1687 | 1687 | CL3-534 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 17.823 | 18 | 2.344 | 3 | 1.758 | 8.4 | 8.4 | 1854100 | 2 | 220726.1905 | 4.5305 | 4.2 | 455.7476
1688 | 1688 | CL3-535 | GALWAY | GALWAY | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 18.09 | 19 | 1.022 | 3 | 1.022 | 4.2 | 4.2 | 1861440 | 1 | 443200 | 2.2563 | 8.4 | 220.7262
1689 | 1689 | CL3-536 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 16.436 | 17 | 0.688 | 3 | 0.688 | 4.2 | 4.2 | 1756040 | 1 | 418104.7619 | 2.3917 | 4.2 | 443.2
1690 | 1690 | CL3-537 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.877 | 16 | 0.939 | 3 | 0.939 | 4.2 | 4.2 | 1703340 | 1 | 405557.1429 | 2.4657 | 4.2 | 418.1048
1691 | 1691 | CL3-538 | MAYO | MAYO | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 17.894 | 18 | 4.17 | 3 | 3.1275 | 21 | 21 | 1612650 | 4 | 76792.8571 | 13.022 | 4.2 | 405.5571
1692 | 1692 | CL3-539 | MAYO | MAYO | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 18.107 | 19 | 1.514 | 3 | 1.1355 | 4.2 | 4.2 | 1861440 | 1 | 443200 | 2.2563 | 21 | 76.7929
1693 | 1693 | CL3-540 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 17.296 | 18 | 1.008 | 3 | 1.008 | 4.2 | 4.2 | 1808740 | 1 | 430652.381 | 2.3221 | 4.2 | 443.2
1694 | 1694 | CL3-541 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 12.464 | 13 | 1.151 | 3 | 1.151 | 4.2 | 4.2 | 2101570 | 7 | 500373.8095 | 1.9985 | 4.2 | 430.6524
1695 | 1695 | CL3-542 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 23.74 | 24 | 0.719 | 3 | 0.719 | 4.2 | 4.2 | 2681270 | 7 | 638397.619 | 1.5664 | 4.2 | 500.3738
1696 | 1696 | CL3-543 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 20.671 | 21 | 0.843 | 3 | 0.843 | 4.2 | 4.2 | 1966840 | 1 | 468295.2381 | 2.1354 | 4.2 | 638.3976
1697 | 1697 | CL3-544 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 23.227 | 24 | 0.814 | 3 | 0.814 | 4.2 | 4.2 | 2681270 | 7 | 638397.619 | 1.5664 | 4.2 | 468.2952
1698 | 1698 | CL3-545 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 23.214 | 24 | 1.487 | 3 | 1.1153 | 4.2 | 4.2 | 2681270 | 7 | 638397.619 | 1.5664 | 4.2 | 638.3976
1699 | 1699 | CL3-546 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 18.716 | 19 | 1.534 | 3 | 1.1505 | 4.2 | 4.2 | 1861440 | 1 | 443200 | 2.2563 | 4.2 | 638.3976
1700 | 1700 | CL3-547 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 29.767 | 30 | 1.22 | 3 | 0.915 | 4.2 | 4.2 | 2997470 | 7 | 713683.3333 | 1.4012 | 4.2 | 443.2
1701 | 1701 | CL3-548 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 25.087 | 26 | 4.013 | 3 | 3.0097 | 21 | 21 | 3421730 | 8 | 162939.5238 | 6.1372 | 4.2 | 713.6833
1702 | 1702 | CL3-549 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 27.731 | 28 | 3.555 | 3 | 2.6663 | 16.8 | 16.8 | 3562270 | 8 | 212039.881 | 4.7161 | 21 | 162.9395
1703 | 1703 | CL3-550 | MAYO | MAYO | SS-317 | Newport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.898 | 12 | 2.296 | 3 | 1.722 | 8.4 | 8.4 | 1537900 | 2 | 183083.3333 | 5.462 | 16.8 | 212.0399
1704 | 1704 | CL3-551 | MAYO | MAYO | SS-170 | Derrynadivva 38kV Substation | ESB Networks | 38000 | low | 38000 | 10.787 | 11 | 3.823 | 3 | 2.8672 | 16.8 | 16.8 | 1120760 | 4 | 66711.9048 | 14.9898 | 8.4 | 183.0833
1705 | 1705 | CL3-552 | MAYO | MAYO | SS-317 | Newport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.975 | 10 | 5.846 | 3 | 4.3845 | 29.4 | 29.4 | 1236090 | 5 | 42043.8776 | 23.7847 | 16.8 | 66.7119
1706 | 1706 | CL3-553 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 12.74 | 13 | 5.267 | 3 | 3.9503 | 25.2 | 25.2 | 3108640 | 9 | 123358.7302 | 8.1064 | 29.4 | 42.0439
1707 | 1707 | CL3-554 | SLIGO | SLIGO | SS-302 | Carrowleagh 38kV Substation | ESB Networks | 38000 | low | 38000 | 5.119 | 6 | 9.462 | 3 | 7.0965 | 50.4 | 50.4 | 2183320 | 11 | 43319.8413 | 23.0841 | 25.2 | 123.3587
1708 | 1708 | CL3-555 | SLIGO | SLIGO | SS-075 | Cunghill 110kV Substation | EirGrid | 110000 | 110000 | medium | 8.035 | 9 | 3.563 | 3 | 2.6723 | 16.8 | 16.8 | 2227140 | 8 | 132567.8571 | 7.5433 | 50.4 | 43.3198
1709 | 1709 | CL3-556 | SLIGO | SLIGO | SS-074 | Tobercurry 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.229 | 9 | 1.111 | 3 | 1.111 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 16.8 | 132.5679
1710 | 1710 | CL3-557 | SLIGO | SLIGO | SS-042 | Ballytivnan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 11.682 | 12 | 4.114 | 3 | 3.0855 | 21 | 21 | 1191030 | 4 | 56715.7143 | 17.6318 | 4.2 | 317.7238
1711 | 1711 | CL3-558 | LEITRIM | LEITRIM | SS-227 | Bundoran 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.708 | 12 | 0.636 | 3 | 0.636 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 21 | 56.7157
1712 | 1712 | CL3-559 | SLIGO | SLIGO | SS-031 | Sligo 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 4.082 | 5 | 0.644 | 3 | 0.644 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5 | 4.2 | 355.3667
1713 | 1713 | CL3-560 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 5.057 | 6 | 2.5 | 3 | 1.875 | 12.6 | 12.6 | 769410 | 4 | 61064.2857 | 16.3762 | 4.2 | 399.9929
1714 | 1714 | CL3-561 | DONEGAL | DONEGAL | SS-252 | Killybegs 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 3.837 | 4 | 0.545 | 3 | 0.545 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 12.6 | 61.0643
1715 | 1715 | CL3-562 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 20.885 | 21 | 0.947 | 3 | 0.947 | 4.2 | 4.2 | 1966840 | 1 | 468295.2381 | 2.1354 | 4.2 | 149.731
1716 | 1716 | CL3-563 | ROSCOMMON | ROSCOMMON | SS-206 | Boyle 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.298 | 8 | 0.684 | 3 | 0.684 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 468.2952
1717 | 1717 | CL3-564 | ROSCOMMON | ROSCOMMON | SS-166 | Tonroe 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 3.877 | 4 | 0.904 | 3 | 0.904 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581 | 4.2 | 216.6548
1718 | 1718 | CL3-565 | SLIGO | LEITRIM | SS-128 | Garvagh Glebe 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 2.076 | 3 | 4.4 | 3 | 3.3 | 21 | 21 | 1550890 | 11 | 73851.9048 | 13.5406 | 4.2 | 387.4452
1719 | 1719 | CL3-566 | LEITRIM | LEITRIM | SS-128 | Garvagh Glebe 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 3.924 | 4 | 0.305 | 3 | 0.305 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581 | 21 | 73.8519
1720 | 1720 | CL3-567 | LEITRIM | LEITRIM | SS-534 | Garvagh Glebe 110kV Substation Extension | EirGrid | 110000 | 20000 | 110000 | 1.433 | 2 | 0.96 | 3 | 0.96 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341 | 4.2 | 387.4452
1721 | 1721 | CL3-568 | CARLOW | CARLOW | SS-481 | Castledockrell 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 11.949 | 12 | 0.414 | 3 | 0.414 | 4.2 | 4.2 | 2048870 | 7 | 487826.1905 | 2.0499 | 4.2 | 319.0667
1722 | 1722 | CL3-569 | CARLOW | WEXFORD | SS-481 | Castledockrell 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 9.698 | 10 | 1.694 | 3 | 1.2705 | 8.4 | 8.4 | 1943470 | 7 | 231365.4762 | 4.3222 | 4.2 | 487.8262
1723 | 1723 | CL3-570 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.561 | 11 | 0.599 | 3 | 0.599 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 8.4 | 231.3655
1724 | 1724 | CL3-571 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.19 | 8 | 1.071 | 3 | 1.071 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 342.819
1725 | 1725 | CL3-572 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.722 | 7 | 1.005 | 3 | 1.005 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 216.6548
1726 | 1726 | CL3-573 | WICKLOW | WICKLOW | SS-699 | Ballycumber 38kV Substation | ESB Networks | 38000 | low | 38000 | 11.665 | 12 | 3.947 | 3 | 2.9603 | 21 | 21 | 1191030 | 4 | 56715.7143 | 17.6318 | 4.2 | 199.9238
1727 | 1727 | CL3-574 | WICKLOW | WICKLOW | SS-062 | Stratford 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.948 | 6 | 1.028 | 3 | 1.028 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424 | 21 | 56.7157
1728 | 1728 | CL3-575 | WICKLOW | WICKLOW | SS-010 | Fassaroe 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 12.405 | 13 | 0.535 | 3 | 0.535 | 4.2 | 4.2 | 2101570 | 7 | 500373.8095 | 1.9985 | 4.2 | 412.5405
1729 | 1729 | CL3-576 | WICKLOW | WICKLOW | SS-616 | Ballinvally 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 2.489 | 3 | 0.648 | 3 | 0.648 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 500.3738
1730 | 1730 | CL3-577 | WICKLOW | WICKLOW | SS-699 | Ballycumber 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.985 | 2 | 0.607 | 3 | 0.607 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007 | 4.2 | 133
1731 | 1731 | CL3-578 | KERRY | KERRY | SS-637 | Kilgarvan 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.059 | 7 | 0.657 | 3 | 0.657 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 116.269
1732 | 1732 | CL3-579 | KERRY | KERRY | SS-668 | Coomataggart 110 kV Substation | EirGrid | 110000 | low | 110000 | 1.397 | 2 | 1.197 | 3 | 1.197 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341 | 4.2 | 199.9238
1733 | 1733 | CL3-580 | CORK | CORK | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.31 | 4 | 1.422 | 3 | 1.0665 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 319.0667
1734 | 1734 | CL3-581 | CORK | CORK | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.519 | 3 | 0.664 | 3 | 0.664 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 149.731
1735 | 1735 | CL3-582 | KERRY | KERRY | SS-071 | Coomagearlahy Substation | EirGrid | 110000 | medium-low | 110000 | 2.652 | 3 | 0.639 | 3 | 0.639 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674 | 4.2 | 133
1736 | 1736 | CL3-583 | KERRY | KERRY | SS-072 | Clonkeen 110kV Substation | EirGrid | 110000 |  |  | 2.391 | 3 | 0.823 | 3 | 0.823 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674 | 4.2 | 374.8976
1737 | 1737 | CL3-584 | KERRY | KERRY | SS-072 | Clonkeen 110kV Substation | EirGrid | 110000 |  |  | 5.528 | 6 | 1.123 | 3 | 1.123 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424 | 4.2 | 374.8976
1738 | 1738 | CL3-585 | KERRY | KERRY | SS-162 | Garrow 110kV Substation | EirGrid | 110000 | 38000 | 110000 | 3.611 | 4 | 1.05 | 3 | 1.05 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581 | 4.2 | 412.5405
1739 | 1739 | CL3-586 | KERRY | KERRY | SS-072 | Clonkeen 110kV Substation | EirGrid | 110000 |  |  | 5.537 | 6 | 1.101 | 3 | 1.101 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424 | 4.2 | 387.4452
1740 | 1740 | CL3-587 | CORK | KERRY | SS-327 | Rathmore 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.212 | 7 | 0.646 | 3 | 0.646 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 412.5405
1741 | 1741 | CL3-588 | CORK | CORK | SS-161 | Gneeves 38kV Substation | ESB Networks | 38000 | low | 38000 | 7.137 | 8 | 2.316 | 3 | 1.737 | 8.4 | 8.4 | 909950 | 4 | 108327.381 | 9.2313 | 4.2 | 199.9238
1742 | 1742 | CL3-589 | CORK | CORK | SS-096 | Boggeragh 110kV Substation | EirGrid | 110000 |  |  | 2.427 | 3 | 0.284 | 3 | 0.284 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674 | 8.4 | 108.3274
1743 | 1743 | CL3-590 | CORK | CORK | SS-615 | Knockduff 110kv Substation | EirGrid | 110000 |  |  | 4.292 | 5 | 2.073 | 3 | 1.5547 | 8.4 | 8.4 | 1679970 | 7 | 199996.4286 | 5.0001 | 4.2 | 374.8976
1744 | 1744 | CL3-591 | CORK | CORK | SS-096 | Boggeragh 110kV Substation | EirGrid | 110000 |  |  | 1.943 | 2 | 0.446 | 3 | 0.446 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341 | 8.4 | 199.9964
1745 | 1745 | CL3-592 | WATERFORD | WATERFORD | SS-532 | Woodhouse 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 1.716 | 2 | 0.877 | 3 | 0.877 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341 | 4.2 | 319.0667
1746 | 1746 | CL3-593 | TIPPERARY | LAOIS | SS-666 | 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.453 | 4 | 0.719 | 3 | 0.719 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 319.0667
1747 | 1747 | CL3-594 | TIPPERARY | TIPPERARY | SS-666 | 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.258 | 2 | 0.401 | 3 | 0.401 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007 | 4.2 | 149.731
1748 | 1748 | CL3-595 | KILDARE | LAOIS | SS-034 | Athy 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 6.786 | 7 | 1.913 | 3 | 1.4347 | 8.4 | 8.4 | 1785370 | 7 | 212544.0476 | 4.7049 | 4.2 | 116.269
1749 | 1749 | CL3-596 | LIMERICK | LIMERICK | SS-069 | Garryspillane 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.7 | 5 | 0.46 | 3 | 0.46 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 8.4 | 212.544
1750 | 1750 | CL3-597 | CLARE | CLARE | SS-116 | Ardnacrusha 110kV Substation | EirGrid | 110000 | low | 110000 | 8.285 | 9 | 1.211 | 3 | 0.90825 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213 | 4.2 | 166.4619
1751 | 1751 | CL3-598 | GALWAY | GALWAY | SS-459 | Ballycrossaun 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.476 | 3 | 0.831 | 3 | 0.831 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 450.1833
1752 | 1752 | CL3-599 | TIPPERARY | TIPPERARY | SS-483 | Birdhill 38kV Substation | ESB Networks | 38000 | 38000 | low | 1.799 | 2 | 0.336 | 3 | 0.336 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007 | 4.2 | 133
1753 | 1753 | CL3-600 | OFFALY | OFFALY | SS-551 | Dallow 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 4.925 | 5 | 0.317 | 3 | 0.317 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5 | 4.2 | 116.269
1754 | 1754 | CL3-601 | GALWAY | GALWAY | SS-459 | Ballycrossaun 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.377 | 4 | 0.436 | 3 | 0.436 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 399.9929
1755 | 1755 | CL3-602 | GALWAY | GALWAY | SS-502 | Ballinasloe 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 2.734 | 3 | 0.417 | 3 | 0.417 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 149.731
1756 | 1756 | CL3-603 | GALWAY | GALWAY | SS-269 | Shannonbridge 110kV Substation | EirGrid | 110000 | low | 110000 | 1.595 | 2 | 0.554 | 3 | 0.554 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341 | 4.2 | 133
1757 | 1757 | CL3-604 | GALWAY | GALWAY | SS-338 | Banagher 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.143 | 3 | 0.825 | 3 | 0.825 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 319.0667
1758 | 1758 | CL3-605 | GALWAY | GALWAY | SS-269 | Shannonbridge 110kV Substation | EirGrid | 110000 | low | 110000 | 4.214 | 5 | 1.588 | 3 | 1.191 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5 | 4.2 | 133
1759 | 1759 | CL3-606 | OFFALY | OFFALY | SS-269 | Shannonbridge 110kV Substation | EirGrid | 110000 | low | 110000 | 7.047 | 8 | 1.723 | 3 | 1.2923 | 8.4 | 8.4 | 1838070 | 7 | 218817.8571 | 4.57 | 4.2 | 399.9929
1760 | 1760 | CL3-607 | OFFALY | OFFALY | SS-269 | Shannonbridge 110kV Substation | EirGrid | 110000 | low | 110000 | 6.966 | 7 | 0.472 | 3 | 0.472 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525 | 8.4 | 218.8179
1761 | 1761 | CL3-608 | OFFALY | OFFALY | SS-269 | Shannonbridge 110kV Substation | EirGrid | 110000 | low | 110000 | 8.204 | 9 | 1.022 | 3 | 1.022 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213 | 4.2 | 425.0881
1762 | 1762 | CL3-609 | MEATH | MEATH | SS-376 | Kells 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.788 | 7 | 1.75 | 3 | 1.3125 | 8.4 | 8.4 | 839680 | 4 | 99961.9048 | 10.0038 | 4.2 | 450.1833
1763 | 1763 | CL3-610 | OFFALY | OFFALY | SS-231 | Lumcloon 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.135 | 7 | 1.07 | 3 | 1.07 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 8.4 | 99.9619
1764 | 1764 | CL3-611 | OFFALY | OFFALY | SS-231 | Lumcloon 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.191 | 8 | 10.428 | 3 | 7.821 | 54.6 | 54.6 | 2604940 | 11 | 47709.5238 | 20.9602 | 4.2 | 199.9238
1765 | 1765 | CL3-612 | OFFALY | OFFALY | SS-231 | Lumcloon 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.87 | 6 | 0.858 | 3 | 0.858 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 54.6 | 47.7095
1766 | 1766 | CL3-613 | OFFALY | WESTMEATH | SS-168 | Derryiron 110kV Substation | EirGrid | 110000 |  |  | 4.91 | 5 | 0.775 | 3 | 0.775 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5 | 4.2 | 183.1929
1767 | 1767 | CL3-614 | OFFALY | WESTMEATH | SS-168 | Derryiron 110kV Substation | EirGrid | 110000 |  |  | 6.522 | 7 | 1.577 | 3 | 1.1827 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525 | 4.2 | 399.9929
1768 | 1768 | CL3-615 | OFFALY | WESTMEATH | SS-059 | Kinnegad 110kV | EirGrid | 110000 |  |  | 4.547 | 5 | 1.792 | 3 | 1.344 | 8.4 | 8.4 | 1679970 | 7 | 199996.4286 | 5.0001 | 4.2 | 425.0881
1769 | 1769 | CL3-616 | KILDARE | LAOIS | SS-034 | Athy 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 9.667 | 10 | 0.662 | 3 | 0.662 | 4.2 | 4.2 | 1943470 | 7 | 462730.9524 | 2.1611 | 8.4 | 199.9964
1770 | 1770 | CL3-617 | KILDARE | OFFALY | SS-167 | Cushaling 110kV Substation | EirGrid | 110000 | low | 110000 | 4.152 | 5 | 3.41 | 3 | 2.5575 | 16.8 | 16.8 | 1946060 | 8 | 115836.9048 | 8.6328 | 4.2 | 462.731
1771 | 1771 | CL3-618 | KILDARE | KILDARE | SS-216 | Blake 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.442 | 6 | 2.046 | 3 | 1.5345 | 8.4 | 8.4 | 1732670 | 7 | 206270.2381 | 4.848 | 16.8 | 115.8369
1772 | 1772 | CL3-619 | OFFALY | OFFALY | SS-167 | Cushaling 110kV Substation | EirGrid | 110000 | low | 110000 | 5.708 | 6 | 3.393 | 3 | 2.5447 | 16.8 | 16.8 | 2016330 | 8 | 120019.6429 | 8.332 | 8.4 | 206.2702
1773 | 1773 | CL3-620 | OFFALY | OFFALY | SS-167 | Cushaling 110kV Substation | EirGrid | 110000 | low | 110000 | 7.357 | 8 | 0.372 | 3 | 0.372 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285 | 16.8 | 120.0196
1774 | 1774 | CL3-621 | OFFALY | OFFALY | SS-469 | Portarlington 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.1 | 7 | 4.026 | 3 | 3.0195 | 21 | 21 | 839680 | 4 | 39984.7619 | 25.0095 | 4.2 | 437.6357
1775 | 1775 | CL3-622 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 7.991 | 8 | 1.071 | 3 | 1.071 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285 | 21 | 39.9848
1776 | 1776 | CL3-623 | ROSCOMMON | ROSCOMMON | SS-124 | Roscommon 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.179 | 7 | 0.448 | 3 | 0.448 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 437.6357
1777 | 1777 | CL3-624 | LONGFORD | LONGFORD | SS-563 | Ballymahon 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.757 | 5 | 0.529 | 3 | 0.529 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 199.9238
1778 | 1778 | CL3-625 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.104 | 8 | 0.431 | 3 | 0.431 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 166.4619
1779 | 1779 | CL3-626 | CAVAN | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.161 | 10 | 6.311 | 3 | 4.7332 | 33.6 | 33.6 | 1460390 | 6 | 43463.9881 | 23.0076 | 4.2 | 216.6548
1780 | 1780 | CL3-627 | LEITRIM | LEITRIM | SS-097 | Corderry 110kV Substation | EirGrid | 110000 |  |  | 5.724 | 6 | 0.583 | 3 | 0.583 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424 | 33.6 | 43.464
1781 | 1781 | CL3-628 | LEITRIM | LEITRIM | SS-097 | Corderry 110kV Substation | EirGrid | 110000 |  |  | 4.539 | 5 | 0.304 | 3 | 0.304 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5 | 4.2 | 412.5405
1782 | 1782 | CL3-629 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.687 | 5 | 1.223 | 3 | 0.91725 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 399.9929
1783 | 1783 | CL3-630 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.426 | 8 | 0.336 | 3 | 0.336 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 166.4619
1784 | 1784 | CL3-631 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.311 | 10 | 0.316 | 3 | 0.316 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 4.2 | 216.6548
1785 | 1785 | CL3-632 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.148 | 12 | 0.178 | 3 | 0.178 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 330.2714
1786 | 1786 | CL3-633 | CAVAN | CAVAN | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 13.253 | 14 | 0.624 | 3 | 0.624 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284 | 4.2 | 355.3667
1787 | 1787 | CL3-634 | CAVAN | CAVAN | SS-110 | Corraclassy 110kV Substation | EirGrid | 110000 |  |  | 5.913 | 6 | 0.452 | 3 | 0.452 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424 | 4.2 | 380.4619
1788 | 1788 | CL3-635 | CAVAN | LEITRIM | SS-110 | Corraclassy 110kV Substation | EirGrid | 110000 |  |  | 9.348 | 10 | 3.572 | 3 | 2.679 | 16.8 | 16.8 | 2297410 | 8 | 136750.5952 | 7.3126 | 4.2 | 412.5405
1789 | 1789 | CL3-636 | LEITRIM | LEITRIM | SS-304 | Arigna 110kV Substation | EirGrid | 110000 | 110000 | 20000 | 10.487 | 11 | 2.433 | 3 | 1.8247 | 12.6 | 12.6 | 1996170 | 7 | 158426.1905 | 6.3121 | 16.8 | 136.7506
1790 | 1790 | CL3-637 | LEITRIM | LEITRIM | SS-304 | Arigna 110kV Substation | EirGrid | 110000 | 110000 | 20000 | 9.407 | 10 | 2.701 | 3 | 2.0257 | 12.6 | 12.6 | 1943470 | 7 | 154243.6508 | 6.4832 | 12.6 | 158.4262
1791 | 1791 | CL3-638 | LEITRIM | LEITRIM | SS-304 | Arigna 110kV Substation | EirGrid | 110000 | 110000 | 20000 | 4.862 | 5 | 0.539 | 3 | 0.539 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5 | 12.6 | 154.2437
1792 | 1792 | CL3-639 | LEITRIM | LEITRIM | SS-304 | Arigna 110kV Substation | EirGrid | 110000 | 110000 | 20000 | 6.037 | 7 | 1.283 | 3 | 0.96225 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525 | 4.2 | 399.9929
1793 | 1793 | CL3-640 | CAVAN | CAVAN | SS-110 | Corraclassy 110kV Substation | EirGrid | 110000 |  |  | 8.21 | 9 | 4.621 | 3 | 3.4658 | 21 | 21 | 2227140 | 8 | 106054.2857 | 9.4291 | 4.2 | 425.0881
1794 | 1794 | CL3-641 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.509 | 5 | 1.173 | 3 | 1.173 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 21 | 106.0543
1795 | 1795 | CL3-642 | DONEGAL | DONEGAL | SS-688 | Clogher 110kV Substation | EirGrid | 110000 |  |  | 9.53 | 10 | 2.006 | 3 | 1.5045 | 8.4 | 8.4 | 1943470 | 7 | 231365.4762 | 4.3222 | 4.2 | 166.4619
1796 | 1796 | CL3-643 | DONEGAL | DONEGAL | SS-688 | Clogher 110kV Substation | EirGrid | 110000 |  |  | 11.189 | 12 | 1.053 | 3 | 1.053 | 4.2 | 4.2 | 2048870 | 7 | 487826.1905 | 2.0499 | 8.4 | 231.3655
1797 | 1797 | CL3-644 | DONEGAL | DONEGAL | SS-083 | Golagh 110kV Substation | EirGrid | 110000 | 38000 | 110000 | 10.141 | 11 | 3.925 | 3 | 2.9437 | 21 | 21 | 2367680 | 8 | 112746.6667 | 8.8694 | 4.2 | 487.8262
1798 | 1798 | CL3-645 | DONEGAL | DONEGAL | SS-688 | Clogher 110kV Substation | EirGrid | 110000 |  |  | 7.895 | 8 | 0.869 | 3 | 0.869 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285 | 21 | 112.7467
1799 | 1799 | CL3-646 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 11.207 | 12 | 3.235 | 3 | 2.4263 | 16.8 | 16.8 | 2437950 | 8 | 145116.0714 | 6.891 | 4.2 | 437.6357
1800 | 1800 | CL3-647 | DONEGAL | DONEGAL | SS-688 | Clogher 110kV Substation | EirGrid | 110000 |  |  | 6.222 | 7 | 0.913 | 3 | 0.913 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525 | 16.8 | 145.1161
1801 | 1801 | CL3-648 | DONEGAL | DONEGAL | SS-083 | Golagh 110kV Substation | EirGrid | 110000 | 38000 | 110000 | 5.815 | 6 | 1.144 | 3 | 1.144 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424 | 4.2 | 425.0881
1802 | 1802 | CL3-649 | DONEGAL | DONEGAL | SS-688 | Clogher 110kV Substation | EirGrid | 110000 |  |  | 8.118 | 9 | 1.82 | 3 | 1.365 | 8.4 | 8.4 | 1890770 | 7 | 225091.6667 | 4.4426 | 4.2 | 412.5405
1803 | 1803 | CL3-650 | DONEGAL | DONEGAL | SS-102 | Binbane 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.078 | 6 | 1.277 | 3 | 0.95775 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424 | 8.4 | 225.0917
1804 | 1804 | CL3-651 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.767 | 5 | 2.178 | 3 | 1.6335 | 8.4 | 8.4 | 699140 | 4 | 83230.9524 | 12.0148 | 4.2 | 412.5405
1805 | 1805 | CL3-652 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.881 | 2 | 0.333 | 3 | 0.333 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007 | 8.4 | 83.231
1806 | 1806 | CL3-653 | TIPPERARY | WATERFORD | SS-630 | Lismore 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.579 | 9 | 5.912 | 3 | 4.434 | 29.4 | 29.4 | 1147260 | 5 | 39022.449 | 25.6263 | 4.2 | 116.269
1807 | 1807 | CL3-654 | TIPPERARY | TIPPERARY | SS-455 | Ardfinnan 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.115 | 8 | 8.175 | 3 | 6.1313 | 42 | 42 | 1237870 | 6 | 29473.0952 | 33.9292 | 29.4 | 39.0224
1808 | 1808 | CL3-655 | TIPPERARY | TIPPERARY | SS-455 | Ardfinnan 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.27 | 7 | 0.86 | 3 | 0.86 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 42 | 29.4731
1809 | 1809 | CL3-656 | TIPPERARY | TIPPERARY | SS-455 | Ardfinnan 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.353 | 10 | 1.135 | 3 | 1.135 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 4.2 | 199.9238
1810 | 1810 | CL3-657 | TIPPERARY | WATERFORD | SS-507 | Kilcloher 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.187 | 9 | 3.326 | 3 | 2.4945 | 16.8 | 16.8 | 980220 | 4 | 58346.4286 | 17.139 | 4.2 | 330.2714
1811 | 1811 | CL3-658 | TIPPERARY | WATERFORD | SS-507 | Kilcloher 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.871 | 10 | 0.76 | 3 | 0.76 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 16.8 | 58.3464
1812 | 1812 | CL3-659 | TIPPERARY | WATERFORD | SS-622 | Barranafaddock 38kV Substation | ESB Networks | 38000 | low | 38000 | 9.556 | 10 | 10.954 | 3 | 8.2155 | 58.8 | 58.8 | 3026560 | 11 | 51472.1088 | 19.428 | 4.2 | 330.2714
1813 | 1813 | CL3-660 | TIPPERARY | TIPPERARY | SS-622 | Barranafaddock 38kV Substation | ESB Networks | 38000 | low | 38000 | 9.24 | 10 | 2.564 | 3 | 1.923 | 12.6 | 12.6 | 1469550 | 3 | 116630.9524 | 8.5741 | 58.8 | 51.4721
1814 | 1814 | CL3-661 | TIPPERARY | WATERFORD | SS-455 | Ardfinnan 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.537 | 9 | 1.658 | 3 | 1.2435 | 8.4 | 8.4 | 1379800 | 2 | 164261.9048 | 6.0878 | 12.6 | 116.631
1815 | 1815 | CL3-662 | WATERFORD | WATERFORD | SS-659 | Spa Road 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 12.24 | 13 | 1.493 | 3 | 1.1198 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718 | 8.4 | 164.2619
1816 | 1816 | CL3-663 | WATERFORD | WATERFORD | SS-659 | Spa Road 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 12.173 | 13 | 4.399 | 3 | 3.2992 | 21 | 21 | 1261300 | 4 | 60061.9048 | 16.6495 | 4.2 | 367.9143
1817 | 1817 | CL3-664 | WATERFORD | WATERFORD | SS-659 | Spa Road 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.965 | 8 | 0.927 | 3 | 0.927 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 21 | 60.0619
1818 | 1818 | CL3-665 | WATERFORD | WATERFORD | SS-659 | Spa Road 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 6.394 | 7 | 1.91 | 3 | 1.4325 | 8.4 | 8.4 | 839680 | 4 | 99961.9048 | 10.0038 | 4.2 | 216.6548
1819 | 1819 | CL3-666 | WATERFORD | WATERFORD | SS-659 | Spa Road 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 3.454 | 4 | 4.15 | 3 | 3.1125 | 21 | 21 | 628870 | 4 | 29946.1905 | 33.3932 | 8.4 | 99.9619
1820 | 1820 | CL3-667 | WATERFORD | WATERFORD | SS-064 | Ballydine 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 7.385 | 8 | 1.165 | 3 | 1.165 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285 | 21 | 29.9462
1821 | 1821 | CL3-668 | WATERFORD | WATERFORD | SS-505 | Kilmacthomas 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.802 | 9 | 1.419 | 3 | 1.0642 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 437.6357
1822 | 1822 | CL3-669 | WATERFORD | WATERFORD | SS-505 | Kilmacthomas 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.49 | 11 | 4.499 | 3 | 3.3742 | 21 | 21 | 1120760 | 4 | 53369.5238 | 18.7373 | 4.2 | 317.7238
1823 | 1823 | CL3-670 | WATERFORD | WATERFORD | SS-205 | Dungarvan 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 9.594 | 10 | 4.244 | 3 | 3.183 | 21 | 21 | 2297410 | 8 | 109400.4762 | 9.1407 | 21 | 53.3695
1824 | 1824 | CL3-671 | WATERFORD | WATERFORD | SS-205 | Dungarvan 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 12.85 | 13 | 2.059 | 3 | 1.5443 | 8.4 | 8.4 | 2101570 | 7 | 250186.9048 | 3.997 | 21 | 109.4005
1825 | 1825 | CL3-672 | CORK | CORK | SS-193 | Charleville 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 4.099 | 5 | 0.686 | 3 | 0.686 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5 | 8.4 | 250.1869
1826 | 1826 | CL3-673 | LIMERICK | LIMERICK | SS-695 | Castlepook 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 2.406 | 3 | 0.627 | 3 | 0.627 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 399.9929
1827 | 1827 | CL3-674 | CORK | LIMERICK | SS-695 | Castlepook 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 2.284 | 3 | 17.711 | 3 | 13.2832 | 92.4 | 92.4 | 1550890 | 11 | 16784.5238 | 59.5787 | 4.2 | 133
1828 | 1828 | CL3-675 | LIMERICK | LIMERICK | SS-695 | Castlepook 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 2.222 | 3 | 1.462 | 3 | 1.0965 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 92.4 | 16.7845
1829 | 1829 | CL3-676 | TIPPERARY | TIPPERARY | SS-585 | Kilross Road 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.642 | 10 | 2.177 | 3 | 1.6328 | 8.4 | 8.4 | 1432500 | 2 | 170535.7143 | 5.8639 | 4.2 | 133
1830 | 1830 | CL3-677 | TIPPERARY | TIPPERARY | SS-585 | Kilross Road 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.186 | 10 | 2.65 | 3 | 1.9875 | 12.6 | 12.6 | 1469550 | 3 | 116630.9524 | 8.5741 | 8.4 | 170.5357
1831 | 1831 | CL3-678 | TIPPERARY | TIPPERARY | SS-127 | Tipperary 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 9.424 | 10 | 5.185 | 3 | 3.8887 | 25.2 | 25.2 | 2842150 | 9 | 112783.7302 | 8.8665 | 12.6 | 116.631
1832 | 1832 | CL3-679 | TIPPERARY | TIPPERARY | SS-315 | Cahir 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.272 | 9 | 2.206 | 3 | 1.6545 | 8.4 | 8.4 | 1379800 | 2 | 164261.9048 | 6.0878 | 25.2 | 112.7837
1833 | 1833 | CL3-680 | TIPPERARY | TIPPERARY | SS-315 | Cahir 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 11.786 | 12 | 19.966 | 3 | 14.9745 | 105 | 105 | 3448180 | 11 | 32839.8095 | 30.4508 | 8.4 | 164.2619
1834 | 1834 | CL3-681 | TIPPERARY | LIMERICK | SS-257 | Kilshanny 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.062 | 11 | 3.94 | 3 | 2.955 | 21 | 21 | 1120760 | 4 | 53369.5238 | 18.7373 | 105 | 32.8398
1835 | 1835 | CL3-682 | LIMERICK | LIMERICK | SS-257 | Kilshanny 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.646 | 9 | 1.834 | 3 | 1.3755 | 8.4 | 8.4 | 1379800 | 2 | 164261.9048 | 6.0878 | 21 | 53.3695
1836 | 1836 | CL3-683 | LIMERICK | LIMERICK | SS-257 | Kilshanny 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.526 | 8 | 1.726 | 3 | 1.2945 | 8.4 | 8.4 | 909950 | 4 | 108327.381 | 9.2313 | 8.4 | 164.2619
1837 | 1837 | CL3-684 | TIPPERARY | TIPPERARY | SS-347 | Glengoole 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.077 | 3 | 0.407 | 3 | 0.407 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 8.4 | 108.3274
1838 | 1838 | CL3-685 | TIPPERARY | TIPPERARY | SS-347 | Glengoole 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.018 | 4 | 0.7 | 3 | 0.7 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 133
1839 | 1839 | CL3-686 | TIPPERARY | TIPPERARY | SS-347 | Glengoole 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.582 | 5 | 1.894 | 3 | 1.4205 | 8.4 | 8.4 | 699140 | 4 | 83230.9524 | 12.0148 | 4.2 | 149.731
1840 | 1840 | CL3-687 | TIPPERARY | TIPPERARY | SS-347 | Glengoole 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.959 | 6 | 0.862 | 3 | 0.862 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 8.4 | 83.231
1841 | 1841 | CL3-688 | TIPPERARY | TIPPERARY | SS-551 | Dallow 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.689 | 9 | 0.499 | 3 | 0.499 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213 | 4.2 | 183.1929
1842 | 1842 | CL3-689 | TIPPERARY | TIPPERARY | SS-551 | Dallow 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.173 | 9 | 0.496 | 3 | 0.496 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213 | 4.2 | 450.1833
1843 | 1843 | CL3-690 | LAOIS | LAOIS | SS-469 | Portarlington 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.825 | 9 | 0.419 | 3 | 0.419 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 450.1833
1844 | 1844 | CL3-691 | GALWAY | GALWAY | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.739 | 9 | 0.788 | 3 | 0.788 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 317.7238
1845 | 1845 | CL3-692 | GALWAY | GALWAY | SS-236 | Creagh 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.458 | 6 | 0.501 | 3 | 0.501 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 317.7238
1846 | 1846 | CL3-693 | CORK | CORK | SS-583 | Castletownroche 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.505 | 8 | 0.243 | 3 | 0.243 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 183.1929
1847 | 1847 | CL3-694 | WATERFORD | WATERFORD | SS-016 | Portlaw 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.572 | 4 | 1.174 | 3 | 1.174 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 216.6548
1848 | 1848 | CL3-695 | CARLOW | CARLOW | SS-492 | Graigue 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.552 | 9 | 1.156 | 3 | 1.156 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 149.731
1849 | 1849 | CL3-696 | KILDARE | KILDARE | SS-035 | Athy South 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.878 | 7 | 0.481 | 3 | 0.481 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 317.7238
1850 | 1850 | CL3-697 | KILDARE | OFFALY | SS-469 | Portarlington 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.981 | 8 | 3.899 | 3 | 2.9242 | 21 | 21 | 909950 | 4 | 43330.9524 | 23.0782 | 4.2 | 199.9238
1851 | 1851 | CL3-698 | GALWAY | GALWAY | SS-120 | Carhoon 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 9.281 | 10 | 0.748 | 3 | 0.748 | 4.2 | 4.2 | 1943470 | 7 | 462730.9524 | 2.1611 | 21 | 43.331
1852 | 1852 | CL3-699 | TIPPERARY | TIPPERARY | SS-594 | Kill Hill 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.476 | 9 | 0.816 | 3 | 0.816 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213 | 4.2 | 462.731
1853 | 1853 | CL3-700 | TIPPERARY | TIPPERARY | SS-185 | Anner 110kV Substation | EirGrid | 110000 | 110000 | low | 6.585 | 7 | 2.021 | 3 | 1.5157 | 8.4 | 8.4 | 1785370 | 7 | 212544.0476 | 4.7049 | 4.2 | 450.1833
1854 | 1854 | CL3-701 | TIPPERARY | TIPPERARY | SS-295 | Doon 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 7.095 | 8 | 1.094 | 3 | 1.094 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285 | 8.4 | 212.544
1855 | 1855 | CL3-702 | WEXFORD | WEXFORD | SS-092 | Crane 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 7.884 | 8 | 0.431 | 3 | 0.431 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285 | 4.2 | 437.6357
1856 | 1856 | CL3-703 | LIMERICK | LIMERICK | SS-596 | Cappamore 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.92 | 4 | 0.388 | 3 | 0.388 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 437.6357
1857 | 1857 | CL3-704 | GALWAY | GALWAY | SS-459 | Ballycrossaun 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.726 | 9 | 0.548 | 3 | 0.548 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 149.731
1858 | 1858 | CL3-705 | TIPPERARY | OFFALY | SS-645 | Toomevara 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.876 | 4 | 0.883 | 3 | 0.883 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 317.7238
1859 | 1859 | CL3-706 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 17.703 | 18 | 0.656 | 3 | 0.656 | 4.2 | 4.2 | 1808740 | 1 | 430652.381 | 2.3221 | 4.2 | 149.731
1860 | 1860 | CL3-707 | LAOIS | LAOIS | SS-537 | Monaincha 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 11.906 | 12 | 0.303 | 3 | 0.303 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 430.6524
1861 | 1861 | CL3-708 | OFFALY | OFFALY | SS-084 | Birr 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.418 | 13 | 0.44 | 3 | 0.44 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718 | 4.2 | 355.3667
1862 | 1862 | CL3-709 | OFFALY | OFFALY | SS-231 | Lumcloon 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.757 | 7 | 0.871 | 3 | 0.871 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 367.9143
1863 | 1863 | CL3-710 | OFFALY | WESTMEATH | SS-467 | Clara 38kV Substation | ESB Networks | 38000 | 38000 | 20000;10000 | 4.048 | 5 | 0.371 | 3 | 0.371 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 199.9238
1864 | 1864 | CL3-711 | GALWAY | GALWAY | SS-236 | Creagh 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.018 | 9 | 1.873 | 3 | 1.4047 | 8.4 | 8.4 | 1379800 | 2 | 164261.9048 | 6.0878 | 4.2 | 166.4619
1865 | 1865 | CL3-712 | ROSCOMMON | ROSCOMMON | SS-236 | Creagh 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.568 | 10 | 0.805 | 3 | 0.805 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 8.4 | 164.2619
1866 | 1866 | CL3-713 | CORK | CORK | SS-433 | Lee Bridge 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.57 | 13 | 1.1 | 3 | 1.1 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718 | 4.2 | 330.2714
1867 | 1867 | CL3-714 | TIPPERARY | TIPPERARY | SS-348 | Furle 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.728 | 4 | 0.492 | 3 | 0.492 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 367.9143
1868 | 1868 | CL3-715 | GALWAY | CLARE | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.845 | 7 | 3.191 | 3 | 2.3933 | 16.8 | 16.8 | 839680 | 4 | 49980.9524 | 20.0076 | 4.2 | 149.731
1869 | 1869 | CL3-716 | OFFALY | OFFALY | SS-167 | Cushaling 110kV Substation | EirGrid | 110000 | low | 110000 | 5.289 | 6 | 1.166 | 3 | 1.166 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424 | 16.8 | 49.981
1870 | 1870 | CL3-717 | GALWAY | GALWAY | SS-439 | Loughrea 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.644 | 16 | 1.594 | 3 | 1.1955 | 4.2 | 4.2 | 1703340 | 1 | 405557.1429 | 2.4657 | 4.2 | 412.5405
1871 | 1871 | CL3-718 | LAOIS | LAOIS | SS-470 | Mountmellick 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.441 | 8 | 0.394 | 3 | 0.394 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 405.5571
1872 | 1872 | CL3-719 | GALWAY | GALWAY | SS-639 | Tonroe 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.124 | 9 | 0.375 | 3 | 0.375 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 216.6548
1873 | 1873 | CL3-720 | TIPPERARY | OFFALY | SS-084 | Birr 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.248 | 7 | 1.529 | 3 | 1.1467 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 317.7238
1874 | 1874 | CL3-721 | CORK | CORK | SS-261 | Milane Hill 38kV Station | ESB Networks | 38000 |  |  | 6.445 | 7 | 0.848 | 3 | 0.848 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 199.9238
1875 | 1875 | CL3-722 | GALWAY | GALWAY | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.737 | 12 | 0.582 | 3 | 0.582 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 199.9238
1876 | 1876 | CL3-723 | CLARE | CLARE | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.418 | 13 | 0.608 | 3 | 0.608 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718 | 4.2 | 355.3667
1877 | 1877 | CL3-724 | LIMERICK | LIMERICK | SS-588 | Kilmallock 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.57 | 6 | 0.479 | 3 | 0.479 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 367.9143
1878 | 1878 | CL3-725 | TIPPERARY | LAOIS | SS-053 | Ikerrin 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 6.671 | 7 | 2.629 | 3 | 1.9718 | 12.6 | 12.6 | 1785370 | 7 | 141696.0317 | 7.0574 | 4.2 | 183.1929
1879 | 1879 | CL3-726 | TIPPERARY | TIPPERARY | SS-455 | Ardfinnan 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.234 | 10 | 0.49 | 3 | 0.49 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 12.6 | 141.696
1880 | 1880 | CL3-727 | KILKENNY | KILKENNY | SS-489 | Ballyhale 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.861 | 6 | 1.103 | 3 | 1.103 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 330.2714
1881 | 1881 | CL3-728 | KILKENNY | KILKENNY | SS-492 | Graigue 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.556 | 6 | 2.168 | 3 | 1.626 | 8.4 | 8.4 | 769410 | 4 | 91596.4286 | 10.9175 | 4.2 | 183.1929
1882 | 1882 | CL3-729 | KILKENNY | KILKENNY | SS-492 | Graigue 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.425 | 3 | 0.809 | 3 | 0.809 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 8.4 | 91.5964
1883 | 1883 | CL3-730 | KILKENNY | KILKENNY | SS-492 | Graigue 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.355 | 6 | 1.918 | 3 | 1.4385 | 8.4 | 8.4 | 769410 | 4 | 91596.4286 | 10.9175 | 4.2 | 133
1884 | 1884 | CL3-731 | OFFALY | OFFALY | SS-530 | Esker 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 5.893 | 6 | 0.534 | 3 | 0.534 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424 | 8.4 | 91.5964
1885 | 1885 | CL3-732 | LIMERICK | LIMERICK | SS-527 | Rathkeale 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.726 | 5 | 1.034 | 3 | 1.034 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 4.2 | 412.5405
1886 | 1886 | CL3-733 | TIPPERARY | TIPPERARY | SS-043 | Thurles 110kV Substation | EirGrid | 110000 |  |  | 5.455 | 6 | 0.727 | 3 | 0.727 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424 | 4.2 | 166.4619
1887 | 1887 | CL3-734 | GALWAY | GALWAY | SS-236 | Creagh 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.654 | 11 | 4.748 | 3 | 3.561 | 25.2 | 25.2 | 1324920 | 5 | 52576.1905 | 19.02 | 4.2 | 412.5405
1888 | 1888 | CL3-735 | CORK | CORK | SS-577 | Whitechurch 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.557 | 10 | 3.947 | 3 | 2.9603 | 21 | 21 | 1050490 | 4 | 50023.3333 | 19.9907 | 25.2 | 52.5762
1889 | 1889 | CL3-736 | CLARE | CLARE | SS-483 | Birdhill 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.057 | 11 | 0.748 | 3 | 0.748 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 21 | 50.0233
1890 | 1890 | CL3-737 | CLARE | CLARE | SS-503 | Scariff 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.932 | 8 | 4.787 | 3 | 3.5903 | 25.2 | 25.2 | 1058430 | 5 | 42001.1905 | 23.8088 | 4.2 | 342.819
1891 | 1891 | CL3-738 | CLARE | CLARE | SS-483 | Birdhill 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.593 | 9 | 0.887 | 3 | 0.887 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 25.2 | 42.0012
1892 | 1892 | CL3-739 | LAOIS | LAOIS | SS-275 | Mountrath ESB Telecoms 38kV Radio Site | ESB Networks | 38000 | 38000 | low | 5.981 | 6 | 0.379 | 3 | 0.379 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 317.7238
1893 | 1893 | CL3-740 | GALWAY | GALWAY | SS-235 | Lisheeny 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.388 | 11 | 1.654 | 3 | 1.2405 | 8.4 | 8.4 | 1485200 | 2 | 176809.5238 | 5.6558 | 4.2 | 183.1929
1894 | 1894 | CL3-741 | OFFALY | WESTMEATH | SS-168 | Derryiron 110kV Substation | EirGrid | 110000 |  |  | 8.639 | 9 | 1.059 | 3 | 1.059 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213 | 8.4 | 176.8095
1895 | 1895 | CL3-742 | WATERFORD | WATERFORD | SS-482 | Foxhole 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.814 | 4 | 0.49 | 3 | 0.49 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 450.1833
1896 | 1896 | CL3-743 | TIPPERARY | TIPPERARY | SS-347 | Glengoole 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.046 | 3 | 0.788 | 3 | 0.788 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 149.731
1897 | 1897 | CL3-744 | CLARE | CLARE | SS-149 | Tulla 38kV Substation | ESB Networks | 38000 |  |  | 5.327 | 6 | 0.516 | 3 | 0.516 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 133
1898 | 1898 | CL3-745 | KERRY | KERRY | SS-706 | Scartaglin 38kV Substation | ESB Networks | 38000 | low | 38000 | 5.847 | 6 | 0.619 | 3 | 0.619 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 183.1929
1899 | 1899 | CL3-746 | TIPPERARY | TIPPERARY | SS-645 | Toomevara 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.373 | 13 | 2.481 | 3 | 1.8607 | 12.6 | 12.6 | 1627650 | 3 | 129178.5714 | 7.7412 | 4.2 | 183.1929
1900 | 1900 | CL3-747 | OFFALY | OFFALY | SS-066 | Thornsberry 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 7.115 | 8 | 0.21 | 3 | 0.21 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285 | 12.6 | 129.1786
1901 | 1901 | CL3-748 | CLARE | CLARE | SS-503 | Scariff 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 6.185 | 7 | 0.814 | 3 | 0.814 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 437.6357
1902 | 1902 | CL3-749 | OFFALY | OFFALY | SS-311 | Clonminch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.476 | 8 | 0.422 | 3 | 0.422 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 199.9238
1903 | 1903 | CL3-750 | LAOIS | LAOIS | SS-311 | Clonminch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.966 | 9 | 0.576 | 3 | 0.576 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 216.6548
1904 | 1904 | CL3-751 | LAOIS | LAOIS | SS-275 | Mountrath ESB Telecoms 38kV Radio Site | ESB Networks | 38000 | 38000 | low | 6.773 | 7 | 0.544 | 3 | 0.544 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 317.7238
1905 | 1905 | CL3-752 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 17.489 | 18 | 0.41 | 3 | 0.41 | 4.2 | 4.2 | 1808740 | 1 | 430652.381 | 2.3221 | 4.2 | 199.9238
1906 | 1906 | CL3-753 | OFFALY | OFFALY | SS-168 | Derryiron 110kV Substation | EirGrid | 110000 |  |  | 2.766 | 3 | 0.323 | 3 | 0.323 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674 | 4.2 | 430.6524
1907 | 1907 | CL3-754 | LEITRIM | LEITRIM | SS-304 | Arigna 110kV Substation | EirGrid | 110000 | 110000 | 20000 | 7.753 | 8 | 0.244 | 3 | 0.244 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285 | 4.2 | 374.8976
1908 | 1908 | CL3-755 | CAVAN | LEITRIM | SS-508 | Ballyconnell 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.745 | 8 | 0.544 | 3 | 0.544 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 437.6357
1909 | 1909 | CL3-756 | ROSCOMMON | SLIGO | SS-206 | Boyle 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 6.039 | 7 | 0.594 | 3 | 0.594 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 216.6548
1910 | 1910 | CL3-757 | ROSCOMMON | SLIGO | SS-206 | Boyle 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 5.963 | 6 | 0.271 | 3 | 0.271 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 199.9238
1911 | 1911 | CL3-758 | ROSCOMMON | ROSCOMMON | SS-206 | Boyle 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 12.101 | 13 | 1.905 | 3 | 1.4287 | 8.4 | 8.4 | 1590600 | 2 | 189357.1429 | 5.281 | 4.2 | 183.1929
1912 | 1912 | CL3-759 | ROSCOMMON | ROSCOMMON | SS-171 | Castlerea 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.479 | 5 | 0.267 | 3 | 0.267 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074 | 8.4 | 189.3571
1913 | 1913 | CL3-760 | ROSCOMMON | ROSCOMMON | SS-171 | Castlerea 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.96 | 7 | 0.448 | 3 | 0.448 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 166.4619
1914 | 1914 | CL3-761 | SLIGO | SLIGO | SS-042 | Ballytivnan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 6.652 | 7 | 0.913 | 3 | 0.913 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 199.9238
1915 | 1915 | CL3-762 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.196 | 10 | 0.484 | 3 | 0.484 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 4.2 | 199.9238
1916 | 1916 | CL3-763 | ROSCOMMON | ROSCOMMON | SS-206 | Boyle 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 6.216 | 7 | 0.665 | 3 | 0.665 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 330.2714
1917 | 1917 | CL3-764 | SLIGO | SLIGO | SS-031 | Sligo 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.826 | 6 | 0.731 | 3 | 0.731 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424 | 4.2 | 199.9238
1918 | 1918 | CL3-765 | GALWAY | GALWAY | SS-175 | Ballygar 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.87 | 3 | 1.51 | 3 | 1.1325 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 412.5405
1919 | 1919 | CL3-766 | GALWAY | GALWAY | SS-175 | Ballygar 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.566 | 7 | 0.557 | 3 | 0.557 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019 | 4.2 | 133
1920 | 1920 | CL3-767 | ROSCOMMON | ROSCOMMON | SS-696 | Sliabh Bawn 110kV Substation | EirGrid | 110000 | low | 110000 | 5.094 | 6 | 7.086 | 3 | 5.3145 | 37.8 | 37.8 | 2621410 | 10 | 69349.4709 | 14.4197 | 4.2 | 199.9238
1921 | 1921 | CL3-768 | ROSCOMMON | ROSCOMMON | SS-575 | Aghamore 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.766 | 13 | 0.428 | 3 | 0.428 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718 | 37.8 | 69.3495
1922 | 1922 | CL3-769 | WEXFORD | LONGFORD | SS-247 | Edgeworthstown 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.115 | 8 | 0.753 | 3 | 0.753 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 367.9143
1923 | 1923 | CL3-770 | WEXFORD | LONGFORD | SS-247 | Edgeworthstown 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.774 | 11 | 1.297 | 3 | 0.97275 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 216.6548
1924 | 1924 | CL3-771 | WESTMEATH | WESTMEATH | SS-247 | Edgeworthstown 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.873 | 11 | 0.525 | 3 | 0.525 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917 | 4.2 | 342.819
1925 | 1925 | CL3-772 | WESTMEATH | WESTMEATH | SS-246 | Loughanalla 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 9.619 | 10 | 0.353 | 3 | 0.353 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278 | 4.2 | 342.819
1926 | 1926 | CL3-773 | WESTMEATH | WESTMEATH | SS-246 | Loughanalla 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.685 | 8 | 1.27 | 3 | 0.9525 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 330.2714
1927 | 1927 | CL3-774 | WESTMEATH | WESTMEATH | SS-246 | Loughanalla 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.755 | 8 | 0.424 | 3 | 0.424 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156 | 4.2 | 216.6548
1928 | 1928 | CL3-775 | WEXFORD | LONGFORD | SS-067 | Finnea 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.646 | 6 | 3.912 | 3 | 2.934 | 21 | 21 | 769410 | 4 | 36638.5714 | 27.2936 | 4.2 | 216.6548
1929 | 1929 | CL3-776 | WESTMEATH | WESTMEATH | SS-067 | Finnea 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.088 | 6 | 0.585 | 3 | 0.585 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 21 | 36.6386
1930 | 1930 | CL3-777 | WEXFORD | LONGFORD | SS-067 | Finnea 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.894 | 3 | 0.632 | 3 | 0.632 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188 | 4.2 | 183.1929
1931 | 1931 | CL3-778 | MEATH | MEATH | SS-067 | Finnea 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.119 | 6 | 0.458 | 3 | 0.458 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 133
1932 | 1932 | CL3-779 | LONGFORD | LONGFORD | SS-247 | Edgeworthstown 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.535 | 6 | 1.273 | 3 | 0.95475 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 183.1929
1933 | 1933 | CL3-780 | LONGFORD | LONGFORD | SS-067 | Finnea 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.015 | 12 | 0.717 | 3 | 0.717 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814 | 4.2 | 183.1929
1934 | 1934 | CL3-781 | WESTMEATH | WESTMEATH | SS-517 | Delvin 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.116 | 4 | 0.729 | 3 | 0.729 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786 | 4.2 | 355.3667
1935 | 1935 | CL3-782 | WESTMEATH | MEATH | SS-517 | Delvin 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.97 | 9 | 0.537 | 3 | 0.537 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474 | 4.2 | 149.731
1936 | 1936 | CL3-783 | WESTMEATH | WESTMEATH | SS-059 | Kinnegad 110kV | EirGrid | 110000 |  |  | 6.292 | 7 | 0.764 | 3 | 0.764 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525 | 4.2 | 317.7238
1937 | 1937 | CL3-784 | WESTMEATH | WESTMEATH | SS-526 | Newbrook 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 5.966 | 6 | 0.427 | 3 | 0.427 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587 | 4.2 | 425.0881
1938 | 1938 | CL3-785 | MONAGHAN | CAVAN | SS-466 | Cootehill 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 3.181 | 4 | 1.646 | 3 | 1.2345 | 8.4 | 8.4 | 628870 | 4 | 74865.4762 | 13.3573 | 4.2 | 183.1929
1939 | 1939 | CL3-786 | MAYO | MAYO | SS-317 | Newport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 12.066 | 13 | 2.632 | 3 | 1.974 | 12.6 | 12.6 | 1627650 | 3 | 129178.5714 | 7.7412 | 8.4 | 74.8655
[22 empty] | 12.6 | 129.1786

## ELC_CCS
Electricity Generators Database - CCS options
Sources:
Techno-economic data: ETRI 2014 (https://setis.ec.europa.eu/publications/jrc-setis-reports/etri-2014 )
Process options: Irish TIMES v1.0 (using Fionn's analysis)
|  |  | ~FI_T: MEUR2015 | [32 empty] | ~FI_Process | [7 empty] | ~FI_Comm
TechName | *TechDesc | Comm-IN | Comm-OUT | EFF | EFF~2020 | EFF~2030 | EFF~2040 | EFF~2050 | Start | INVCOST | INVCOST~2020 | INVCOST~2030 | INVCOST~2040 | INVCOST~2050 | FIXOM | FIXOM~2020 | FIXOM~2030 | FIXOM~2040 | FIXOM~2050 | VAROM | VAROM~2020 | VAROM~2030 | VAROM~2040 | VAROM~2050 | *INVCOST | *INVCOST | *VAROM | *VAROM | LIFE | Cap2Act | AFA | AFA~2020 | AFA~2030 | AFA~2040 | AFA~2050 | Sets | TechName | TechDesc | Tact | Tcap | Tslvl | PrimaryCG | Vintage | Csets | CommName | CommDesc | Unit | LimType | CTSLvl | PeakTS | Ctype
*Technology Name | Technology Description | Input Commodity | Output Commodity | Efficiency | [5 empty] | Overall CAPEX (€2013/kW) |  |  |  |  | FOM (€2013/kW) |  |  |  |  | Overall VOM (€2013/GJ) |  |  |  |  | Pipeline | Storage | Pipeline | Storage | Technical life |  | Max. capacity factor |  |  |  |  | \I: Process Set Membership | Technology Name | Technology Description | Activity Unit | Capacity Unit | Timeslice Operational Level | Operational Commodity Group | Vintage Tracking | *Commodity Set Membership | Commodity Name | Commodity Description | Unit | Balance Equ Type Override | Timeslice Tracking Level | Peak Monitoring | Electricity Indicator
P-TH-SC-COA-CCS04-MP1 | New Power Plant - Pulverised coal supercritical CCS post-combustion_Moneypoint Kinsale | PWRCOA | ELCC, PWRCO2S | 34% | 35% | 35% | 38% | 38% | 2030 |  |  | 3102.3219 | 2952.3219 | 2932.3219 | 75 | 67.5 | 63.75 | 63.75 | 63.75 | 0.87578 | 0.85928 | 0.85103 | 0.85103 | 0.85103 | 303.1602 | 59.1616 | 0.59138 | 0.1194 | 40 | 31.536 | 90% |  |  |  |  | ELE | P-TH-SC-COA-CCS04-MP1 | New Power Plant - Pulverised coal supercritical CCS post-combustion_Moneypoint Kinsale | PJ | GW | DAYNITE |  |  | ENV | PWRCO2S | Sequestered CO2 (PWR) | kt |  |  |  |  | Pulverised coal supercritical CCS post-combustion_Moneypoint Kinsale
P-TH-IGCC-COA-CCS06-MP1 | New Power Plant - IGCC coal CCS pre-combustion_Moneypoint Kinsale | PWRCOA | ELCC, PWRCO2S | 35% | 37% | 40% | 41% | 44% | 2030 |  |  | 2902.3219 | 2582.3219 | 2542.3219 | 93 | 86.55 | 84.75 | 84.75 | 84.75 | 0.89678 | 0.88388 | 0.88028 | 0.88028 | 0.88028 | 303.1602 | 59.1616 | 0.59138 | 0.1194 | 35 | 31.536 | 90% |  |  |  |  | ELE | P-TH-IGCC-COA-CCS06-MP1 | New Power Plant - IGCC coal CCS pre-combustion_Moneypoint Kinsale | PJ | GW | DAYNITE | [10 empty] | IGCC coal CCS pre-combustion_Moneypoint Kinsale
P-TH-SC-COA-CCS04-MP2 | New Power Plant - Pulverised coal supercritical CCS post-combustion_Moneypoint Spanish Point | PWRCOA | ELCC, PWRCO2S | 34% | 35% | 35% | 38% | 38% | 2030 |  |  | 3451.1153 | 3301.1153 | 3281.1153 | 75 | 67.5 | 63.75 | 63.75 | 63.75 | 0.83067 | 0.81417 | 0.80592 | 0.80592 | 0.80592 | 651.9537 | 59.1616 | 0.54628 | 0.1194 | 40 | 31.536 | 90% |  |  |  |  | ELE | P-TH-SC-COA-CCS04-MP2 | New Power Plant - Pulverised coal supercritical CCS post-combustion_Moneypoint Spanish Point | PJ | GW | DAYNITE | [10 empty] | Pulverised coal supercritical CCS post-combustion_Moneypoint Spanish Point
P-TH-IGCC-COA-CCS06-MP2 | New Power Plant - IGCC coal CCS pre-combustion_Moneypoint Spanish Point | PWRCOA | ELCC, PWRCO2S | 35% | 37% | 40% | 41% | 44% | 2030 |  |  | 3310.277 | 2990.277 | 2950.277 | 93 | 86.55 | 84.75 | 84.75 | 84.75 | 0.85167 | 0.83877 | 0.83517 | 0.83517 | 0.83517 | 651.9537 | 118.3233 | 0.54628 | 0.1194 | 35 | 31.536 | 90% |  |  |  |  | ELE | P-TH-IGCC-COA-CCS06-MP2 | New Power Plant - IGCC coal CCS pre-combustion_Moneypoint Spanish Point | PJ | GW | DAYNITE | [10 empty] | IGCC coal CCS pre-combustion_Moneypoint Spanish Point
P-TH-CCGT-GAS-CCS04-Cork1 | New Power Plant - CCGT advanced CCS post combustion_Cork Kinsale | PWRGAS | ELCC, PWRCO2S | 50% | 52% | 55% | 55% | 55% | 2030 |  |  | 1491.5259 | 1411.5259 | 1381.5259 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 0.24715 | 0.24715 | 0.24715 | 0.24715 | 0.24715 | 68.0303 | 33.4955 | 0.12237 | 0.064781 | 30 | 31.536 | 90% |  |  |  |  | ELE | P-TH-CCGT-GAS-CCS04-Cork1 | New Power Plant - CCGT advanced CCS post combustion_Cork Kinsale | PJ | GW | DAYNITE | [10 empty] | CCGT advanced CCS post combustion_Cork Kinsale
P-TH-CCGT-GAS-CCS04-Cork2 | New Power Plant - CCGT advanced CCS post combustion_Cork Spanish Point | PWRGAS | ELCC, PWRCO2S | 50% | 52% | 55% | 55% | 55% | 2030 |  |  | 2499.5522 | 2419.5522 | 2389.5522 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 0.76539 | 0.76539 | 0.76539 | 0.76539 | 0.76539 | 1042.5611 | 66.991 | 0.586 | 0.1194 | 30 | 31.536 | 90% |  |  |  |  | ELE | P-TH-CCGT-GAS-CCS04-Cork2 | New Power Plant - CCGT advanced CCS post combustion_Cork Spanish Point | PJ | GW | DAYNITE | [10 empty] | CCGT advanced CCS post combustion_Cork Spanish Point
P-TH-IGCC-PEA-CCS05-Offaly1 | New Power Plant - IGCC peat CCS pre combustion_Offaly Kinsale | PWRPEA | ELCC, PWRCO2S | 35% | 37% | 40% | 41% | 44% | 2030 | 3473.817 | 3133.817 | 2843.817 | 2573.817 | 2343.817 | 93 | 86.55 | 84.75 | 84.75 | 84.75 | 0.96521 | 0.95229 | 0.94127 | 0.93101 | 0.92227 | 395.4937 | 118.3233 | 0.73334 | 0.1194 | 35 | 31.536 | 90% |  |  |  |  | ELE | P-TH-IGCC-PEA-CCS05-Offaly1 | New Power Plant - IGCC peat CCS pre combustion_Offaly Kinsale | PJ | GW | DAYNITE | [10 empty] | IGCC peat CCS pre combustion_Offaly Kinsale
P-TH-IGCC-PEA-CCS05-Offaly2 | New Power Plant - IGCC peat CCS pre combustion_Offaly East Irish Sea | PWRPEA | ELCC, PWRCO2S | 35% | 37% | 40% | 41% | 44% | 2030 | 3625.7907 | 3285.7907 | 2995.7907 | 2725.7907 | 2495.7907 | 93 | 86.55 | 84.75 | 84.75 | 84.75 | 0.86936 | 0.85644 | 0.84542 | 0.83516 | 0.82642 | 547.4675 | 118.3233 | 0.63749 | 0.1194 | 35 | 31.536 | 90% |  |  |  |  | ELE | P-TH-IGCC-PEA-CCS05-Offaly2 | New Power Plant - IGCC peat CCS pre combustion_Offaly East Irish Sea | PJ | GW | DAYNITE | [10 empty] | IGCC peat CCS pre combustion_Offaly East Irish Sea
P-TH-IGCC-PEA-CCS05-Offaly3 | New Power Plant - IGCC peat CCS pre combustion_Offaly Central Irish Sea | PWRPEA | ELCC, PWRCO2S | 35% | 37% | 40% | 41% | 44% | 2030 | 3532.6197 | 3192.6197 | 2902.6197 | 2632.6197 | 2402.6197 | 93 | 86.55 | 84.75 | 84.75 | 84.75 | 0.79419 | 0.78127 | 0.77025 | 0.75999 | 0.75125 | 454.2965 | 118.3233 | 0.56231 | 0.1194 | 35 | 31.536 | 90% |  |  |  |  | ELE | P-TH-IGCC-PEA-CCS05-Offaly3 | New Power Plant - IGCC peat CCS pre combustion_Offaly Central Irish Sea | PJ | GW | DAYNITE | [10 empty] | IGCC peat CCS pre combustion_Offaly Central Irish Sea
P-TH-CCGT-GAS-CCS04-Dublin1 | New Power Plant - CCGT advanced CCS post combustion_Dublin East Irish Sea | PWRGAS | ELCC, PWRCO2S | 50% | 52% | 55% | 55% | 55% | 2030 |  |  | 1748.6567 | 1668.6567 | 1638.6567 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 0.24715 | 0.24715 | 0.24715 | 0.24715 | 0.24715 | 291.6657 | 66.991 | 0.12237 | 0.064781 | 30 | 31.536 | 90% |  |  |  |  | ELE | P-TH-CCGT-GAS-CCS04-Dublin1 | New Power Plant - CCGT advanced CCS post combustion_Dublin East Irish Sea | PJ | GW | DAYNITE | [10 empty] | CCGT advanced CCS post combustion_Dublin East Irish Sea
P-TH-CCGT-GAS-CCS04-Dublin2 | New Power Plant - CCGT advanced CCS post combustion_Dublin Central Irish Sea | PWRGAS | ELCC, PWRCO2S | 50% | 52% | 55% | 55% | 55% | 2030 |  |  | 1651.4348 | 1571.4348 | 1541.4348 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 0.20636 | 0.20636 | 0.20636 | 0.20636 | 0.20636 | 194.4438 | 66.991 | 0.081577 | 0.064781 | 30 | 31.536 | 90% |  |  |  |  | ELE | P-TH-CCGT-GAS-CCS04-Dublin2 | New Power Plant - CCGT advanced CCS post combustion_Dublin Central Irish Sea | PJ | GW | DAYNITE | [10 empty] | CCGT advanced CCS post combustion_Dublin Central Irish Sea
P-TH-SC-COA-CCS04-Kilroot1 | New Power Plant - Pulverised coal supercritical CCS post-combustion_Kilroot Portpatrick | PWRCOA | ELCC, PWRCO2S | 34% | 35% | 35% | 38% | 38% | 2030 |  |  | 2982.5512 | 2832.5512 | 2812.5512 | 75 | 67.5 | 63.75 | 63.75 | 63.75 | 0.38463 | 0.36813 | 0.35988 | 0.35988 | 0.35988 | 124.228 | 118.3233 | 0.10023 | 0.1194 | 40 | 31.536 | 90% |  |  |  |  | ELE | P-TH-SC-COA-CCS04-Kilroot1 | New Power Plant - Pulverised coal supercritical CCS post-combustion_Kilroot Portpatrick | PJ | GW | DAYNITE | [10 empty] | Pulverised coal supercritical CCS post-combustion_Kilroot Portpatrick
|  |  | ~FI_T | [21 empty] | 1.3122 | -> | 2000-2012 CPI
TechName | Comm-IN | Comm-Out | Year | START | Life | AF | CAP2ACT | NCAP_DRATE | EFF | INVCOST | FIXOM | VAROM | [12 empty] | (source Eurostat)
P-RNW-ST-BIO-CCS05 | PWRBIO | ELCC | 2018 | 2019 | 20 | 0.61 | 31.536 | 0.082 | 0.34 | 3373 | 118 |  |  |  |  | Source: JRC-EU-TIMES model documentation 2013 (p. 87 Biomass with carbon sequestration)
|  |  | 2020 |  |  |  |  | 0.09 | 0.34 | 3373 | 118
|  |  | 2030 |  |  |  |  | 0.09 | 0.35 | 2652 | 93
|  |  | 2050 |  |  |  |  | 0.09 | 0.36 | 2321 | 81
~FI_Process
Sets | TechName | TechDesc | Tact | Tcap | Tslvl | PrimaryCG | Vintage
ELE | P-RNW-ST-BIO-CCS05 | Steam Turbine Biomass WOO with CO2seq | PJ | GW | DAYNITE
Note on AT7: Possible TsLvl ANNUAL (Annual level) SEASON (Seasonal level) WEEKLY (Weekly level) DAYNITE (day and night level)
Note on AV7: Possible Vintage NO (if empty by default mean NO) YES
Note on AX7: Csets declarations are inherited until the next one is encountered. Possible Cset: NRG (Energy) ENV (Emission) DEM (Demand) MAT (Material) FIN (Financial)
Note on BB7: Possible Lim Type UP (upper for >=) LO (Lower for <=) FX (Fix for =)
Note on BC7: Possible CTSLvl SEASON (Seasonal level) WEEKLY (Weekly level) DAYNITE (day and night level)
Note on BD7: Possible PeakTS ANNUAL (to generate Peak Equation for all the TimeSlices) User TS (to generate Peak Equation for a single TS)
Note on BE7: Possible Ctype ELC (Electricity)
Note on L8: Alessandro Chiodi: Plant + Pipeline + Storage
Note on V8: Alessandro Chiodi: Plant + Pipeline + Storage
Note on AO8: Sets declarations are NOT inherited. Possible Process Sets ELE (Thermal Electric Power Plant) CHP (Combined Heat and Power) STGTSS (Pump Storage) PRE (Genric Process/Technology) DMD (Demand Device) IMP (Import) EXP (Export) MIN (Mining Process) RNW (Renewable Technology) HPL (Heating Plant)

## Win_ON_Cost_Data
fid | Merged_ID | Parcel | COUNTY - 1 | COUNTY - 2 | Station ID | name | operator | voltage | voltage_pr | voltage_te | Distance | Round Up Distance | Area_km_2_ | Class | Area With Packing Density Applied(km2) | Rationalised Output Per Parcel (MW) | Rationalised Output Per Parcel (MW) | Cost (€) | PS | Cost Per MW | Watt per Euro
1 | 1 | CL1-001 | KERRY | KERRY | SS-636 | Garranebane 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 15.861 | 16 | 0.122 | 1 | 0.122 | 3.45 | 3.45 | 1703340 | 1 | 493721.7391 | 2.0254
2 | 2 | CL1-002 | KERRY | KERRY | SS-636 | Garranebane 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.42 | 6 | 0.263 | 1 | 0.263 | 3.45 | 3.45 | 769410 | 4 | 223017.3913 | 4.484
3 | 3 | CL1-003 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.691 | 12 | 0.133 | 1 | 0.133 | 3.45 | 3.45 | 1492540 | 1 | 432620.2899 | 2.3115
4 | 4 | CL1-004 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 13.24 | 14 | 0.133 | 1 | 0.133 | 3.45 | 3.45 | 1597940 | 1 | 463171.0145 | 2.159
5 | 5 | CL1-005 | DONEGAL | DONEGAL | SS-138 | Creeslough 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.962 | 10 | 0.157 | 1 | 0.157 | 3.45 | 3.45 | 1387140 | 1 | 402069.5652 | 2.4871
6 | 6 | CL1-006 | DONEGAL | DONEGAL | SS-119 | Drumlough Hill (1) 38kV Substation | ESB Networks | 38000 | low | 38000 | 10.639 | 11 | 0.093 | 1 | 0.093 | 3.45 | 3.45 | 1439840 | 1 | 417344.9275 | 2.3961
7 | 7 | CL1-007 | CLARE | CLARE | SS-708 |  | EirGrid | 110000 | medium | 110000 | 1.526 | 2 | 0.126 | 1 | 0.126 | 3.45 | 3.45 | 1340080 | 11 | 388428.9855 | 2.5745
8 | 8 | CL1-008 | DUBLIN | DUBLIN | SS-014 | Ballyboden 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 6.009 | 7 | 0.28 | 1 | 0.28 | 3.45 | 3.45 | 839680 | 4 | 243385.5072 | 4.1087
9 | 9 | CL1-009 | DUBLIN | DUBLIN | SS-014 | Ballyboden 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 5.282 | 6 | 0.178 | 1 | 0.178 | 3.45 | 3.45 | 769410 | 4 | 223017.3913 | 4.484
10 | 10 | CL1-010 | WICKLOW | WICKLOW | SS-010 | Fassaroe 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 4.695 | 5 | 0.2 | 1 | 0.2 | 3.45 | 3.45 | 1679970 | 7 | 486947.8261 | 2.0536
11 | 11 | CL1-011 | WICKLOW | WICKLOW | SS-010 | Fassaroe 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.608 | 6 | 0.116 | 1 | 0.116 | 3.45 | 3.45 | 1732670 | 7 | 502223.1884 | 1.9911
12 | 12 | CL1-012 | WICKLOW | WICKLOW | SS-597 | Kilmartin 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.924 | 6 | 0.134 | 1 | 0.134 | 3.45 | 3.45 | 769410 | 4 | 223017.3913 | 4.484
13 | 13 | CL1-013 | CORK | CORK | SS-253 | Ballydehob 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.843 | 9 | 0.139 | 1 | 0.139 | 3.45 | 3.45 | 1334440 | 1 | 386794.2029 | 2.5854
14 | 14 | CL1-014 | WICKLOW | WICKLOW | SS-037 | Ballybeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 4.542 | 5 | 0.154 | 1 | 0.154 | 3.45 | 3.45 | 1679970 | 7 | 486947.8261 | 2.0536
15 | 15 | CL1-015 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.995 | 12 | 0.155 | 1 | 0.155 | 3.45 | 3.45 | 1492540 | 1 | 432620.2899 | 2.3115
16 | 16 | CL1-016 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.179 | 12 | 0.101 | 1 | 0.101 | 3.45 | 3.45 | 1492540 | 1 | 432620.2899 | 2.3115
17 | 17 | CL1-017 | DONEGAL | DONEGAL | SS-610 | Milford (North) 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.864 | 15 | 0.149 | 1 | 0.149 | 3.45 | 3.45 | 1650640 | 1 | 478446.3768 | 2.0901
18 | 18 | CL1-018 | DONEGAL | DONEGAL | SS-117 | Crockahenny 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.217 | 3 | 0.259 | 1 | 0.259 | 3.45 | 3.45 | 558600 | 4 | 161913.0435 | 6.1762
19 | 19 | CL1-019 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.887 | 8 | 0.337 | 1 | 0.337 | 3.45 | 3.45 | 909950 | 4 | 263753.6232 | 3.7914
20 | 20 | CL1-020 | DONEGAL | DONEGAL | SS-123 | Derrybeg 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.548 | 9 | 0.523 | 1 | 0.523 | 3.45 | 3.45 | 1334440 | 1 | 386794.2029 | 2.5854
21 | 21 | CL1-021 | KERRY | KERRY | SS-636 | Garranebane 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 13.635 | 14 | 0.289 | 1 | 0.289 | 3.45 | 3.45 | 1597940 | 1 | 463171.0145 | 2.159
22 | 22 | CL1-022 | WICKLOW | WICKLOW | SS-209 | Blessington 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.06 | 8 | 0.325 | 1 | 0.325 | 3.45 | 3.45 | 909950 | 4 | 263753.6232 | 3.7914
23 | 23 | CL1-023 | DONEGAL | DONEGAL | SS-117 | Crockahenny 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.876 | 5 | 0.614 | 1 | 0.4605 | 3.45 | 3.45 | 699140 | 4 | 202649.2754 | 4.9346
24 | 24 | CL1-024 | DONEGAL | DONEGAL | SS-617 | Mulreavy 110kV Substation | EirGrid | 110000 | 33000 | 110000 | 12.664 | 13 | 0.209 | 1 | 0.209 | 3.45 | 3.45 | 2101570 | 7 | 609150.7246 | 1.6416
25 | 25 | CL1-025 | CAVAN | CAVAN | SS-110 | Corraclassy 110kV Substation | EirGrid | 110000 |  |  | 10.905 | 11 | 0.786 | 1 | 0.5895 | 3.45 | 3.45 | 1996170 | 7 | 578600 | 1.7283
26 | 26 | CL1-026 | LOUTH | LOUTH | SS-650 | Ballymascanlan 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.994 | 5 | 0.211 | 1 | 0.211 | 3.45 | 3.45 | 699140 | 4 | 202649.2754 | 4.9346
27 | 27 | CL1-027 | CORK | CORK | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 12.641 | 13 | 0.281 | 1 | 0.281 | 3.45 | 3.45 | 1545240 | 1 | 447895.6522 | 2.2327
28 | 28 | CL1-028 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 12.848 | 13 | 0.134 | 1 | 0.134 | 3.45 | 3.45 | 1545240 | 1 | 447895.6522 | 2.2327
29 | 29 | CL1-029 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 12.044 | 13 | 0.17 | 1 | 0.17 | 3.45 | 3.45 | 1545240 | 1 | 447895.6522 | 2.2327
30 | 30 | CL1-030 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 13.637 | 14 | 0.496 | 1 | 0.496 | 3.45 | 3.45 | 1597940 | 1 | 463171.0145 | 2.159
31 | 31 | CL1-031 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.786 | 13 | 0.351 | 1 | 0.351 | 3.45 | 3.45 | 1545240 | 1 | 447895.6522 | 2.2327
32 | 32 | CL1-032 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.48 | 15 | 0.438 | 1 | 0.438 | 3.45 | 3.45 | 1650640 | 1 | 478446.3768 | 2.0901
33 | 33 | CL1-033 | KERRY | KERRY | SS-321 | Milltown 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.713 | 12 | 0.121 | 1 | 0.121 | 3.45 | 3.45 | 1492540 | 1 | 432620.2899 | 2.3115
34 | 34 | CL1-034 | KERRY | KERRY | SS-387 | Coolcorcoran 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.301 | 12 | 0.237 | 1 | 0.237 | 3.45 | 3.45 | 1492540 | 1 | 432620.2899 | 2.3115
35 | 35 | CL1-035 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.65 | 16 | 0.262 | 1 | 0.262 | 3.45 | 3.45 | 1703340 | 1 | 493721.7391 | 2.0254
36 | 36 | CL1-036 | KERRY | KERRY | SS-636 | Garranebane 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.091 | 5 | 0.567 | 1 | 0.567 | 3.45 | 3.45 | 699140 | 4 | 202649.2754 | 4.9346
37 | 37 | CL1-037 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.79 | 3 | 0.399 | 1 | 0.399 | 3.45 | 3.45 | 558600 | 4 | 161913.0435 | 6.1762
38 | 38 | CL1-038 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 14.268 | 15 | 0.109 | 1 | 0.109 | 3.45 | 3.45 | 1650640 | 1 | 478446.3768 | 2.0901
39 | 39 | CL1-039 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 9.745 | 10 | 0.123 | 1 | 0.123 | 3.45 | 3.45 | 1387140 | 1 | 402069.5652 | 2.4871
40 | 40 | CL1-040 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 9.612 | 10 | 0.099 | 1 | 0.099 | 3.45 | 3.45 | 1387140 | 1 | 402069.5652 | 2.4871
41 | 41 | CL1-041 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 15.118 | 16 | 0.109 | 1 | 0.109 | 3.45 | 3.45 | 1703340 | 1 | 493721.7391 | 2.0254
42 | 42 | CL1-042 | CORK | CORK | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 1.996 | 2 | 0.14 | 1 | 0.14 | 3.45 | 3.45 | 488330 | 4 | 141544.9275 | 7.0649
43 | 43 | CL1-043 | CORK | CORK | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 2.393 | 3 | 0.093 | 1 | 0.093 | 3.45 | 3.45 | 558600 | 4 | 161913.0435 | 6.1762
44 | 44 | CL1-044 | CORK | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.316 | 5 | 0.219 | 1 | 0.219 | 3.45 | 3.45 | 699140 | 4 | 202649.2754 | 4.9346
45 | 45 | CL1-045 | KERRY | KERRY | SS-637 | Kilgarvan 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.375 | 5 | 0.163 | 1 | 0.163 | 3.45 | 3.45 | 699140 | 4 | 202649.2754 | 4.9346
46 | 46 | CL1-046 | KERRY | KERRY | SS-637 | Kilgarvan 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.589 | 6 | 0.256 | 1 | 0.256 | 3.45 | 3.45 | 769410 | 4 | 223017.3913 | 4.484
47 | 47 | CL1-047 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.077 | 11 | 0.349 | 1 | 0.349 | 3.45 | 3.45 | 1439840 | 1 | 417344.9275 | 2.3961
48 | 48 | CL1-048 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.851 | 8 | 0.591 | 1 | 0.591 | 3.45 | 3.45 | 909950 | 4 | 263753.6232 | 3.7914
49 | 49 | CL1-049 | KERRY | KERRY | SS-140 | Ballyard 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 4.771 | 5 | 0.381 | 1 | 0.381 | 3.45 | 3.45 | 699140 | 4 | 202649.2754 | 4.9346
50 | 50 | CL1-050 | CLARE | CLARE | SS-595 | Kilkee 38kV Substation | ESB Networks | 38000 | 38000 | low | 23.476 | 24 | 0.195 | 1 | 0.195 | 3.45 | 3.45 | 2124940 | 1 | 615924.6377 | 1.6236
51 | 51 | CL1-051 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.891 | 16 | 0.111 | 1 | 0.111 | 3.45 | 3.45 | 1703340 | 1 | 493721.7391 | 2.0254
52 | 52 | CL1-052 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.806 | 16 | 0.437 | 1 | 0.437 | 3.45 | 3.45 | 1703340 | 1 | 493721.7391 | 2.0254
53 | 53 | CL1-053 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.451 | 12 | 0.189 | 1 | 0.189 | 3.45 | 3.45 | 1492540 | 1 | 432620.2899 | 2.3115
54 | 54 | CL1-054 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.715 | 6 | 0.331 | 1 | 0.331 | 3.45 | 3.45 | 769410 | 4 | 223017.3913 | 4.484
55 | 55 | CL1-055 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.746 | 5 | 0.316 | 1 | 0.316 | 3.45 | 3.45 | 699140 | 4 | 202649.2754 | 4.9346
56 | 56 | CL1-056 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.998 | 15 | 0.394 | 1 | 0.394 | 3.45 | 3.45 | 1650640 | 1 | 478446.3768 | 2.0901
57 | 57 | CL1-057 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 15.493 | 16 | 0.104 | 1 | 0.104 | 3.45 | 3.45 | 1703340 | 1 | 493721.7391 | 2.0254
58 | 58 | CL1-058 | GALWAY | GALWAY | SS-638 | Oughterard 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 12.648 | 13 | 0.377 | 1 | 0.377 | 3.45 | 3.45 | 1545240 | 1 | 447895.6522 | 2.2327
59 | 59 | CL1-059 | GALWAY | GALWAY | SS-638 | Oughterard 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.696 | 9 | 0.246 | 1 | 0.246 | 3.45 | 3.45 | 1334440 | 1 | 386794.2029 | 2.5854
60 | 60 | CL1-060 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 23.516 | 24 | 0.218 | 1 | 0.218 | 3.45 | 3.45 | 2681270 | 7 | 777179.7101 | 1.2867
61 | 61 | CL1-061 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 23.133 | 24 | 0.191 | 1 | 0.191 | 3.45 | 3.45 | 2681270 | 7 | 777179.7101 | 1.2867
62 | 62 | CL1-062 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 20.874 | 21 | 0.106 | 1 | 0.106 | 3.45 | 3.45 | 2523170 | 7 | 731353.6232 | 1.3673
63 | 63 | CL1-063 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.98 | 4 | 0.279 | 1 | 0.279 | 3.45 | 3.45 | 628870 | 4 | 182281.1594 | 5.486
64 | 64 | CL1-064 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.894 | 12 | 0.276 | 1 | 0.276 | 3.45 | 3.45 | 1492540 | 1 | 432620.2899 | 2.3115
65 | 65 | CL1-065 | MAYO | MAYO | SS-317 | Newport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.804 | 12 | 0.167 | 1 | 0.167 | 3.45 | 3.45 | 1492540 | 1 | 432620.2899 | 2.3115
66 | 66 | CL1-066 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 10.284 | 11 | 0.094 | 1 | 0.094 | 3.45 | 3.45 | 1996170 | 7 | 578600 | 1.7283
67 | 67 | CL1-067 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.543 | 6 | 0.698 | 1 | 0.5235 | 3.45 | 3.45 | 769410 | 4 | 223017.3913 | 4.484
68 | 68 | CL1-068 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.459 | 15 | 0.288 | 1 | 0.288 | 3.45 | 3.45 | 1650640 | 1 | 478446.3768 | 2.0901
69 | 69 | CL1-069 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.611 | 16 | 0.148 | 1 | 0.148 | 3.45 | 3.45 | 1703340 | 1 | 493721.7391 | 2.0254
70 | 70 | CL1-070 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.467 | 16 | 0.187 | 1 | 0.187 | 3.45 | 3.45 | 1703340 | 1 | 493721.7391 | 2.0254
71 | 71 | CL1-071 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 16.38 | 17 | 0.131 | 1 | 0.131 | 3.45 | 3.45 | 1756040 | 1 | 508997.1014 | 1.9646
72 | 72 | CL1-072 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 1.724 | 2 | 0.688 | 1 | 0.516 | 3.45 | 3.45 | 488330 | 4 | 141544.9275 | 7.0649
73 | 73 | CL1-073 | MAYO | MAYO | SS-234 | Crossmolina 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.238 | 14 | 0.596 | 1 | 0.447 | 3.45 | 3.45 | 1597940 | 1 | 463171.0145 | 2.159
74 | 74 | CL1-074 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 13.919 | 14 | 0.619 | 1 | 0.46425 | 3.45 | 3.45 | 2154270 | 7 | 624426.087 | 1.6015
75 | 75 | CL1-075 | MAYO | MAYO | SS-710 | Tawnaghmore 110kV Substation | EirGrid | 110000 | low | 110000 | 14.333 | 15 | 0.103 | 1 | 0.103 | 3.45 | 3.45 | 2206970 | 7 | 639701.4493 | 1.5632
76 | 76 | CL1-076 | MAYO | MAYO | SS-710 | Tawnaghmore 110kV Substation | EirGrid | 110000 | low | 110000 | 16.962 | 17 | 0.325 | 1 | 0.325 | 3.45 | 3.45 | 2312370 | 7 | 670252.1739 | 1.492
77 | 77 | CL1-077 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.99 | 8 | 0.129 | 1 | 0.129 | 3.45 | 3.45 | 909950 | 4 | 263753.6232 | 3.7914
78 | 78 | CL1-078 | SLIGO | SLIGO | SS-075 | Cunghill 110kV Substation | EirGrid | 110000 | 110000 | medium | 11.375 | 12 | 0.246 | 1 | 0.246 | 3.45 | 3.45 | 2048870 | 7 | 593875.3623 | 1.6839
79 | 79 | CL1-079 | SLIGO | SLIGO | SS-075 | Cunghill 110kV Substation | EirGrid | 110000 | 110000 | medium | 11.206 | 12 | 0.242 | 1 | 0.242 | 3.45 | 3.45 | 2048870 | 7 | 593875.3623 | 1.6839
80 | 80 | CL1-080 | SLIGO | LEITRIM | SS-042 | Ballytivnan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 10.22 | 11 | 0.206 | 1 | 0.206 | 3.45 | 3.45 | 1439840 | 1 | 417344.9275 | 2.3961
81 | 81 | CL1-081 | SLIGO | SLIGO | SS-042 | Ballytivnan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.688 | 9 | 0.249 | 1 | 0.249 | 3.45 | 3.45 | 1334440 | 1 | 386794.2029 | 2.5854
82 | 82 | CL1-082 | SLIGO | SLIGO | SS-042 | Ballytivnan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.236 | 9 | 0.132 | 1 | 0.132 | 3.45 | 3.45 | 1334440 | 1 | 386794.2029 | 2.5854
83 | 83 | CL1-083 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 4.929 | 5 | 0.527 | 1 | 0.527 | 3.45 | 3.45 | 699140 | 4 | 202649.2754 | 4.9346
84 | 84 | CL1-084 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 13.065 | 14 | 0.101 | 1 | 0.101 | 3.45 | 3.45 | 1597940 | 1 | 463171.0145 | 2.159
85 | 85 | CL1-085 | DONEGAL | DONEGAL | SS-090 | Corkermore 38kV Substation | ESB Networks | 38000 | low | 38000 | 9.143 | 10 | 0.599 | 1 | 0.44925 | 3.45 | 3.45 | 1387140 | 1 | 402069.5652 | 2.4871
86 | 86 | CL1-086 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 11.022 | 12 | 0.205 | 1 | 0.205 | 3.45 | 3.45 | 1492540 | 1 | 432620.2899 | 2.3115
87 | 87 | CL1-087 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 3.316 | 4 | 0.442 | 1 | 0.442 | 3.45 | 3.45 | 628870 | 4 | 182281.1594 | 5.486
88 | 88 | CL1-088 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 2.243 | 3 | 0.097 | 1 | 0.097 | 3.45 | 3.45 | 558600 | 4 | 161913.0435 | 6.1762
89 | 89 | CL1-089 | DONEGAL | DONEGAL | SS-252 | Killybegs 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 4.306 | 5 | 0.197 | 1 | 0.197 | 3.45 | 3.45 | 699140 | 4 | 202649.2754 | 4.9346
90 | 90 | CL1-090 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 3.787 | 4 | 0.318 | 1 | 0.318 | 3.45 | 3.45 | 1627270 | 7 | 471672.4638 | 2.1201
91 | 91 | CL1-091 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 3.504 | 4 | 0.395 | 1 | 0.395 | 3.45 | 3.45 | 1627270 | 7 | 471672.4638 | 2.1201
92 | 92 | CL1-092 | DONEGAL | DONEGAL | SS-123 | Derrybeg 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 10.189 | 11 | 0.286 | 1 | 0.286 | 3.45 | 3.45 | 1439840 | 1 | 417344.9275 | 2.3961
93 | 93 | CL1-093 | DONEGAL | DONEGAL | SS-119 | Drumlough Hill (1) 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.583 | 2 | 0.166 | 1 | 0.166 | 3.45 | 3.45 | 488330 | 4 | 141544.9275 | 7.0649
94 | 94 | CL1-094 | DONEGAL | DONEGAL | SS-239 | Moville 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 3.296 | 4 | 0.115 | 1 | 0.115 | 3.45 | 3.45 | 628870 | 4 | 182281.1594 | 5.486
95 | 95 | CL1-095 | DONEGAL | DONEGAL | SS-689 |  | ESB Networks | 38000 |  |  | 5.174 | 6 | 0.108 | 1 | 0.108 | 3.45 | 3.45 | 769410 | 4 | 223017.3913 | 4.484
96 | 96 | CL1-096 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.713 | 11 | 0.108 | 1 | 0.108 | 3.45 | 3.45 | 1439840 | 1 | 417344.9275 | 2.3961
97 | 97 | CL1-097 | CARLOW | CARLOW | SS-481 | Castledockrell 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 10.637 | 11 | 0.364 | 1 | 0.364 | 3.45 | 3.45 | 1996170 | 7 | 578600 | 1.7283
98 | 98 | CL1-098 | CARLOW | WEXFORD | SS-481 | Castledockrell 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 9.874 | 10 | 0.328 | 1 | 0.328 | 3.45 | 3.45 | 1943470 | 7 | 563324.6377 | 1.7752
99 | 99 | CL1-099 | CARLOW | CARLOW | SS-494 | Bunclody 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.975 | 10 | 0.438 | 1 | 0.438 | 3.45 | 3.45 | 1387140 | 1 | 402069.5652 | 2.4871
100 | 100 | CL1-100 | WICKLOW | WICKLOW | SS-062 | Stratford 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.266 | 9 | 1.033 | 1 | 0.77475 | 6.9 | 6.9 | 1890770 | 7 | 274024.6377 | 3.6493
101 | 101 | CL1-101 | WICKLOW | WICKLOW | SS-062 | Stratford 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 10.241 | 11 | 0.101 | 1 | 0.101 | 3.45 | 3.45 | 1996170 | 7 | 578600 | 1.7283
102 | 102 | CL1-102 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.313 | 10 | 0.157 | 1 | 0.157 | 3.45 | 3.45 | 1387140 | 1 | 402069.5652 | 2.4871
103 | 103 | CL1-103 | WICKLOW | WICKLOW | SS-209 | Blessington 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.176 | 7 | 0.405 | 1 | 0.405 | 3.45 | 3.45 | 839680 | 4 | 243385.5072 | 4.1087
104 | 104 | CL1-104 | WICKLOW | WICKLOW | SS-209 | Blessington 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.937 | 11 | 0.309 | 1 | 0.309 | 3.45 | 3.45 | 1439840 | 1 | 417344.9275 | 2.3961
105 | 105 | CL1-105 | DUBLIN | DUBLIN | SS-018 | Old Bawn 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 10.006 | 11 | 0.442 | 1 | 0.442 | 3.45 | 3.45 | 1439840 | 1 | 417344.9275 | 2.3961
106 | 106 | CL1-106 | DUBLIN | DUBLIN | SS-017 | Sandyford 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.975 | 4 | 0.279 | 1 | 0.279 | 3.45 | 3.45 | 628870 | 4 | 182281.1594 | 5.486
107 | 107 | CL1-107 | DUBLIN | DUBLIN | SS-018 | Old Bawn 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 5.83 | 6 | 0.405 | 1 | 0.405 | 3.45 | 3.45 | 769410 | 4 | 223017.3913 | 4.484
108 | 108 | CL1-108 | KERRY | KERRY | SS-637 | Kilgarvan 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.286 | 5 | 0.503 | 1 | 0.503 | 3.45 | 3.45 | 699140 | 4 | 202649.2754 | 4.9346
109 | 109 | CL1-109 | CORK | CORK | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.288 | 4 | 0.491 | 1 | 0.491 | 3.45 | 3.45 | 628870 | 4 | 182281.1594 | 5.486
110 | 110 | CL1-110 | CORK | CORK | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.534 | 3 | 0.277 | 1 | 0.277 | 3.45 | 3.45 | 558600 | 4 | 161913.0435 | 6.1762
111 | 111 | CL1-111 | TIPPERARY | TIPPERARY | SS-645 | Toomevara 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.354 | 8 | 0.314 | 1 | 0.314 | 3.45 | 3.45 | 909950 | 4 | 263753.6232 | 3.7914
112 | 112 | CL1-112 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 4.496 | 5 | 0.154 | 1 | 0.154 | 3.45 | 3.45 | 1679970 | 7 | 486947.8261 | 2.0536
113 | 113 | CL1-113 | DONEGAL | DONEGAL | SS-686 | Dungloe 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.425 | 9 | 0.894 | 1 | 0.6705 | 6.9 | 6.9 | 1379800 | 2 | 199971.0145 | 5.0007
114 | 114 | CL1-114 | DONEGAL | DONEGAL | SS-195 | Cark 110kV Substation | EirGrid | 110000 | low | 110000 | 3.157 | 4 | 0.159 | 1 | 0.159 | 3.45 | 3.45 | 1627270 | 7 | 471672.4638 | 2.1201
115 | 115 | CL1-115 | CAVAN | LEITRIM | SS-110 | Corraclassy 110kV Substation | EirGrid | 110000 |  |  | 10.141 | 11 | 0.273 | 1 | 0.273 | 3.45 | 3.45 | 1996170 | 7 | 578600 | 1.7283
116 | 116 | CL1-116 | LEITRIM | LEITRIM | SS-304 | Arigna 110kV Substation | EirGrid | 110000 | 110000 | 20000 | 9.782 | 10 | 0.13 | 1 | 0.13 | 3.45 | 3.45 | 1943470 | 7 | 563324.6377 | 1.7752
117 | 117 | CL1-117 | SLIGO | SLIGO | SS-078 | Glenree 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 4.591 | 5 | 0.175 | 1 | 0.175 | 3.45 | 3.45 | 1679970 | 7 | 486947.8261 | 2.0536
118 | 118 | CL1-118 | DONEGAL | DONEGAL | SS-195 | Cark 110kV Substation | EirGrid | 110000 | low | 110000 | 3.643 | 4 | 0.246 | 1 | 0.246 | 3.45 | 3.45 | 1627270 | 7 | 471672.4638 | 2.1201
119 | 119 | CL1-119 | DONEGAL | DONEGAL | SS-643 | Donegal 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.667 | 7 | 0.213 | 1 | 0.213 | 3.45 | 3.45 | 839680 | 4 | 243385.5072 | 4.1087
120 | 120 | CL1-120 | DONEGAL | DONEGAL | SS-688 | Clogher 110kV Substation | EirGrid | 110000 |  |  | 4.568 | 5 | 1.008 | 1 | 0.756 | 6.9 | 6.9 | 1679970 | 7 | 243473.913 | 4.1072
121 | 121 | CL1-121 | DONEGAL | DONEGAL | SS-083 | Golagh 110kV Substation | EirGrid | 110000 | 38000 | 110000 | 8.397 | 9 | 0.146 | 1 | 0.146 | 3.45 | 3.45 | 1890770 | 7 | 548049.2754 | 1.8247
122 | 122 | CL1-122 | DONEGAL | DONEGAL | SS-688 | Clogher 110kV Substation | EirGrid | 110000 |  |  | 9.522 | 10 | 0.479 | 1 | 0.479 | 3.45 | 3.45 | 1943470 | 7 | 563324.6377 | 1.7752
123 | 123 | CL1-123 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 7.106 | 8 | 0.523 | 1 | 0.523 | 3.45 | 3.45 | 1838070 | 7 | 532773.913 | 1.877
124 | 124 | CL1-124 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 9.667 | 10 | 0.187 | 1 | 0.187 | 3.45 | 3.45 | 1943470 | 7 | 563324.6377 | 1.7752
125 | 125 | CL1-125 | GALWAY | GALWAY | SS-662 | Cloosh 110kV Substation | EirGrid | 110000 | low | 110000 | 6.474 | 7 | 0.621 | 1 | 0.46575 | 3.45 | 3.45 | 1785370 | 7 | 517498.5507 | 1.9324
126 | 126 | CL1-126 | GALWAY | GALWAY | SS-623 | Uggool 110kV Substation | EirGrid | 110000 | 33000 | 110000 | 6.479 | 7 | 0.665 | 1 | 0.49875 | 3.45 | 3.45 | 1785370 | 7 | 517498.5507 | 1.9324
127 | 127 | CL1-127 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 6.76 | 7 | 0.109 | 1 | 0.109 | 3.45 | 3.45 | 1785370 | 7 | 517498.5507 | 1.9324
128 | 128 | CL1-128 | WATERFORD | TIPPERARY | SS-455 | Ardfinnan 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.754 | 8 | 0.315 | 1 | 0.315 | 3.45 | 3.45 | 909950 | 4 | 263753.6232 | 3.7914
129 | 129 | CL1-129 | WATERFORD | WATERFORD | SS-659 | Spa Road 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 4.24 | 5 | 0.563 | 1 | 0.563 | 3.45 | 3.45 | 699140 | 4 | 202649.2754 | 4.9346
130 | 130 | CL1-130 | WATERFORD | WATERFORD | SS-205 | Dungarvan 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 9.346 | 10 | 0.182 | 1 | 0.182 | 3.45 | 3.45 | 1943470 | 7 | 563324.6377 | 1.7752
131 | 131 | CL1-131 | TIPPERARY | TIPPERARY | SS-257 | Kilshanny 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.74 | 11 | 0.164 | 1 | 0.164 | 3.45 | 3.45 | 1439840 | 1 | 417344.9275 | 2.3961
132 | 132 | CL1-132 | TIPPERARY | TIPPERARY | SS-315 | Cahir 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 9.181 | 10 | 0.101 | 1 | 0.101 | 3.45 | 3.45 | 1387140 | 1 | 402069.5652 | 2.4871
133 | 133 | CL1-133 | TIPPERARY | TIPPERARY | SS-585 | Kilross Road 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.796 | 9 | 0.223 | 1 | 0.223 | 3.45 | 3.45 | 1334440 | 1 | 386794.2029 | 2.5854
134 | 134 | CL1-134 | CARLOW | WEXFORD | SS-492 | Graigue 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.378 | 10 | 0.537 | 1 | 0.537 | 3.45 | 3.45 | 1387140 | 1 | 402069.5652 | 2.4871
135 | 135 | CL1-135 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.92 | 16 | 0.552 | 1 | 0.552 | 3.45 | 3.45 | 1703340 | 1 | 493721.7391 | 2.0254
136 | 136 | CL1-136 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.727 | 8 | 0.298 | 1 | 0.298 | 3.45 | 3.45 | 909950 | 4 | 263753.6232 | 3.7914
137 | 137 | CL1-137 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.653 | 5 | 0.518 | 1 | 0.518 | 3.45 | 3.45 | 699140 | 4 | 202649.2754 | 4.9346
138 | 138 | CL1-138 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.195 | 11 | 0.188 | 1 | 0.188 | 3.45 | 3.45 | 1439840 | 1 | 417344.9275 | 2.3961
139 | 139 | CL1-139 | WEXFORD | WEXFORD | SS-616 | Ballinvally 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 6.932 | 7 | 0.165 | 1 | 0.165 | 3.45 | 3.45 | 839680 | 4 | 243385.5072 | 4.1087
140 | 140 | CL1-140 | CORK | CORK | SS-562 | Bantry 38kV Substation | ESB Networks | 38000 | 38000 | low | 19.408 | 20 | 0.436 | 1 | 0.436 | 3.45 | 3.45 | 1914140 | 1 | 554823.1884 | 1.8024
141 | 141 | CL1-141 | CORK | CORK | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 7.195 | 8 | 0.559 | 1 | 0.559 | 3.45 | 3.45 | 909950 | 4 | 263753.6232 | 3.7914
142 | 142 | CL1-142 | CORK | CORK | SS-261 | Milane Hill 38kV Station | ESB Networks | 38000 |  |  | 4.465 | 5 | 0.223 | 1 | 0.223 | 3.45 | 3.45 | 699140 | 4 | 202649.2754 | 4.9346
143 | 143 | CL1-143 | CLARE | CLARE | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.07 | 16 | 0.367 | 1 | 0.367 | 3.45 | 3.45 | 1703340 | 1 | 493721.7391 | 2.0254
144 | 144 | CL1-144 | KILKENNY | KILKENNY | SS-492 | Graigue 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.279 | 4 | 0.606 | 1 | 0.4545 | 3.45 | 3.45 | 628870 | 4 | 182281.1594 | 5.486
145 | 145 | CL1-145 | WICKLOW | WICKLOW | SS-591 | Shillelagh 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.399 | 5 | 0.227 | 1 | 0.227 | 3.45 | 3.45 | 699140 | 4 | 202649.2754 | 4.9346
146 | 146 | CL1-146 | CLARE | CLARE | SS-503 | Scariff 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 9.263 | 10 | 0.449 | 1 | 0.449 | 3.45 | 3.45 | 1387140 | 1 | 402069.5652 | 2.4871
147 | 147 | CL1-147 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.032 | 6 | 0.247 | 1 | 0.247 | 3.45 | 3.45 | 769410 | 4 | 223017.3913 | 4.484
148 | 148 | CL1-148 | CORK | CORK | SS-355 | Carrigcannon 38kV Substation | ESB Networks | 38000 | low | 38000 | 6.544 | 7 | 0.653 | 1 | 0.48975 | 3.45 | 3.45 | 839680 | 4 | 243385.5072 | 4.1087
149 | 149 | CL1-149 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 13.503 | 14 | 0.366 | 1 | 0.366 | 3.45 | 3.45 | 1597940 | 1 | 463171.0145 | 2.159
150 | 150 | CL1-150 | WICKLOW | WICKLOW | SS-570 | Kilcoole 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.276 | 6 | 0.343 | 1 | 0.343 | 3.45 | 3.45 | 769410 | 4 | 223017.3913 | 4.484
151 | 151 | CL1-151 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.562 | 8 | 0.278 | 1 | 0.278 | 3.45 | 3.45 | 909950 | 4 | 263753.6232 | 3.7914
152 | 152 | CL1-152 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.932 | 8 | 0.197 | 1 | 0.197 | 3.45 | 3.45 | 909950 | 4 | 263753.6232 | 3.7914
153 | 153 | CL1-153 | CLARE | CLARE | SS-708 |  | EirGrid | 110000 | medium | 110000 | 4.096 | 5 | 0.188 | 1 | 0.188 | 3.45 | 3.45 | 1679970 | 7 | 486947.8261 | 2.0536
154 | 154 | CL1-154 | DONEGAL | DONEGAL | SS-138 | Creeslough 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.186 | 9 | 0.287 | 1 | 0.287 | 3.45 | 3.45 | 1334440 | 1 | 386794.2029 | 2.5854
155 | 155 | CL1-155 | DONEGAL | DONEGAL | SS-138 | Creeslough 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.543 | 7 | 0.85 | 1 | 0.6375 | 6.9 | 6.9 | 839680 | 4 | 121692.7536 | 8.2174
156 | 156 | CL1-156 | DONEGAL | DONEGAL | SS-610 | Milford (North) 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.01 | 9 | 0.424 | 1 | 0.424 | 3.45 | 3.45 | 1334440 | 1 | 386794.2029 | 2.5854
157 | 157 | CL1-157 | DONEGAL | DONEGAL | SS-610 | Milford (North) 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.213 | 8 | 0.457 | 1 | 0.457 | 3.45 | 3.45 | 909950 | 4 | 263753.6232 | 3.7914
158 | 158 | CL1-158 | MAYO | MAYO | SS-234 | Crossmolina 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.817 | 11 | 0.405 | 1 | 0.405 | 3.45 | 3.45 | 1439840 | 1 | 417344.9275 | 2.3961
159 | 159 | CL1-159 | MAYO | MAYO | SS-710 | Tawnaghmore 110kV Substation | EirGrid | 110000 | low | 110000 | 12.265 | 13 | 0.562 | 1 | 0.562 | 3.45 | 3.45 | 2101570 | 7 | 609150.7246 | 1.6416
160 | 160 | CL1-160 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.322 | 10 | 0.224 | 1 | 0.224 | 3.45 | 3.45 | 1387140 | 1 | 402069.5652 | 2.4871
161 | 161 | CL1-161 | SLIGO | SLIGO | SS-206 | Boyle 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 10.985 | 11 | 0.211 | 1 | 0.211 | 3.45 | 3.45 | 1439840 | 1 | 417344.9275 | 2.3961
162 | 162 | CL1-162 | SLIGO | SLIGO | SS-068 | Ballymote 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.173 | 8 | 0.152 | 1 | 0.152 | 3.45 | 3.45 | 909950 | 4 | 263753.6232 | 3.7914
163 | 163 | CL1-163 | MAYO | MAYO | SS-078 | Glenree 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 7.654 | 8 | 0.25 | 1 | 0.25 | 3.45 | 3.45 | 1838070 | 7 | 532773.913 | 1.877
164 | 164 | CL1-164 | MAYO | MAYO | SS-203 | Foxford 38kV Substation | ESB Networks | 38000 |  |  | 4.082 | 5 | 0.202 | 1 | 0.202 | 3.45 | 3.45 | 699140 | 4 | 202649.2754 | 4.9346
165 | 165 | CL1-165 | SLIGO | LEITRIM | SS-042 | Ballytivnan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.739 | 8 | 0.379 | 1 | 0.379 | 3.45 | 3.45 | 909950 | 4 | 263753.6232 | 3.7914
166 | 166 | CL1-166 | SLIGO | LEITRIM | SS-042 | Ballytivnan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.068 | 8 | 0.265 | 1 | 0.265 | 3.45 | 3.45 | 909950 | 4 | 263753.6232 | 3.7914
167 | 167 | CL1-167 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 3.702 | 4 | 0.159 | 1 | 0.159 | 3.45 | 3.45 | 628870 | 4 | 182281.1594 | 5.486
168 | 168 | CL1-168 | DONEGAL | DONEGAL | SS-239 | Moville 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.191 | 5 | 0.178 | 1 | 0.178 | 3.45 | 3.45 | 699140 | 4 | 202649.2754 | 4.9346
169 | 169 | CL1-169 | DONEGAL | DONEGAL | SS-272 | Carndonagh 38kV | ESB Networks | 38000 | 38000 | low | 5.402 | 6 | 0.25 | 1 | 0.25 | 3.45 | 3.45 | 769410 | 4 | 223017.3913 | 4.484
170 | 170 | CL1-170 | DONEGAL | DONEGAL | SS-117 | Crockahenny 38kV Substation | ESB Networks | 38000 | low | 38000 | 6.305 | 7 | 0.442 | 1 | 0.442 | 3.45 | 3.45 | 839680 | 4 | 243385.5072 | 4.1087
171 | 171 | CL1-171 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.1 | 14 | 0.44 | 1 | 0.44 | 3.45 | 3.45 | 1597940 | 1 | 463171.0145 | 2.159
172 | 172 | CL1-172 | CAVAN | MEATH | SS-110 | Corraclassy 110kV Substation | EirGrid | 110000 |  |  | 6.682 | 7 | 2.542 | 1 | 1.9065 | 20.7 | 20.7 | 2086600 | 8 | 100801.9324 | 9.9204
173 | 173 | CL1-173 | LOUTH | LOUTH | SS-651 | Grange 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.29 | 6 | 2.45 | 1 | 1.8375 | 17.25 | 17.25 | 769410 | 4 | 44603.4783 | 22.4198
174 | 174 | CL1-174 | CORK | CORK | SS-562 | Bantry 38kV Substation | ESB Networks | 38000 | 38000 | low | 24.774 | 25 | 1.095 | 1 | 0.82125 | 6.9 | 6.9 | 2223000 | 2 | 322173.913 | 3.1039
175 | 175 | CL1-175 | CORK | CORK | SS-562 | Bantry 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.734 | 16 | 0.571 | 1 | 0.571 | 3.45 | 3.45 | 1703340 | 1 | 493721.7391 | 2.0254
176 | 176 | CL1-176 | CORK | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 13.7 | 14 | 4.122 | 1 | 3.0915 | 31.05 | 31.05 | 1905430 | 6 | 61366.5056 | 16.2955
177 | 177 | CL1-177 | CORK | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.203 | 11 | 13.51 | 1 | 10.1325 | 110.4 | 110.4 | 3237370 | 11 | 29324.0036 | 34.1018
178 | 178 | CL1-178 | CORK | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.849 | 8 | 0.465 | 1 | 0.465 | 3.45 | 3.45 | 909950 | 4 | 263753.6232 | 3.7914
179 | 179 | CL1-179 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.332 | 10 | 1.394 | 1 | 1.0455 | 10.35 | 10.35 | 1469550 | 3 | 141985.5072 | 7.043
180 | 180 | CL1-180 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.323 | 12 | 1.358 | 1 | 1.0185 | 10.35 | 10.35 | 1574950 | 3 | 152169.0821 | 6.5716
181 | 181 | CL1-181 | CORK | KERRY | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.874 | 9 | 4.963 | 1 | 3.7222 | 37.95 | 37.95 | 1349130 | 6 | 35550.1976 | 28.1292
182 | 182 | CL1-182 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.859 | 5 | 6.039 | 1 | 4.5292 | 48.3 | 48.3 | 1972510 | 11 | 40838.7164 | 24.4866
183 | 183 | CL1-183 | CORK | KERRY | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.054 | 10 | 5.872 | 1 | 4.404 | 48.3 | 48.3 | 3026560 | 11 | 62661.6977 | 15.9587
184 | 184 | CL1-184 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 15.354 | 16 | 8.86 | 1 | 6.645 | 72.45 | 72.45 | 4291420 | 11 | 59232.8502 | 16.8825
185 | 185 | CL1-185 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 11.12 | 12 | 6.948 | 1 | 5.211 | 55.2 | 55.2 | 3448180 | 11 | 62467.029 | 16.0084
186 | 186 | CL1-186 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.97 | 10 | 2.042 | 1 | 1.5315 | 13.8 | 13.8 | 1050490 | 4 | 76122.4638 | 13.1367
187 | 187 | CL1-187 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 10.584 | 11 | 2.392 | 1 | 1.794 | 17.25 | 17.25 | 1120760 | 4 | 64971.5942 | 15.3913
188 | 188 | CL1-188 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 13.975 | 14 | 13.357 | 1 | 10.0177 | 106.95 | 106.95 | 3869800 | 11 | 36183.2632 | 27.6371
189 | 189 | CL1-189 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 12.384 | 13 | 1.422 | 1 | 1.0665 | 10.35 | 10.35 | 1627650 | 3 | 157260.8696 | 6.3589
190 | 190 | CL1-190 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.513 | 14 | 5.568 | 1 | 4.176 | 44.85 | 44.85 | 1905430 | 6 | 42484.5039 | 23.538
191 | 191 | CL1-191 | KERRY | KERRY | SS-321 | Milltown 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 18.797 | 19 | 1.104 | 1 | 0.828 | 6.9 | 6.9 | 1906800 | 2 | 276347.8261 | 3.6186
192 | 192 | CL1-192 | KERRY | KERRY | SS-321 | Milltown 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 14.896 | 15 | 15.406 | 1 | 11.5545 | 124.2 | 124.2 | 5849260 | 13 | 47095.4911 | 21.2335
193 | 193 | CL1-193 | KERRY | KERRY | SS-387 | Coolcorcoran 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.408 | 11 | 2.861 | 1 | 2.1458 | 20.7 | 20.7 | 1120760 | 4 | 54142.9952 | 18.4696
194 | 194 | CL1-194 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.569 | 6 | 2.152 | 1 | 1.614 | 17.25 | 17.25 | 769410 | 4 | 44603.4783 | 22.4198
195 | 195 | CL1-195 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.039 | 8 | 0.663 | 1 | 0.49725 | 3.45 | 3.45 | 909950 | 4 | 263753.6232 | 3.7914
196 | 196 | CL1-196 | KERRY | KERRY | SS-637 | Kilgarvan 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.924 | 8 | 9.987 | 1 | 7.4902 | 79.35 | 79.35 | 2604940 | 11 | 32828.4814 | 30.4614
197 | 197 | CL1-197 | KERRY | KERRY | SS-072 | Clonkeen 110kV Substation | EirGrid | 110000 |  |  | 5.594 | 6 | 2.063 | 1 | 1.5473 | 13.8 | 13.8 | 2016330 | 8 | 146110.8696 | 6.8441
198 | 198 | CL1-198 | KERRY | KERRY | SS-636 | Garranebane 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.144 | 10 | 0.369 | 1 | 0.369 | 3.45 | 3.45 | 1387140 | 1 | 402069.5652 | 2.4871
199 | 199 | CL1-199 | KERRY | KERRY | SS-636 | Garranebane 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.532 | 9 | 6.743 | 1 | 5.0572 | 55.2 | 55.2 | 2815750 | 11 | 51009.9638 | 19.604
200 | 200 | CL1-200 | KERRY | KERRY | SS-636 | Garranebane 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.371 | 6 | 1.184 | 1 | 0.888 | 6.9 | 6.9 | 769410 | 4 | 111508.6957 | 8.9679
201 | 201 | CL1-201 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 8.279 | 9 | 17.913 | 1 | 13.4348 | 144.9 | 144.9 | 4339180 | 12 | 29946.0317 | 33.3934
202 | 202 | CL1-202 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 13.341 | 14 | 0.966 | 1 | 0.7245 | 6.9 | 6.9 | 1643300 | 2 | 238159.4203 | 4.1989
203 | 203 | CL1-203 | KERRY | KERRY | SS-321 | Milltown 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 16.988 | 17 | 1.43 | 1 | 1.0725 | 10.35 | 10.35 | 1838450 | 3 | 177628.0193 | 5.6297
204 | 204 | CL1-204 | CORK | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.629 | 9 | 12.789 | 1 | 9.5917 | 103.5 | 103.5 | 2815750 | 11 | 27205.314 | 36.7575
205 | 205 | CL1-205 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 3.383 | 4 | 3.72 | 1 | 2.79 | 27.6 | 27.6 | 703110 | 5 | 25475 | 39.2542
206 | 206 | CL1-206 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 14.468 | 15 | 2.644 | 1 | 1.983 | 20.7 | 20.7 | 1401840 | 4 | 67721.7391 | 14.7663
207 | 207 | CL1-207 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.946 | 9 | 15.538 | 1 | 11.6535 | 127.65 | 127.65 | 4339180 | 12 | 33992.7928 | 29.418
208 | 208 | CL1-208 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 3.081 | 4 | 6.578 | 1 | 4.9335 | 51.75 | 51.75 | 1761700 | 11 | 34042.5121 | 29.375
209 | 209 | CL1-209 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.995 | 8 | 8.582 | 1 | 6.4365 | 69 | 69 | 2604940 | 11 | 37752.7536 | 26.4881
210 | 210 | CL1-210 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.843 | 8 | 10.34 | 1 | 7.755 | 82.8 | 82.8 | 2604940 | 11 | 31460.628 | 31.7858
211 | 211 | CL1-211 | KERRY | KERRY | SS-667 | Ballyrickard 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 9.133 | 10 | 16.492 | 1 | 12.369 | 134.55 | 134.55 | 4719260 | 12 | 35074.3961 | 28.5108
212 | 212 | CL1-212 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.018 | 5 | 4.313 | 1 | 3.2348 | 34.5 | 34.5 | 904090 | 6 | 26205.5072 | 38.1599
213 | 213 | CL1-213 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 21.669 | 22 | 1.913 | 1 | 1.4347 | 13.8 | 13.8 | 1893730 | 4 | 137226.8116 | 7.2872
214 | 214 | CL1-214 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 22.972 | 23 | 4.004 | 1 | 3.003 | 31.05 | 31.05 | 2906770 | 6 | 93615.781 | 10.682
215 | 215 | CL1-215 | CLARE | CLARE | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 19.212 | 20 | 1.345 | 1 | 1.0088 | 10.35 | 10.35 | 1996550 | 3 | 192903.3816 | 5.1839
216 | 216 | CL1-216 | CLARE | CLARE | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 19.128 | 20 | 0.554 | 1 | 0.554 | 3.45 | 3.45 | 1914140 | 1 | 554823.1884 | 1.8024
217 | 217 | CL1-217 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.741 | 14 | 5.485 | 1 | 4.1138 | 44.85 | 44.85 | 1905430 | 6 | 42484.5039 | 23.538
218 | 218 | CL1-218 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.695 | 4 | 2.983 | 1 | 2.2372 | 24.15 | 24.15 | 703110 | 5 | 29114.2857 | 34.3474
219 | 219 | CL1-219 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.263 | 7 | 11.505 | 1 | 8.6288 | 93.15 | 93.15 | 2394130 | 11 | 25701.8787 | 38.9077
220 | 220 | CL1-220 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.121 | 8 | 1.63 | 1 | 1.2225 | 10.35 | 10.35 | 909950 | 4 | 87917.8744 | 11.3743
221 | 221 | CL1-221 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.911 | 11 | 1.547 | 1 | 1.1603 | 10.35 | 10.35 | 1522250 | 3 | 147077.2947 | 6.7991
222 | 222 | CL1-222 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.39 | 10 | 18.324 | 1 | 13.743 | 148.35 | 148.35 | 4719260 | 12 | 31811.6616 | 31.435
223 | 223 | CL1-223 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.161 | 14 | 6.434 | 1 | 4.8255 | 51.75 | 51.75 | 3869800 | 11 | 74778.744 | 13.3728
224 | 224 | CL1-224 | MAYO | GALWAY | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 20.358 | 21 | 20.53 | 1 | 15.3975 | 169.05 | 169.05 | 15643160 | 13 | 92535.6995 | 10.8066
225 | 225 | CL1-225 | MAYO | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 18.419 | 19 | 2.496 | 1 | 1.872 | 17.25 | 17.25 | 1682920 | 4 | 97560.5797 | 10.25
226 | 226 | CL1-226 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 16.926 | 17 | 10.236 | 1 | 7.677 | 82.8 | 82.8 | 4502230 | 11 | 54374.7585 | 18.3909
227 | 227 | CL1-227 | GALWAY | GALWAY | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 15.008 | 16 | 1.758 | 1 | 1.3185 | 13.8 | 13.8 | 1472110 | 4 | 106674.6377 | 9.3743
228 | 228 | CL1-228 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 17.091 | 18 | 12.993 | 1 | 9.7447 | 106.95 | 106.95 | 4713040 | 11 | 44067.6952 | 22.6924
229 | 229 | CL1-229 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 13.438 | 14 | 8.719 | 1 | 6.5392 | 69 | 69 | 3869800 | 11 | 56084.058 | 17.8304
230 | 230 | CL1-230 | GALWAY | GALWAY | SS-638 | Oughterard 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 10.127 | 11 | 2.15 | 1 | 1.6125 | 17.25 | 17.25 | 1120760 | 4 | 64971.5942 | 15.3913
231 | 231 | CL1-231 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 12.156 | 13 | 1.283 | 1 | 0.96225 | 10.35 | 10.35 | 2101570 | 7 | 203050.2415 | 4.9249
232 | 232 | CL1-232 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.141 | 8 | 1.998 | 1 | 1.4985 | 13.8 | 13.8 | 909950 | 4 | 65938.4058 | 15.1657
233 | 233 | CL1-233 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.739 | 8 | 4.156 | 1 | 3.117 | 31.05 | 31.05 | 1237870 | 6 | 39866.9887 | 25.0834
234 | 234 | CL1-234 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 24.853 | 25 | 4.089 | 1 | 3.0668 | 31.05 | 31.05 | 4735350 | 10 | 152507.2464 | 6.5571
235 | 235 | CL1-235 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 20.307 | 21 | 18.723 | 1 | 14.0422 | 151.8 | 151.8 | 7821580 | 13 | 51525.5599 | 19.4078
236 | 236 | CL1-236 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 16.598 | 17 | 4.129 | 1 | 3.0967 | 31.05 | 31.05 | 2239210 | 6 | 72116.2641 | 13.8665
237 | 237 | CL1-237 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.876 | 12 | 2.761 | 1 | 2.0708 | 20.7 | 20.7 | 1191030 | 4 | 57537.6812 | 17.3799
238 | 238 | CL1-238 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 11.364 | 12 | 6.367 | 1 | 4.7752 | 51.75 | 51.75 | 3448180 | 11 | 66631.4976 | 15.0079
239 | 239 | CL1-239 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 28.426 | 29 | 1.094 | 1 | 0.8205 | 6.9 | 6.9 | 2944770 | 7 | 426778.2609 | 2.3431
240 | 240 | CL1-240 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 27.225 | 28 | 15.775 | 1 | 11.8313 | 127.65 | 127.65 | 10122620 | 13 | 79299.8042 | 12.6104
241 | 241 | CL1-241 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.101 | 11 | 2.372 | 1 | 1.779 | 17.25 | 17.25 | 1120760 | 4 | 64971.5942 | 15.3913
242 | 242 | CL1-242 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.846 | 11 | 10.837 | 1 | 8.1277 | 86.25 | 86.25 | 3237370 | 11 | 37534.7246 | 26.642
243 | 243 | CL1-243 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.486 | 6 | 14.814 | 1 | 11.1105 | 120.75 | 120.75 | 2183320 | 11 | 18081.3251 | 55.3057
244 | 244 | CL1-244 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 2.066 | 3 | 2.707 | 1 | 2.0302 | 20.7 | 20.7 | 558600 | 4 | 26985.5072 | 37.0569
245 | 245 | CL1-245 | MAYO | MAYO | SS-317 | Newport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.604 | 9 | 2.832 | 1 | 2.124 | 20.7 | 20.7 | 980220 | 4 | 47353.6232 | 21.1177
246 | 246 | CL1-246 | MAYO | MAYO | SS-317 | Newport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 12.316 | 13 | 9.635 | 1 | 7.2263 | 79.35 | 79.35 | 3658990 | 11 | 46112.0353 | 21.6863
247 | 247 | CL1-247 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 11.611 | 12 | 1.172 | 1 | 0.879 | 6.9 | 6.9 | 2048870 | 7 | 296937.6812 | 3.3677
248 | 248 | CL1-248 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.216 | 6 | 2.556 | 1 | 1.917 | 20.7 | 20.7 | 769410 | 4 | 37169.5652 | 26.9037
249 | 249 | CL1-249 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.999 | 7 | 0.758 | 1 | 0.5685 | 3.45 | 3.45 | 839680 | 4 | 243385.5072 | 4.1087
250 | 250 | CL1-250 | MAYO | MAYO | SS-498 | Belmullet 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.885 | 14 | 0.782 | 1 | 0.5865 | 3.45 | 3.45 | 1597940 | 1 | 463171.0145 | 2.159
251 | 251 | CL1-251 | MAYO | MAYO | SS-498 | Belmullet 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.205 | 9 | 1 | 1 | 0.75 | 6.9 | 6.9 | 1379800 | 2 | 199971.0145 | 5.0007
252 | 252 | CL1-252 | MAYO | MAYO | SS-498 | Belmullet 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.962 | 6 | 0.524 | 1 | 0.524 | 3.45 | 3.45 | 769410 | 4 | 223017.3913 | 4.484
253 | 253 | CL1-253 | MAYO | MAYO | SS-498 | Belmullet 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.933 | 8 | 4.247 | 1 | 3.1852 | 34.5 | 34.5 | 1237870 | 6 | 35880.2899 | 27.8705
254 | 254 | CL1-254 | MAYO | MAYO | SS-498 | Belmullet 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.321 | 10 | 0.648 | 1 | 0.486 | 3.45 | 3.45 | 1387140 | 1 | 402069.5652 | 2.4871
255 | 255 | CL1-255 | MAYO | MAYO | SS-170 | Derrynadivva 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.829 | 4 | 1.46 | 1 | 1.095 | 10.35 | 10.35 | 628870 | 4 | 60760.3865 | 16.4581
256 | 256 | CL1-256 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 20.892 | 21 | 2.12 | 1 | 1.59 | 17.25 | 17.25 | 1823460 | 4 | 105707.8261 | 9.46
257 | 257 | CL1-257 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 19.36 | 20 | 4.433 | 1 | 3.3247 | 34.5 | 34.5 | 2572990 | 6 | 74579.4203 | 13.4085
258 | 258 | CL1-258 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 19.862 | 20 | 4.701 | 1 | 3.5257 | 37.95 | 37.95 | 2572990 | 6 | 67799.473 | 14.7494
259 | 259 | CL1-259 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 18.649 | 19 | 3.594 | 1 | 2.6955 | 27.6 | 27.6 | 2035560 | 5 | 73752.1739 | 13.5589
260 | 260 | CL1-260 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.249 | 6 | 4.087 | 1 | 3.0652 | 31.05 | 31.05 | 1015350 | 6 | 32700.4831 | 30.5806
261 | 261 | CL1-261 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.634 | 8 | 13.508 | 1 | 10.131 | 110.4 | 110.4 | 2604940 | 11 | 23595.471 | 42.381
262 | 262 | CL1-262 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 11.935 | 12 | 1.656 | 1 | 1.242 | 10.35 | 10.35 | 2048870 | 7 | 197958.4541 | 5.0516
263 | 263 | CL1-263 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 12.838 | 13 | 0.609 | 1 | 0.45675 | 3.45 | 3.45 | 2101570 | 7 | 609150.7246 | 1.6416
264 | 264 | CL1-264 | MAYO | MAYO | SS-710 | Tawnaghmore 110kV Substation | EirGrid | 110000 | low | 110000 | 14.993 | 15 | 2.679 | 1 | 2.0092 | 20.7 | 20.7 | 2648760 | 8 | 127959.4203 | 7.815
265 | 265 | CL1-265 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 14.738 | 15 | 2.013 | 1 | 1.5097 | 13.8 | 13.8 | 2648760 | 8 | 191939.1304 | 5.21
266 | 266 | CL1-266 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 18.245 | 19 | 15.594 | 1 | 11.6955 | 127.65 | 127.65 | 7164140 | 13 | 56123.3059 | 17.8179
267 | 267 | CL1-267 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.128 | 11 | 2.296 | 1 | 1.722 | 17.25 | 17.25 | 1120760 | 4 | 64971.5942 | 15.3913
268 | 268 | CL1-268 | MAYO | MAYO | SS-498 | Belmullet 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.132 | 9 | 5.163 | 1 | 3.8723 | 41.4 | 41.4 | 1349130 | 6 | 32587.6812 | 30.6864
269 | 269 | CL1-269 | SLIGO | MAYO | SS-302 | Carrowleagh 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.842 | 3 | 2.725 | 1 | 2.0438 | 20.7 | 20.7 | 558600 | 4 | 26985.5072 | 37.0569
270 | 270 | CL1-270 | SLIGO | SLIGO | SS-075 | Cunghill 110kV Substation | EirGrid | 110000 | 110000 | medium | 8.03 | 9 | 0.97 | 1 | 0.7275 | 6.9 | 6.9 | 1890770 | 7 | 274024.6377 | 3.6493
271 | 271 | CL1-271 | SLIGO | SLIGO | SS-075 | Cunghill 110kV Substation | EirGrid | 110000 | 110000 | medium | 9.282 | 10 | 1.414 | 1 | 1.0605 | 10.35 | 10.35 | 1943470 | 7 | 187774.8792 | 5.3255
272 | 272 | CL1-272 | SLIGO | SLIGO | SS-042 | Ballytivnan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 10.469 | 11 | 0.841 | 1 | 0.63075 | 6.9 | 6.9 | 1485200 | 2 | 215246.3768 | 4.6458
273 | 273 | CL1-273 | SLIGO | LEITRIM | SS-227 | Bundoran 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.815 | 12 | 5.689 | 1 | 4.2668 | 44.85 | 44.85 | 1682910 | 6 | 37523.0769 | 26.6503
274 | 274 | CL1-274 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 9.236 | 10 | 9.968 | 1 | 7.476 | 79.35 | 79.35 | 3026560 | 11 | 38141.903 | 26.2179
275 | 275 | CL1-275 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 10.019 | 11 | 0.8 | 1 | 0.6 | 6.9 | 6.9 | 1485200 | 2 | 215246.3768 | 4.6458
276 | 276 | CL1-276 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.646 | 8 | 2.904 | 1 | 2.178 | 20.7 | 20.7 | 909950 | 4 | 43958.9372 | 22.7485
277 | 277 | CL1-277 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 9.77 | 10 | 4.818 | 1 | 3.6135 | 37.95 | 37.95 | 1460390 | 6 | 38481.9499 | 25.9862
278 | 278 | CL1-278 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.452 | 9 | 0.912 | 1 | 0.684 | 6.9 | 6.9 | 1379800 | 2 | 199971.0145 | 5.0007
279 | 279 | CL1-279 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 11.802 | 12 | 0.67 | 1 | 0.5025 | 3.45 | 3.45 | 1492540 | 1 | 432620.2899 | 2.3115
280 | 280 | CL1-280 | DONEGAL | DONEGAL | SS-090 | Corkermore 38kV Substation | ESB Networks | 38000 | low | 38000 | 8.711 | 9 | 2.276 | 1 | 1.707 | 17.25 | 17.25 | 980220 | 4 | 56824.3478 | 17.5981
281 | 281 | CL1-281 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 12.646 | 13 | 1.967 | 1 | 1.4752 | 13.8 | 13.8 | 1261300 | 4 | 91398.5507 | 10.9411
282 | 282 | CL1-282 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 11.973 | 12 | 11.981 | 1 | 8.9857 | 96.6 | 96.6 | 3448180 | 11 | 35695.4451 | 28.0148
283 | 283 | CL1-283 | DONEGAL | DONEGAL | SS-252 | Killybegs 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 4.503 | 5 | 1.343 | 1 | 1.0072 | 10.35 | 10.35 | 699140 | 4 | 67549.7585 | 14.8039
284 | 284 | CL1-284 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 2.813 | 3 | 1.037 | 1 | 0.77775 | 6.9 | 6.9 | 558600 | 4 | 80956.5217 | 12.3523
285 | 285 | CL1-285 | DONEGAL | DONEGAL | SS-090 | Corkermore 38kV Substation | ESB Networks | 38000 | low | 38000 | 7.324 | 8 | 3.946 | 1 | 2.9595 | 31.05 | 31.05 | 1237870 | 6 | 39866.9887 | 25.0834
286 | 286 | CL1-286 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 5.937 | 6 | 1.646 | 1 | 1.2345 | 10.35 | 10.35 | 769410 | 4 | 74339.1304 | 13.4519
287 | 287 | CL1-287 | DONEGAL | DONEGAL | SS-090 | Corkermore 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.155 | 4 | 1.55 | 1 | 1.1625 | 10.35 | 10.35 | 628870 | 4 | 60760.3865 | 16.4581
288 | 288 | CL1-288 | DONEGAL | DONEGAL | SS-686 | Dungloe 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.46 | 7 | 0.554 | 1 | 0.554 | 3.45 | 3.45 | 839680 | 4 | 243385.5072 | 4.1087
289 | 289 | CL1-289 | DONEGAL | DONEGAL | SS-138 | Creeslough 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.95 | 11 | 0.831 | 1 | 0.62325 | 6.9 | 6.9 | 1485200 | 2 | 215246.3768 | 4.6458
290 | 290 | CL1-290 | DONEGAL | DONEGAL | SS-610 | Milford (North) 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.05 | 11 | 2.185 | 1 | 1.6387 | 17.25 | 17.25 | 1120760 | 4 | 64971.5942 | 15.3913
291 | 291 | CL1-291 | DONEGAL | DONEGAL | SS-119 | Drumlough Hill (1) 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.531 | 3 | 2.733 | 1 | 2.0497 | 20.7 | 20.7 | 558600 | 4 | 26985.5072 | 37.0569
292 | 292 | CL1-292 | DONEGAL | DONEGAL | SS-119 | Drumlough Hill (1) 38kV Substation | ESB Networks | 38000 | low | 38000 | 5.448 | 6 | 5.765 | 1 | 4.3237 | 44.85 | 44.85 | 1015350 | 6 | 22638.796 | 44.172
293 | 293 | CL1-293 | DONEGAL | DONEGAL | SS-272 | Carndonagh 38kV | ESB Networks | 38000 | 38000 | low | 11.922 | 12 | 1.662 | 1 | 1.2465 | 10.35 | 10.35 | 1574950 | 3 | 152169.0821 | 6.5716
294 | 294 | CL1-294 | DONEGAL | DONEGAL | SS-239 | Moville 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.566 | 7 | 5.047 | 1 | 3.7852 | 41.4 | 41.4 | 1126610 | 6 | 27212.8019 | 36.7474
295 | 295 | CL1-295 | DONEGAL | DONEGAL | SS-272 | Carndonagh 38kV | ESB Networks | 38000 | 38000 | low | 4.304 | 5 | 1.5 | 1 | 1.125 | 10.35 | 10.35 | 699140 | 4 | 67549.7585 | 14.8039
296 | 296 | CL1-296 | DONEGAL | DONEGAL | SS-125 | Drumlough Hill (2) 38kV Substation | ESB Networks | 38000 | low | 38000 | 6.28 | 7 | 10.893 | 1 | 8.1698 | 89.7 | 89.7 | 2394130 | 11 | 26690.4125 | 37.4666
297 | 297 | CL1-297 | DONEGAL | DONEGAL | SS-689 |  | ESB Networks | 38000 |  |  | 3.247 | 4 | 6.507 | 1 | 4.8803 | 51.75 | 51.75 | 1761700 | 11 | 34042.5121 | 29.375
298 | 298 | CL1-298 | DONEGAL | DONEGAL | SS-689 |  | ESB Networks | 38000 |  |  | 5.159 | 6 | 0.583 | 1 | 0.583 | 3.45 | 3.45 | 769410 | 4 | 223017.3913 | 4.484
299 | 299 | CL1-299 | DONEGAL | DONEGAL | SS-689 |  | ESB Networks | 38000 |  |  | 2.28 | 3 | 1.624 | 1 | 1.218 | 10.35 | 10.35 | 558600 | 4 | 53971.0145 | 18.5285
300 | 300 | CL1-300 | DONEGAL | DONEGAL | SS-687 | Gweedore Wind Farm 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.454 | 3 | 6.746 | 1 | 5.0595 | 55.2 | 55.2 | 1550890 | 11 | 28095.8333 | 35.5925
301 | 301 | CL1-301 | DONEGAL | DONEGAL | SS-687 | Gweedore Wind Farm 38kV Substation | ESB Networks | 38000 | low | 38000 | 5.054 | 6 | 4.506 | 1 | 3.3795 | 34.5 | 34.5 | 1015350 | 6 | 29430.4348 | 33.9784
302 | 302 | CL1-302 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.459 | 8 | 1.977 | 1 | 1.4828 | 13.8 | 13.8 | 909950 | 4 | 65938.4058 | 15.1657
303 | 303 | CL1-303 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.238 | 7 | 4.423 | 1 | 3.3173 | 34.5 | 34.5 | 1126610 | 6 | 32655.3623 | 30.6228
304 | 304 | CL1-304 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.479 | 8 | 1.943 | 1 | 1.4573 | 13.8 | 13.8 | 909950 | 4 | 65938.4058 | 15.1657
305 | 305 | CL1-305 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.634 | 10 | 1.036 | 1 | 0.777 | 6.9 | 6.9 | 1432500 | 2 | 207608.6957 | 4.8168
306 | 306 | CL1-306 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.101 | 11 | 1.13 | 1 | 0.8475 | 6.9 | 6.9 | 1485200 | 2 | 215246.3768 | 4.6458
307 | 307 | CL1-307 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 13.898 | 14 | 4.42 | 1 | 3.315 | 34.5 | 34.5 | 1905430 | 6 | 55229.8551 | 18.1061
308 | 308 | CL1-308 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 18.984 | 19 | 14.303 | 1 | 10.7273 | 117.3 | 117.3 | 4923850 | 11 | 41976.5558 | 23.8228
309 | 309 | CL1-309 | DONEGAL | DONEGAL | SS-686 | Dungloe 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.432 | 14 | 3.26 | 1 | 2.445 | 24.15 | 24.15 | 1591410 | 5 | 65896.8944 | 15.1752
311 | 311 | CL1-311 | WEXFORD | WEXFORD | SS-481 | Castledockrell 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 7.589 | 8 | 2.162 | 1 | 1.6215 | 17.25 | 17.25 | 2156870 | 8 | 125035.942 | 7.9977
312 | 312 | CL1-312 | CARLOW | CARLOW | SS-481 | Castledockrell 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 11.318 | 12 | 1.034 | 1 | 0.7755 | 6.9 | 6.9 | 2048870 | 7 | 296937.6812 | 3.3677
313 | 313 | CL1-313 | WICKLOW | WICKLOW | SS-062 | Stratford 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 7.135 | 8 | 1.989 | 1 | 1.4918 | 13.8 | 13.8 | 2156870 | 8 | 156294.9275 | 6.3982
314 | 314 | CL1-314 | WICKLOW | WICKLOW | SS-222 | Poulaphouca 110kV Substation | EirGrid | 110000 | low | 110000 | 7.433 | 8 | 1.038 | 1 | 0.7785 | 6.9 | 6.9 | 1838070 | 7 | 266386.9565 | 3.7539
315 | 315 | CL1-315 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.011 | 10 | 0.807 | 1 | 0.60525 | 6.9 | 6.9 | 1432500 | 2 | 207608.6957 | 4.8168
316 | 316 | CL1-316 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.015 | 8 | 0.346 | 1 | 0.346 | 3.45 | 3.45 | 909950 | 4 | 263753.6232 | 3.7914
317 | 317 | CL1-317 | WICKLOW | WICKLOW | SS-062 | Stratford 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 7.293 | 8 | 2.401 | 1 | 1.8007 | 17.25 | 17.25 | 2156870 | 8 | 125035.942 | 7.9977
318 | 318 | CL1-318 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.852 | 9 | 6.064 | 1 | 4.548 | 48.3 | 48.3 | 2815750 | 11 | 58297.1014 | 17.1535
319 | 319 | CL1-319 | WICKLOW | WICKLOW | SS-699 | Ballycumber 38kV Substation | ESB Networks | 38000 | low | 38000 | 12.249 | 13 | 1.659 | 1 | 1.2443 | 10.35 | 10.35 | 1627650 | 3 | 157260.8696 | 6.3589
320 | 320 | CL1-320 | WICKLOW | WICKLOW | SS-222 | Poulaphouca 110kV Substation | EirGrid | 110000 | low | 110000 | 14.393 | 15 | 0.194 | 1 | 0.194 | 3.45 | 3.45 | 2206970 | 7 | 639701.4493 | 1.5632
321 | 321 | CL1-321 | WICKLOW | WICKLOW | SS-209 | Blessington 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.332 | 11 | 0.422 | 1 | 0.422 | 3.45 | 3.45 | 1439840 | 1 | 417344.9275 | 2.3961
322 | 322 | CL1-322 | WICKLOW | WICKLOW | SS-570 | Kilcoole 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.819 | 12 | 0.672 | 1 | 0.504 | 3.45 | 3.45 | 1492540 | 1 | 432620.2899 | 2.3115
323 | 323 | CL1-323 | WICKLOW | WICKLOW | SS-570 | Kilcoole 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.044 | 14 | 0.584 | 1 | 0.584 | 3.45 | 3.45 | 1597940 | 1 | 463171.0145 | 2.159
324 | 324 | CL1-324 | WEXFORD | WICKLOW | SS-616 | Ballinvally 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 2.575 | 3 | 1.018 | 1 | 0.7635 | 6.9 | 6.9 | 558600 | 4 | 80956.5217 | 12.3523
325 | 325 | CL1-325 | CORK | KERRY | SS-668 | Coomataggart 110 kV Substation | EirGrid | 110000 | low | 110000 | 4.598 | 5 | 8.841 | 1 | 6.6307 | 72.45 | 72.45 | 1972510 | 11 | 27225.8109 | 36.7299
326 | 326 | CL1-326 | CORK | KERRY | SS-668 | Coomataggart 110 kV Substation | EirGrid | 110000 | low | 110000 | 1.293 | 2 | 1.653 | 1 | 1.2397 | 10.35 | 10.35 | 1340080 | 11 | 129476.3285 | 7.7234
327 | 327 | CL1-327 | CORK | CORK | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 6.498 | 7 | 1.688 | 1 | 1.266 | 13.8 | 13.8 | 839680 | 4 | 60846.3768 | 16.4348
328 | 328 | CL1-328 | CORK | KERRY | SS-668 | Coomataggart 110 kV Substation | EirGrid | 110000 | low | 110000 | 3.847 | 4 | 0.928 | 1 | 0.696 | 6.9 | 6.9 | 1627270 | 7 | 235836.2319 | 4.2402
329 | 329 | CL1-329 | CORK | KERRY | SS-162 | Garrow 110kV Substation | EirGrid | 110000 | 38000 | 110000 | 1.679 | 2 | 0.778 | 1 | 0.5835 | 3.45 | 3.45 | 1340080 | 11 | 388428.9855 | 2.5745
330 | 330 | CL1-330 | KERRY | KERRY | SS-072 | Clonkeen 110kV Substation | EirGrid | 110000 |  |  | 3.747 | 4 | 2.918 | 1 | 2.1885 | 20.7 | 20.7 | 1875790 | 8 | 90617.8744 | 11.0354
331 | 331 | CL1-331 | KERRY | KERRY | SS-072 | Clonkeen 110kV Substation | EirGrid | 110000 |  |  | 6.185 | 7 | 1.525 | 1 | 1.1437 | 10.35 | 10.35 | 1785370 | 7 | 172499.5169 | 5.7971
332 | 332 | CL1-332 | CORK | KERRY | SS-161 | Gneeves 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.021 | 5 | 6.163 | 1 | 4.6223 | 48.3 | 48.3 | 1972510 | 11 | 40838.7164 | 24.4866
333 | 333 | CL1-333 | CORK | CORK | SS-615 | Knockduff 110kv Substation | EirGrid | 110000 |  |  | 5.262 | 6 | 1.717 | 1 | 1.2877 | 13.8 | 13.8 | 2016330 | 8 | 146110.8696 | 6.8441
334 | 334 | CL1-334 | DONEGAL | DONEGAL | SS-686 | Dungloe 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.824 | 5 | 0.787 | 1 | 0.59025 | 3.45 | 3.45 | 699140 | 4 | 202649.2754 | 4.9346
335 | 335 | CL1-335 | DONEGAL | DONEGAL | SS-333 | Clady 38kV Substation | ESB Networks | 38000 |  |  | 4.422 | 5 | 1.552 | 1 | 1.164 | 10.35 | 10.35 | 699140 | 4 | 67549.7585 | 14.8039
336 | 336 | CL1-336 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.097 | 9 | 2.353 | 1 | 1.7648 | 17.25 | 17.25 | 2227140 | 8 | 129109.5652 | 7.7454
337 | 337 | CL1-337 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 4.966 | 5 | 5.023 | 1 | 3.7672 | 41.4 | 41.4 | 2510150 | 10 | 60631.6425 | 16.493
338 | 338 | CL1-338 | LEITRIM | LEITRIM | SS-227 | Bundoran 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.889 | 9 | 1.9 | 1 | 1.425 | 13.8 | 13.8 | 980220 | 4 | 71030.4348 | 14.0785
339 | 339 | CL1-339 | LEITRIM | LEITRIM | SS-227 | Bundoran 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.917 | 9 | 8.488 | 1 | 6.366 | 69 | 69 | 2815750 | 11 | 40807.971 | 24.505
340 | 340 | CL1-340 | LEITRIM | LEITRIM | SS-227 | Bundoran 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.87 | 9 | 2.771 | 1 | 2.0782 | 20.7 | 20.7 | 980220 | 4 | 47353.6232 | 21.1177
341 | 341 | CL1-341 | LEITRIM | LEITRIM | SS-304 | Arigna 110kV Substation | EirGrid | 110000 | 110000 | 20000 | 6.203 | 7 | 2.189 | 1 | 1.6418 | 17.25 | 17.25 | 2086600 | 8 | 120962.3188 | 8.267
342 | 342 | CL1-342 | LEITRIM | LEITRIM | SS-304 | Arigna 110kV Substation | EirGrid | 110000 | 110000 | 20000 | 7.547 | 8 | 1.88 | 1 | 1.41 | 13.8 | 13.8 | 2156870 | 8 | 156294.9275 | 6.3982
343 | 343 | CL1-343 | CAVAN | LEITRIM | SS-304 | Arigna 110kV Substation | EirGrid | 110000 | 110000 | 20000 | 12.263 | 13 | 2.756 | 1 | 2.067 | 20.7 | 20.7 | 2508220 | 8 | 121170.0483 | 8.2529
344 | 344 | CL1-344 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.699 | 7 | 1.083 | 1 | 0.81225 | 6.9 | 6.9 | 839680 | 4 | 121692.7536 | 8.2174
345 | 345 | CL1-345 | SLIGO | MAYO | SS-078 | Glenree 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 3.298 | 4 | 5.047 | 1 | 3.7852 | 41.4 | 41.4 | 2398890 | 10 | 57944.2029 | 17.258
346 | 346 | CL1-346 | MAYO | MAYO | SS-170 | Derrynadivva 38kV Substation | ESB Networks | 38000 | low | 38000 | 8.009 | 9 | 1.369 | 1 | 1.0268 | 10.35 | 10.35 | 1416850 | 3 | 136893.7198 | 7.3049
347 | 347 | CL1-347 | MAYO | MAYO | SS-234 | Crossmolina 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.18 | 12 | 5.554 | 1 | 4.1655 | 44.85 | 44.85 | 1682910 | 6 | 37523.0769 | 26.6503
348 | 348 | CL1-348 | DONEGAL | DONEGAL | SS-102 | Binbane 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 2.585 | 3 | 2.703 | 1 | 2.0272 | 20.7 | 20.7 | 1550890 | 11 | 74922.2222 | 13.3472
349 | 349 | CL1-349 | DONEGAL | DONEGAL | SS-688 | Clogher 110kV Substation | EirGrid | 110000 |  |  | 6.776 | 7 | 3.551 | 1 | 2.6633 | 27.6 | 27.6 | 2575660 | 9 | 93321.0145 | 10.7157
350 | 350 | CL1-350 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.61 | 9 | 0.601 | 1 | 0.45075 | 3.45 | 3.45 | 1890770 | 7 | 548049.2754 | 1.8247
351 | 351 | CL1-351 | DONEGAL | DONEGAL | SS-688 | Clogher 110kV Substation | EirGrid | 110000 |  |  | 10.138 | 11 | 14.991 | 1 | 11.2432 | 120.75 | 120.75 | 3237370 | 11 | 26810.5176 | 37.2988
352 | 352 | CL1-352 | DONEGAL | DONEGAL | SS-196 | Culliagh 110kV Substation | EirGrid | 110000 | low | 110000 | 11.387 | 12 | 1.79 | 1 | 1.3425 | 13.8 | 13.8 | 2437950 | 8 | 176663.0435 | 5.6605
353 | 353 | CL1-353 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 9.466 | 10 | 2.878 | 1 | 2.1585 | 20.7 | 20.7 | 2297410 | 8 | 110985.9903 | 9.0101
354 | 354 | CL1-354 | DONEGAL | DONEGAL | SS-196 | Culliagh 110kV Substation | EirGrid | 110000 | low | 110000 | 10.717 | 11 | 1.836 | 1 | 1.377 | 13.8 | 13.8 | 2367680 | 8 | 171571.0145 | 5.8285
355 | 355 | CL1-355 | DONEGAL | DONEGAL | SS-196 | Culliagh 110kV Substation | EirGrid | 110000 | low | 110000 | 8.105 | 9 | 0.547 | 1 | 0.547 | 3.45 | 3.45 | 1890770 | 7 | 548049.2754 | 1.8247
356 | 356 | CL1-356 | GALWAY | GALWAY | SS-623 | Uggool 110kV Substation | EirGrid | 110000 | 33000 | 110000 | 9.236 | 10 | 2.297 | 1 | 1.7228 | 17.25 | 17.25 | 2297410 | 8 | 133183.1884 | 7.5085
357 | 357 | CL1-357 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 7.172 | 8 | 4.848 | 1 | 3.636 | 37.95 | 37.95 | 2843930 | 10 | 74938.8669 | 13.3442
358 | 358 | CL1-358 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 4.082 | 5 | 1.768 | 1 | 1.326 | 13.8 | 13.8 | 1946060 | 8 | 141018.8406 | 7.0913
359 | 359 | CL1-359 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 6.15 | 7 | 1.289 | 1 | 0.96675 | 10.35 | 10.35 | 1785370 | 7 | 172499.5169 | 5.7971
360 | 360 | CL1-360 | KERRY | KERRY | SS-636 | Garranebane 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.635 | 6 | 1.725 | 1 | 1.2938 | 13.8 | 13.8 | 769410 | 4 | 55754.3478 | 17.9358
361 | 361 | CL1-361 | CORK | CORK | SS-192 | Ballylickey 110kV Station | EirGrid | 110000 | 110000 | 38000 | 7.786 | 8 | 1.241 | 1 | 0.93075 | 6.9 | 6.9 | 1838070 | 7 | 266386.9565 | 3.7539
362 | 362 | CL1-362 | TIPPERARY | WATERFORD | SS-455 | Ardfinnan 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.503 | 10 | 1.994 | 1 | 1.4955 | 13.8 | 13.8 | 1050490 | 4 | 76122.4638 | 13.1367
363 | 363 | CL1-363 | TIPPERARY | WATERFORD | SS-455 | Ardfinnan 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.598 | 9 | 2.784 | 1 | 2.088 | 20.7 | 20.7 | 980220 | 4 | 47353.6232 | 21.1177
364 | 364 | CL1-364 | TIPPERARY | WATERFORD | SS-455 | Ardfinnan 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.11 | 10 | 0.688 | 1 | 0.516 | 3.45 | 3.45 | 1387140 | 1 | 402069.5652 | 2.4871
365 | 365 | CL1-365 | TIPPERARY | TIPPERARY | SS-622 | Barranafaddock 38kV Substation | ESB Networks | 38000 | low | 38000 | 10.261 | 11 | 1.054 | 1 | 0.7905 | 6.9 | 6.9 | 1485200 | 2 | 215246.3768 | 4.6458
366 | 366 | CL1-366 | WATERFORD | WATERFORD | SS-505 | Kilmacthomas 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.166 | 13 | 23.269 | 1 | 17.4517 | 189.75 | 189.75 | 10383640 | 13 | 54722.7404 | 18.2739
367 | 367 | CL1-367 | LIMERICK | LIMERICK | SS-695 | Castlepook 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 3.561 | 4 | 1.56 | 1 | 1.17 | 10.35 | 10.35 | 628870 | 4 | 60760.3865 | 16.4581
368 | 368 | CL1-368 | LIMERICK | LIMERICK | SS-257 | Kilshanny 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.142 | 9 | 1.717 | 1 | 1.2877 | 13.8 | 13.8 | 980220 | 4 | 71030.4348 | 14.0785
369 | 369 | CL1-369 | TIPPERARY | LIMERICK | SS-585 | Kilross Road 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.095 | 12 | 11.912 | 1 | 8.934 | 96.6 | 96.6 | 3448180 | 11 | 35695.4451 | 28.0148
370 | 370 | CL1-370 | CARLOW | WEXFORD | SS-492 | Graigue 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.064 | 12 | 3.091 | 1 | 2.3182 | 24.15 | 24.15 | 1413750 | 5 | 58540.3727 | 17.0822
371 | 371 | CL1-371 | TIPPERARY | TIPPERARY | SS-064 | Ballydine 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.022 | 9 | 2.632 | 1 | 1.974 | 20.7 | 20.7 | 2227140 | 8 | 107591.3043 | 9.2944
372 | 372 | CL1-372 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 17.982 | 18 | 5.172 | 1 | 3.879 | 41.4 | 41.4 | 2350470 | 6 | 56774.6377 | 17.6135
373 | 373 | CL1-373 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 18.012 | 19 | 1.064 | 1 | 0.798 | 6.9 | 6.9 | 1906800 | 2 | 276347.8261 | 3.6186
374 | 374 | CL1-374 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.349 | 8 | 1.487 | 1 | 1.1153 | 10.35 | 10.35 | 909950 | 4 | 87917.8744 | 11.3743
375 | 375 | CL1-375 | CORK | CORK | SS-261 | Milane Hill 38kV Station | ESB Networks | 38000 |  |  | 6.673 | 7 | 0.822 | 1 | 0.6165 | 6.9 | 6.9 | 839680 | 4 | 121692.7536 | 8.2174
376 | 376 | CL1-376 | GALWAY | CLARE | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.593 | 13 | 1.678 | 1 | 1.2585 | 13.8 | 13.8 | 1261300 | 4 | 91398.5507 | 10.9411
377 | 377 | CL1-377 | GALWAY | CLARE | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.301 | 15 | 0.791 | 1 | 0.59325 | 3.45 | 3.45 | 1650640 | 1 | 478446.3768 | 2.0901
378 | 378 | CL1-378 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 12.594 | 13 | 1.657 | 1 | 1.2428 | 10.35 | 10.35 | 1627650 | 3 | 157260.8696 | 6.3589
379 | 379 | CL1-379 | CLARE | CLARE | SS-503 | Scariff 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.445 | 9 | 1.098 | 1 | 0.8235 | 6.9 | 6.9 | 1379800 | 2 | 199971.0145 | 5.0007
380 | 380 | CL1-380 | WICKLOW | WICKLOW | SS-699 | Ballycumber 38kV Substation | ESB Networks | 38000 | low | 38000 | 6.186 | 7 | 1.285 | 1 | 0.96375 | 10.35 | 10.35 | 839680 | 4 | 81128.5024 | 12.3261
381 | 381 | CL1-381 | DONEGAL | DONEGAL | SS-610 | Milford (North) 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.001 | 7 | 4.038 | 1 | 3.0285 | 31.05 | 31.05 | 1126610 | 6 | 36283.7359 | 27.5606
382 | 382 | CL1-382 | GALWAY | GALWAY | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 10.631 | 11 | 1.42 | 1 | 1.065 | 10.35 | 10.35 | 1522250 | 3 | 147077.2947 | 6.7991
383 | 383 | CL1-383 | MAYO | MAYO | SS-710 | Tawnaghmore 110kV Substation | EirGrid | 110000 | low | 110000 | 11.377 | 12 | 0.716 | 1 | 0.537 | 3.45 | 3.45 | 2048870 | 7 | 593875.3623 | 1.6839
384 | 384 | CL1-384 | MAYO | MAYO | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 12.936 | 13 | 0.665 | 1 | 0.49875 | 3.45 | 3.45 | 1545240 | 1 | 447895.6522 | 2.2327
385 | 385 | CL1-385 | DONEGAL | DONEGAL | SS-117 | Crockahenny 38kV Substation | ESB Networks | 38000 | low | 38000 | 5.462 | 6 | 0.804 | 1 | 0.603 | 6.9 | 6.9 | 769410 | 4 | 111508.6957 | 8.9679
386 | 386 | CL1-386 | MAYO | MAYO | SS-498 | Belmullet 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.255 | 14 | 1.149 | 1 | 0.86175 | 6.9 | 6.9 | 1643300 | 2 | 238159.4203 | 4.1989
387 | 387 | CL2-001 | DONEGAL | DONEGAL | SS-118 | Sorne Hill 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 1.519 | 2 | 0.136 | 2 | 0.136 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341
388 | 388 | CL2-002 | DONEGAL | DONEGAL | SS-688 | Clogher 110kV Substation | EirGrid | 110000 |  |  | 2.046 | 3 | 0.292 | 2 | 0.292 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674
389 | 389 | CL2-003 | DONEGAL | DONEGAL | SS-643 | Donegal 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.945 | 5 | 0.288 | 2 | 0.288 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
390 | 390 | CL2-004 | WEXFORD | WEXFORD | SS-237 | Carnsore 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 2.07 | 3 | 0.091 | 2 | 0.091 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
391 | 391 | CL2-005 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.145 | 7 | 0.094 | 2 | 0.094 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
392 | 392 | CL2-006 | CLARE | CLARE | SS-595 | Kilkee 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.668 | 6 | 0.09 | 2 | 0.09 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
393 | 393 | CL2-007 | CLARE | CLARE | SS-595 | Kilkee 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.385 | 6 | 0.192 | 2 | 0.192 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
394 | 394 | CL2-008 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 3.407 | 4 | 0.143 | 2 | 0.143 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581
395 | 395 | CL2-009 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 12.305 | 13 | 0.114 | 2 | 0.114 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718
396 | 396 | CL2-010 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.624 | 7 | 0.09 | 2 | 0.09 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
397 | 397 | CL2-011 | MAYO | MAYO | SS-170 | Derrynadivva 38kV Substation | ESB Networks | 38000 | low | 38000 | 7.282 | 8 | 0.144 | 2 | 0.144 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
398 | 398 | CL2-012 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 17.352 | 18 | 0.096 | 2 | 0.096 | 4.2 | 4.2 | 1808740 | 1 | 430652.381 | 2.3221
399 | 399 | CL2-013 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 21.42 | 22 | 0.099 | 2 | 0.099 | 4.2 | 4.2 | 2575870 | 7 | 613302.381 | 1.6305
400 | 400 | CL2-014 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.424 | 8 | 0.094 | 2 | 0.094 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
401 | 401 | CL2-015 | SLIGO | SLIGO | SS-075 | Cunghill 110kV Substation | EirGrid | 110000 | 110000 | medium | 8.315 | 9 | 0.101 | 2 | 0.101 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213
402 | 402 | CL2-016 | SLIGO | SLIGO | SS-042 | Ballytivnan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 9.487 | 10 | 0.165 | 2 | 0.165 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
403 | 403 | CL2-017 | DONEGAL | DONEGAL | SS-670 | Acres 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 6.088 | 7 | 0.144 | 2 | 0.144 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
404 | 404 | CL2-018 | DONEGAL | DONEGAL | SS-697 | Clogheravaddy 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.188 | 2 | 0.169 | 2 | 0.169 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007
405 | 405 | CL2-019 | DONEGAL | DONEGAL | SS-252 | Killybegs 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 4.884 | 5 | 0.094 | 2 | 0.094 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
406 | 406 | CL2-020 | DONEGAL | DONEGAL | SS-125 | Drumlough Hill (2) 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.634 | 5 | 0.129 | 2 | 0.129 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
407 | 407 | CL2-021 | DONEGAL | DONEGAL | SS-689 |  | ESB Networks | 38000 |  |  | 5.587 | 6 | 0.12 | 2 | 0.12 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
408 | 408 | CL2-022 | DONEGAL | DONEGAL | SS-686 | Dungloe 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.287 | 4 | 0.336 | 2 | 0.336 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
409 | 409 | CL2-023 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 4.945 | 5 | 0.105 | 2 | 0.105 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5
410 | 410 | CL2-024 | MAYO | MAYO | SS-702 |  | ESB Networks | 38000 | low | 38000 | 1.455 | 2 | 0.101 | 2 | 0.101 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007
411 | 411 | CL2-025 | CARLOW | CARLOW | SS-494 | Bunclody 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.386 | 7 | 0.099 | 2 | 0.099 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
412 | 412 | CL2-026 | WICKLOW | WICKLOW | SS-222 | Poulaphouca 110kV Substation | EirGrid | 110000 | low | 110000 | 10.122 | 11 | 0.094 | 2 | 0.094 | 4.2 | 4.2 | 1996170 | 7 | 475278.5714 | 2.104
413 | 413 | CL2-027 | WICKLOW | WICKLOW | SS-222 | Poulaphouca 110kV Substation | EirGrid | 110000 | low | 110000 | 10.942 | 11 | 0.132 | 2 | 0.132 | 4.2 | 4.2 | 1996170 | 7 | 475278.5714 | 2.104
414 | 414 | CL2-028 | WICKLOW | WICKLOW | SS-222 | Poulaphouca 110kV Substation | EirGrid | 110000 | low | 110000 | 8.578 | 9 | 0.145 | 2 | 0.145 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213
415 | 415 | CL2-029 | DUBLIN | DUBLIN | SS-018 | Old Bawn 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.02 | 8 | 0.272 | 2 | 0.272 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
416 | 416 | CL2-030 | WICKLOW | WICKLOW | SS-010 | Fassaroe 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 7.03 | 8 | 0.156 | 2 | 0.156 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285
417 | 417 | CL2-031 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.978 | 3 | 0.152 | 2 | 0.152 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
418 | 418 | CL2-032 | CORK | CORK | SS-070 | Glanlee 110kV Substation | EirGrid | 110000 | low | 110000 | 1.568 | 2 | 0.247 | 2 | 0.247 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341
419 | 419 | CL2-033 | CORK | CORK | SS-162 | Garrow 110kV Substation | EirGrid | 110000 | 38000 | 110000 | 3.66 | 4 | 0.137 | 2 | 0.137 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581
420 | 420 | CL2-034 | CORK | CORK | SS-161 | Gneeves 38kV Substation | ESB Networks | 38000 | low | 38000 | 5.787 | 6 | 0.091 | 2 | 0.091 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
421 | 421 | CL2-035 | CORK | CORK | SS-096 | Boggeragh 110kV Substation | EirGrid | 110000 |  |  | 3.731 | 4 | 0.136 | 2 | 0.136 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581
422 | 422 | CL2-036 | LIMERICK | LIMERICK | SS-378 | Foynes 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.661 | 5 | 0.178 | 2 | 0.178 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
423 | 423 | CL2-037 | DONEGAL | DONEGAL | SS-090 | Corkermore 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.324 | 2 | 0.127 | 2 | 0.127 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007
424 | 424 | CL2-038 | ROSCOMMON | ROSCOMMON | SS-384 | Largan Hill 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.345 | 2 | 0.108 | 2 | 0.108 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007
425 | 425 | CL2-039 | DONEGAL | DONEGAL | SS-196 | Culliagh 110kV Substation | EirGrid | 110000 | low | 110000 | 2.274 | 3 | 0.189 | 2 | 0.189 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674
426 | 426 | CL2-040 | DONEGAL | DONEGAL | SS-196 | Culliagh 110kV Substation | EirGrid | 110000 | low | 110000 | 9.903 | 10 | 0.224 | 2 | 0.224 | 4.2 | 4.2 | 1943470 | 7 | 462730.9524 | 2.1611
427 | 427 | CL2-041 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 8.467 | 9 | 0.166 | 2 | 0.166 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213
428 | 428 | CL2-042 | DONEGAL | DONEGAL | SS-690 | Stranrolar 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.52 | 4 | 0.17 | 2 | 0.17 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
429 | 429 | CL2-043 | KERRY | KERRY | SS-636 | Garranebane 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.126 | 8 | 0.224 | 2 | 0.224 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
430 | 430 | CL2-044 | TIPPERARY | TIPPERARY | SS-347 | Glengoole 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.444 | 9 | 0.104 | 2 | 0.104 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
431 | 431 | CL2-045 | WEXFORD | WEXFORD | SS-251 | Ballybrennan 38kV Substation | ESB Networks | 38000 | 38000 | low | 1.758 | 2 | 0.195 | 2 | 0.195 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007
432 | 432 | CL2-046 | KILKENNY | KILKENNY | SS-372 | Ballyconra 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.024 | 13 | 0.197 | 2 | 0.197 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718
433 | 433 | CL2-047 | TIPPERARY | TIPPERARY | SS-645 | Toomevara 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.541 | 8 | 0.138 | 2 | 0.138 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
434 | 434 | CL2-048 | GALWAY | GALWAY | SS-131 | Ros a Mh├¡l 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.764 | 11 | 0.332 | 2 | 0.332 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
435 | 435 | CL2-049 | TIPPERARY | TIPPERARY | SS-660 | Nenagh 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.321 | 10 | 0.12 | 2 | 0.12 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
436 | 436 | CL2-050 | TIPPERARY | TIPPERARY | SS-397 | Glenough 38kV Substation | ESB Networks | 38000 | low | 38000 | 5.796 | 6 | 0.218 | 2 | 0.218 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
437 | 437 | CL2-051 | OFFALY | OFFALY | SS-537 | Monaincha 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 8.055 | 9 | 0.206 | 2 | 0.206 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
438 | 438 | CL2-052 | WICKLOW | WICKLOW | SS-209 | Blessington 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.753 | 7 | 0.128 | 2 | 0.128 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
439 | 439 | CL2-053 | WICKLOW | WICKLOW | SS-222 | Poulaphouca 110kV Substation | EirGrid | 110000 | low | 110000 | 7.819 | 8 | 0.112 | 2 | 0.112 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285
440 | 440 | CL2-054 | GALWAY | GALWAY | SS-057 | Galway 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.136 | 6 | 0.29 | 2 | 0.29 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424
441 | 441 | CL2-055 | GALWAY | GALWAY | SS-038 | Salthill 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 6.375 | 7 | 0.21 | 2 | 0.21 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525
442 | 442 | CL2-056 | CORK | CORK | SS-562 | Bantry 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.792 | 7 | 0.163 | 2 | 0.163 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
443 | 443 | CL2-057 | GALWAY | GALWAY | SS-131 | Ros a Mh├¡l 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.18 | 3 | 0.255 | 2 | 0.255 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
444 | 444 | CL2-058 | CORK | CORK | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 6.514 | 7 | 0.166 | 2 | 0.166 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
445 | 445 | CL2-059 | GALWAY | GALWAY | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 5.907 | 6 | 0.109 | 2 | 0.109 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
446 | 446 | CL2-060 | GALWAY | GALWAY | SS-638 | Oughterard 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 4.42 | 5 | 0.131 | 2 | 0.131 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
447 | 447 | CL2-061 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.053 | 11 | 0.112 | 2 | 0.112 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
448 | 448 | CL2-062 | CLARE | CLARE | SS-595 | Kilkee 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.87 | 5 | 0.127 | 2 | 0.127 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
449 | 449 | CL2-063 | WATERFORD | WATERFORD | SS-607 | Curraglass 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.549 | 9 | 0.282 | 2 | 0.282 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
450 | 450 | CL2-064 | LIMERICK | LIMERICK | SS-596 | Cappamore 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.113 | 7 | 0.097 | 2 | 0.097 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
451 | 451 | CL2-065 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 2.567 | 3 | 0.208 | 2 | 0.208 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674
452 | 452 | CL2-066 | CORK | CORK | SS-607 | Curraglass 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.605 | 9 | 0.094 | 2 | 0.094 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
453 | 453 | CL2-067 | CORK | CORK | SS-536 | Knockacummer 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 4.482 | 5 | 0.099 | 2 | 0.099 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5
454 | 454 | CL2-068 | WICKLOW | WICKLOW | SS-616 | Ballinvally 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 9.164 | 10 | 0.111 | 2 | 0.111 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
455 | 455 | CL2-069 | GALWAY | GALWAY | SS-646 | Oranmore 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.744 | 5 | 0.108 | 2 | 0.108 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
456 | 456 | CL2-070 | WEXFORD | WEXFORD | SS-033 | Ballywater 110kV Substation | EirGrid | 110000 | low | 110000 | 7.574 | 8 | 0.317 | 2 | 0.317 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285
457 | 457 | CL2-071 | TIPPERARY | TIPPERARY | SS-535 | Garracummer 38kV Substation | ESB Networks | 38000 | low | 38000 | 7.443 | 8 | 0.294 | 2 | 0.294 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
458 | 458 | CL2-072 | KERRY | LIMERICK | SS-703 |  | EirGrid | 110000 | low | 110000 | 7.224 | 8 | 0.111 | 2 | 0.111 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285
459 | 459 | CL2-073 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 7.822 | 8 | 0.114 | 2 | 0.114 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285
460 | 460 | CL2-074 | GALWAY | GALWAY | SS-131 | Ros a Mh├¡l 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.176 | 6 | 0.115 | 2 | 0.115 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
461 | 461 | CL2-075 | CORK | CORK | SS-263 | Lake 38kV Station | ESB Networks | 38000 | 38000 | low | 4.225 | 5 | 0.383 | 2 | 0.383 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
462 | 462 | CL2-076 | KERRY | KERRY | SS-189 | Knockearagh 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 6.526 | 7 | 0.113 | 2 | 0.113 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525
463 | 463 | CL2-077 | WATERFORD | WATERFORD | SS-532 | Woodhouse 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 5.986 | 6 | 0.285 | 2 | 0.285 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424
464 | 464 | CL2-078 | MAYO | MAYO | SS-203 | Foxford 38kV Substation | ESB Networks | 38000 |  |  | 6.169 | 7 | 0.196 | 2 | 0.196 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
465 | 465 | CL2-079 | MAYO | MAYO | SS-640 | Ballinrobe 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.835 | 7 | 0.108 | 2 | 0.108 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
466 | 466 | CL2-080 | MAYO | MAYO | SS-431 | Knockaphunta 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.056 | 12 | 0.166 | 2 | 0.166 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
467 | 467 | CL2-081 | SLIGO | SLIGO | SS-095 | Collooney 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 6.099 | 7 | 0.137 | 2 | 0.137 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
468 | 468 | CL2-082 | SLIGO | SLIGO | SS-095 | Collooney 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 3.086 | 4 | 0.157 | 2 | 0.157 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
469 | 469 | CL2-083 | SLIGO | MAYO | SS-201 | Swinford 38kV Station | ESB Networks | 38000 | 38000 | low | 8.724 | 9 | 0.28 | 2 | 0.28 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
470 | 470 | CL2-084 | MAYO | MAYO | SS-170 | Derrynadivva 38kV Substation | ESB Networks | 38000 | low | 38000 | 11.466 | 12 | 0.13 | 2 | 0.13 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
471 | 471 | CL2-085 | GALWAY | GALWAY | SS-598 | Glennamaddy 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.604 | 7 | 0.214 | 2 | 0.214 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
472 | 472 | CL2-086 | GALWAY | GALWAY | SS-598 | Glennamaddy 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.383 | 8 | 0.103 | 2 | 0.103 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
473 | 473 | CL2-087 | GALWAY | GALWAY | SS-598 | Glennamaddy 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.079 | 8 | 0.124 | 2 | 0.124 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
474 | 474 | CL2-088 | MAYO | MAYO | SS-234 | Crossmolina 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.983 | 6 | 0.208 | 2 | 0.208 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
475 | 475 | CL2-089 | LOUTH | LOUTH | SS-650 | Ballymascanlan 38kV Substation | ESB Networks | 38000 | 38000 | low | 1.639 | 2 | 0.222 | 2 | 0.222 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007
476 | 476 | CL2-090 | GALWAY | GALWAY | SS-549 | Tuam North 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.713 | 7 | 0.343 | 2 | 0.343 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
477 | 477 | CL2-091 | MAYO | MAYO | SS-639 | Tonroe 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.212 | 9 | 0.385 | 2 | 0.385 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
478 | 478 | CL2-092 | MAYO | MAYO | SS-640 | Ballinrobe 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.744 | 7 | 0.211 | 2 | 0.211 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
479 | 479 | CL2-093 | MAYO | MAYO | SS-640 | Ballinrobe 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.292 | 8 | 0.274 | 2 | 0.274 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
480 | 480 | CL2-094 | DONEGAL | DONEGAL | SS-272 | Carndonagh 38kV | ESB Networks | 38000 | 38000 | low | 6.06 | 7 | 0.134 | 2 | 0.134 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
481 | 481 | CL2-095 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.372 | 10 | 0.128 | 2 | 0.128 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
482 | 482 | CL2-096 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 12.004 | 13 | 0.103 | 2 | 0.103 | 4.2 | 4.2 | 2101570 | 7 | 500373.8095 | 1.9985
483 | 483 | CL2-097 | SLIGO | SLIGO | SS-302 | Carrowleagh 38kV Substation | ESB Networks | 38000 | low | 38000 | 8.565 | 9 | 0.113 | 2 | 0.113 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
484 | 484 | CL2-098 | MAYO | MAYO | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 5.78 | 6 | 0.109 | 2 | 0.109 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
485 | 485 | CL2-099 | DONEGAL | DONEGAL | SS-083 | Golagh 110kV Substation | EirGrid | 110000 | 38000 | 110000 | 1.279 | 2 | 0.329 | 2 | 0.329 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341
486 | 486 | CL2-100 | MAYO | MAYO | SS-170 | Derrynadivva 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.818 | 2 | 0.301 | 2 | 0.301 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007
487 | 487 | CL2-101 | GALWAY | GALWAY | SS-109 | Cloon 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 9.631 | 10 | 0.517 | 2 | 0.517 | 4.2 | 4.2 | 1943470 | 7 | 462730.9524 | 2.1611
488 | 488 | CL2-102 | CORK | CORK | SS-161 | Gneeves 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.338 | 3 | 0.512 | 2 | 0.512 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
489 | 489 | CL2-103 | KERRY | KERRY | SS-636 | Garranebane 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.235 | 11 | 0.488 | 2 | 0.488 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
490 | 490 | CL2-104 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.346 | 9 | 0.103 | 2 | 0.103 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
491 | 491 | CL2-105 | KILKENNY | KILKENNY | SS-347 | Glengoole 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.804 | 12 | 0.154 | 2 | 0.154 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
492 | 492 | CL2-106 | WATERFORD | WATERFORD | SS-505 | Kilmacthomas 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.321 | 7 | 0.412 | 2 | 0.412 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
493 | 493 | CL2-107 | DONEGAL | DONEGAL | SS-689 |  | ESB Networks | 38000 |  |  | 11.25 | 12 | 0.312 | 2 | 0.312 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
494 | 494 | CL2-108 | SLIGO | SLIGO | SS-227 | Bundoran 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.622 | 13 | 0.393 | 2 | 0.393 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718
495 | 495 | CL2-109 | MAYO | MAYO | SS-201 | Swinford 38kV Station | ESB Networks | 38000 | 38000 | low | 7.333 | 8 | 0.148 | 2 | 0.148 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
496 | 496 | CL2-110 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.874 | 11 | 0.438 | 2 | 0.438 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
497 | 497 | CL2-111 | DONEGAL | DONEGAL | SS-617 | Mulreavy 110kV Substation | EirGrid | 110000 | 33000 | 110000 | 8.807 | 9 | 0.316 | 2 | 0.316 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213
498 | 498 | CL2-112 | LOUTH | LOUTH | SS-651 | Grange 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.124 | 7 | 0.109 | 2 | 0.109 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
499 | 499 | CL2-113 | LOUTH | LOUTH | SS-651 | Grange 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.509 | 5 | 0.093 | 2 | 0.093 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
500 | 500 | CL2-114 | LOUTH | LOUTH | SS-650 | Ballymascanlan 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.596 | 9 | 0.272 | 2 | 0.272 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
501 | 501 | CL2-115 | CORK | CORK | SS-253 | Ballydehob 38kV Substation | ESB Networks | 38000 | 38000 | low | 20.362 | 21 | 0.19 | 2 | 0.19 | 4.2 | 4.2 | 1966840 | 1 | 468295.2381 | 2.1354
502 | 502 | CL2-116 | CORK | CORK | SS-562 | Bantry 38kV Substation | ESB Networks | 38000 | 38000 | low | 25.701 | 26 | 0.154 | 2 | 0.154 | 4.2 | 4.2 | 2230340 | 1 | 531033.3333 | 1.8831
503 | 503 | CL2-117 | CORK | CORK | SS-562 | Bantry 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.634 | 16 | 0.15 | 2 | 0.15 | 4.2 | 4.2 | 1703340 | 1 | 405557.1429 | 2.4657
504 | 504 | CL2-118 | CORK | CORK | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.195 | 11 | 0.12 | 2 | 0.12 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
505 | 505 | CL2-119 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.503 | 7 | 0.139 | 2 | 0.139 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
506 | 506 | CL2-120 | CORK | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.068 | 6 | 0.151 | 2 | 0.151 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
507 | 507 | CL2-121 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.211 | 14 | 0.269 | 2 | 0.269 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284
508 | 508 | CL2-122 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 17.54 | 18 | 0.241 | 2 | 0.241 | 4.2 | 4.2 | 1808740 | 1 | 430652.381 | 2.3221
509 | 509 | CL2-123 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 17.443 | 18 | 0.348 | 2 | 0.348 | 4.2 | 4.2 | 1808740 | 1 | 430652.381 | 2.3221
510 | 510 | CL2-124 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.848 | 9 | 0.199 | 2 | 0.199 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
511 | 511 | CL2-125 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.643 | 9 | 0.155 | 2 | 0.155 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
512 | 512 | CL2-126 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 18.412 | 19 | 0.118 | 2 | 0.118 | 4.2 | 4.2 | 1861440 | 1 | 443200 | 2.2563
513 | 513 | CL2-127 | KERRY | KERRY | SS-321 | Milltown 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 19.015 | 20 | 0.4 | 2 | 0.4 | 4.2 | 4.2 | 1914140 | 1 | 455747.619 | 2.1942
514 | 514 | CL2-128 | KERRY | KERRY | SS-387 | Coolcorcoran 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.843 | 9 | 0.454 | 2 | 0.454 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
515 | 515 | CL2-129 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.158 | 15 | 0.156 | 2 | 0.156 | 4.2 | 4.2 | 1650640 | 1 | 393009.5238 | 2.5445
516 | 516 | CL2-130 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.708 | 8 | 0.132 | 2 | 0.132 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
517 | 517 | CL2-131 | KERRY | KERRY | SS-636 | Garranebane 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.801 | 9 | 0.109 | 2 | 0.109 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
518 | 518 | CL2-132 | KERRY | KERRY | SS-321 | Milltown 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 16.282 | 17 | 0.144 | 2 | 0.144 | 4.2 | 4.2 | 1756040 | 1 | 418104.7619 | 2.3917
519 | 519 | CL2-133 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.432 | 3 | 0.208 | 2 | 0.208 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
520 | 520 | CL2-134 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.545 | 2 | 0.093 | 2 | 0.093 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007
521 | 521 | CL2-135 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.3 | 3 | 0.405 | 2 | 0.405 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
522 | 522 | CL2-136 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 12.421 | 13 | 0.108 | 2 | 0.108 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718
523 | 523 | CL2-137 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.419 | 9 | 0.495 | 2 | 0.495 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
524 | 524 | CL2-138 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 3.448 | 4 | 0.351 | 2 | 0.351 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
525 | 525 | CL2-139 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 3.687 | 4 | 0.42 | 2 | 0.42 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
526 | 526 | CL2-140 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.867 | 7 | 0.21 | 2 | 0.21 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
527 | 527 | CL2-141 | KERRY | KERRY | SS-555 | Ballybunion 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.189 | 6 | 0.147 | 2 | 0.147 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
528 | 528 | CL2-142 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 20.278 | 21 | 0.33 | 2 | 0.33 | 4.2 | 4.2 | 1966840 | 1 | 468295.2381 | 2.1354
529 | 529 | CL2-143 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 22.224 | 23 | 0.092 | 2 | 0.092 | 4.2 | 4.2 | 2072240 | 1 | 493390.4762 | 2.0268
530 | 530 | CL2-144 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.655 | 15 | 0.171 | 2 | 0.171 | 4.2 | 4.2 | 1650640 | 1 | 393009.5238 | 2.5445
531 | 531 | CL2-145 | CLARE | CLARE | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 18.608 | 19 | 0.312 | 2 | 0.312 | 4.2 | 4.2 | 1861440 | 1 | 443200 | 2.2563
532 | 532 | CL2-146 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.936 | 11 | 0.172 | 2 | 0.172 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
533 | 533 | CL2-147 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.888 | 15 | 0.174 | 2 | 0.174 | 4.2 | 4.2 | 1650640 | 1 | 393009.5238 | 2.5445
534 | 534 | CL2-148 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.564 | 12 | 0.433 | 2 | 0.433 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
535 | 535 | CL2-149 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.629 | 5 | 0.272 | 2 | 0.272 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
536 | 536 | CL2-150 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.222 | 6 | 0.248 | 2 | 0.248 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
537 | 537 | CL2-151 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.288 | 9 | 0.207 | 2 | 0.207 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
538 | 538 | CL2-152 | MAYO | MAYO | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 18.506 | 19 | 0.212 | 2 | 0.212 | 4.2 | 4.2 | 1861440 | 1 | 443200 | 2.2563
539 | 539 | CL2-153 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 16.36 | 17 | 0.41 | 2 | 0.41 | 4.2 | 4.2 | 1756040 | 1 | 418104.7619 | 2.3917
540 | 540 | CL2-154 | GALWAY | GALWAY | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 14.183 | 15 | 0.476 | 2 | 0.476 | 4.2 | 4.2 | 1650640 | 1 | 393009.5238 | 2.5445
541 | 541 | CL2-155 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 16.065 | 17 | 0.117 | 2 | 0.117 | 4.2 | 4.2 | 2312370 | 7 | 550564.2857 | 1.8163
542 | 542 | CL2-156 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 15.196 | 16 | 0.198 | 2 | 0.198 | 4.2 | 4.2 | 2259670 | 7 | 538016.6667 | 1.8587
543 | 543 | CL2-157 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.059 | 16 | 0.27 | 2 | 0.27 | 4.2 | 4.2 | 1703340 | 1 | 405557.1429 | 2.4657
544 | 544 | CL2-158 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.984 | 15 | 0.217 | 2 | 0.217 | 4.2 | 4.2 | 1650640 | 1 | 393009.5238 | 2.5445
545 | 545 | CL2-159 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.57 | 15 | 0.111 | 2 | 0.111 | 4.2 | 4.2 | 1650640 | 1 | 393009.5238 | 2.5445
546 | 546 | CL2-160 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.119 | 7 | 0.201 | 2 | 0.201 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
547 | 547 | CL2-161 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 18.275 | 19 | 0.094 | 2 | 0.094 | 4.2 | 4.2 | 1861440 | 1 | 443200 | 2.2563
548 | 548 | CL2-162 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 6.147 | 7 | 0.107 | 2 | 0.107 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525
549 | 549 | CL2-163 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.226 | 10 | 0.353 | 2 | 0.353 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
550 | 550 | CL2-164 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.486 | 7 | 0.371 | 2 | 0.371 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
551 | 551 | CL2-165 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.285 | 6 | 0.406 | 2 | 0.406 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
552 | 552 | CL2-166 | MAYO | MAYO | SS-317 | Newport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 12.325 | 13 | 0.11 | 2 | 0.11 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718
553 | 553 | CL2-167 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 12.785 | 13 | 0.09 | 2 | 0.09 | 4.2 | 4.2 | 2101570 | 7 | 500373.8095 | 1.9985
554 | 554 | CL2-168 | MAYO | MAYO | SS-170 | Derrynadivva 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.362 | 5 | 0.33 | 2 | 0.33 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
555 | 555 | CL2-169 | MAYO | MAYO | SS-170 | Derrynadivva 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.767 | 4 | 0.391 | 2 | 0.391 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
556 | 556 | CL2-170 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.967 | 12 | 0.192 | 2 | 0.192 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
557 | 557 | CL2-171 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 16.383 | 17 | 0.36 | 2 | 0.36 | 4.2 | 4.2 | 1756040 | 1 | 418104.7619 | 2.3917
558 | 558 | CL2-172 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 19.204 | 20 | 0.648 | 2 | 0.486 | 4.2 | 4.2 | 1914140 | 1 | 455747.619 | 2.1942
559 | 559 | CL2-173 | MAYO | MAYO | SS-710 | Tawnaghmore 110kV Substation | EirGrid | 110000 | low | 110000 | 13.533 | 14 | 0.243 | 2 | 0.243 | 4.2 | 4.2 | 2154270 | 7 | 512921.4286 | 1.9496
560 | 560 | CL2-174 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.677 | 6 | 0.281 | 2 | 0.281 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
561 | 561 | CL2-175 | SLIGO | SLIGO | SS-198 | Enniscrone 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 3.204 | 4 | 0.603 | 2 | 0.603 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
562 | 562 | CL2-176 | SLIGO | SLIGO | SS-042 | Ballytivnan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 11.373 | 12 | 0.284 | 2 | 0.284 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
563 | 563 | CL2-177 | SLIGO | SLIGO | SS-042 | Ballytivnan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.941 | 8 | 0.153 | 2 | 0.153 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
564 | 564 | CL2-178 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.751 | 7 | 0.344 | 2 | 0.344 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
565 | 565 | CL2-179 | DONEGAL | DONEGAL | SS-643 | Donegal 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.074 | 8 | 0.402 | 2 | 0.402 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
566 | 566 | CL2-180 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 6.814 | 7 | 0.107 | 2 | 0.107 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
567 | 567 | CL2-181 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 5.533 | 6 | 0.332 | 2 | 0.332 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
568 | 568 | CL2-182 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 5.79 | 6 | 0.621 | 2 | 0.46575 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
569 | 569 | CL2-183 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 12.903 | 13 | 0.638 | 2 | 0.4785 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718
570 | 570 | CL2-184 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.589 | 9 | 0.301 | 2 | 0.301 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
571 | 571 | CL2-185 | DONEGAL | DONEGAL | SS-252 | Killybegs 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.054 | 9 | 0.204 | 2 | 0.204 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
572 | 572 | CL2-186 | DONEGAL | DONEGAL | SS-252 | Killybegs 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 5.256 | 6 | 0.121 | 2 | 0.121 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
573 | 573 | CL2-187 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 10.587 | 11 | 0.182 | 2 | 0.182 | 4.2 | 4.2 | 1996170 | 7 | 475278.5714 | 2.104
574 | 574 | CL2-188 | DONEGAL | DONEGAL | SS-686 | Dungloe 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.116 | 8 | 0.098 | 2 | 0.098 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
575 | 575 | CL2-189 | DONEGAL | DONEGAL | SS-687 | Gweedore Wind Farm 38kV Substation | ESB Networks | 38000 | low | 38000 | 10.865 | 11 | 0.261 | 2 | 0.261 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
576 | 576 | CL2-190 | DONEGAL | DONEGAL | SS-138 | Creeslough 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.187 | 6 | 0.451 | 2 | 0.451 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
577 | 577 | CL2-191 | DONEGAL | DONEGAL | SS-119 | Drumlough Hill (1) 38kV Substation | ESB Networks | 38000 | low | 38000 | 6.5 | 7 | 0.41 | 2 | 0.41 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
578 | 578 | CL2-192 | DONEGAL | DONEGAL | SS-119 | Drumlough Hill (1) 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.362 | 4 | 0.168 | 2 | 0.168 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
579 | 579 | CL2-193 | DONEGAL | DONEGAL | SS-125 | Drumlough Hill (2) 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.583 | 2 | 0.16 | 2 | 0.16 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007
580 | 580 | CL2-194 | DONEGAL | DONEGAL | SS-239 | Moville 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.499 | 9 | 0.269 | 2 | 0.269 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
581 | 581 | CL2-195 | DONEGAL | DONEGAL | SS-272 | Carndonagh 38kV | ESB Networks | 38000 | 38000 | low | 3.406 | 4 | 0.14 | 2 | 0.14 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
582 | 582 | CL2-196 | DONEGAL | DONEGAL | SS-689 |  | ESB Networks | 38000 |  |  | 2.678 | 3 | 0.181 | 2 | 0.181 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
583 | 583 | CL2-197 | DONEGAL | DONEGAL | SS-687 | Gweedore Wind Farm 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.067 | 3 | 0.095 | 2 | 0.095 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
584 | 584 | CL2-198 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.348 | 6 | 0.136 | 2 | 0.136 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
585 | 585 | CL2-199 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.028 | 11 | 0.43 | 2 | 0.43 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
586 | 586 | CL2-200 | CORK | KERRY | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.494 | 11 | 0.132 | 2 | 0.132 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
587 | 587 | CL2-201 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 18.922 | 19 | 0.366 | 2 | 0.366 | 4.2 | 4.2 | 1861440 | 1 | 443200 | 2.2563
588 | 588 | CL2-202 | LEITRIM | LEITRIM | SS-534 | Garvagh Glebe 110kV Substation Extension | EirGrid | 110000 | 20000 | 110000 | 2.074 | 3 | 0.236 | 2 | 0.236 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674
589 | 589 | CL2-203 | WICKLOW | WICKLOW | SS-222 | Poulaphouca 110kV Substation | EirGrid | 110000 | low | 110000 | 11.628 | 12 | 0.411 | 2 | 0.411 | 4.2 | 4.2 | 2048870 | 7 | 487826.1905 | 2.0499
590 | 590 | CL2-204 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.271 | 9 | 0.128 | 2 | 0.128 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
591 | 591 | CL2-205 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.191 | 11 | 0.395 | 2 | 0.395 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
592 | 592 | CL2-206 | WICKLOW | WICKLOW | SS-062 | Stratford 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 7.029 | 8 | 0.315 | 2 | 0.315 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285
593 | 593 | CL2-207 | WICKLOW | WICKLOW | SS-209 | Blessington 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.407 | 7 | 0.414 | 2 | 0.414 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
594 | 594 | CL2-208 | WICKLOW | WICKLOW | SS-209 | Blessington 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.957 | 5 | 0.128 | 2 | 0.128 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
595 | 595 | CL2-209 | WICKLOW | WICKLOW | SS-209 | Blessington 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.185 | 12 | 0.213 | 2 | 0.213 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
596 | 596 | CL2-210 | WICKLOW | WICKLOW | SS-570 | Kilcoole 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.539 | 12 | 0.094 | 2 | 0.094 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
597 | 597 | CL2-211 | DUBLIN | DUBLIN | SS-091 | Whitestown 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.173 | 7 | 0.101 | 2 | 0.101 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
598 | 598 | CL2-212 | WICKLOW | WICKLOW | SS-699 | Ballycumber 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.313 | 2 | 0.407 | 2 | 0.407 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007
599 | 599 | CL2-213 | WICKLOW | WICKLOW | SS-699 | Ballycumber 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.392 | 3 | 0.143 | 2 | 0.143 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
600 | 600 | CL2-214 | KERRY | KERRY | SS-637 | Kilgarvan 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.281 | 5 | 0.265 | 2 | 0.265 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
601 | 601 | CL2-215 | CORK | CORK | SS-668 | Coomataggart 110 kV Substation | EirGrid | 110000 | low | 110000 | 1.6 | 2 | 0.187 | 2 | 0.187 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341
602 | 602 | CL2-216 | CORK | CORK | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 7.879 | 8 | 0.091 | 2 | 0.091 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
603 | 603 | CL2-217 | CORK | CORK | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 7.009 | 8 | 0.105 | 2 | 0.105 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
604 | 604 | CL2-218 | CORK | CORK | SS-161 | Gneeves 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.873 | 5 | 0.35 | 2 | 0.35 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
605 | 605 | CL2-219 | CORK | CORK | SS-161 | Gneeves 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.263 | 3 | 0.247 | 2 | 0.247 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
606 | 606 | CL2-220 | CORK | CORK | SS-161 | Gneeves 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.572 | 4 | 0.136 | 2 | 0.136 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
607 | 607 | CL2-221 | CORK | CORK | SS-161 | Gneeves 38kV Substation | ESB Networks | 38000 | low | 38000 | 6.496 | 7 | 0.311 | 2 | 0.311 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
608 | 608 | CL2-222 | CORK | CORK | SS-096 | Boggeragh 110kV Substation | EirGrid | 110000 |  |  | 1.741 | 2 | 0.601 | 2 | 0.601 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341
609 | 609 | CL2-223 | WATERFORD | WATERFORD | SS-532 | Woodhouse 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 1.491 | 2 | 0.586 | 2 | 0.586 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341
610 | 610 | CL2-224 | KILKENNY | KILKENNY | SS-495 | New Ross (West) 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.894 | 10 | 0.121 | 2 | 0.121 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
611 | 611 | CL2-225 | LIMERICK | LIMERICK | SS-069 | Garryspillane 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.414 | 5 | 0.324 | 2 | 0.324 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
612 | 612 | CL2-226 | LIMERICK | LIMERICK | SS-069 | Garryspillane 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.875 | 4 | 0.382 | 2 | 0.382 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
613 | 613 | CL2-227 | TIPPERARY | TIPPERARY | SS-645 | Toomevara 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.683 | 8 | 0.128 | 2 | 0.128 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
614 | 614 | CL2-228 | TIPPERARY | TIPPERARY | SS-645 | Toomevara 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.306 | 7 | 0.431 | 2 | 0.431 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
615 | 615 | CL2-229 | TIPPERARY | TIPPERARY | SS-540 | Templemore 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.271 | 9 | 0.236 | 2 | 0.236 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
616 | 616 | CL2-230 | DONEGAL | DONEGAL | SS-686 | Dungloe 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.555 | 6 | 0.403 | 2 | 0.403 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
617 | 617 | CL2-231 | DONEGAL | DONEGAL | SS-686 | Dungloe 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.384 | 13 | 0.193 | 2 | 0.193 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718
618 | 618 | CL2-232 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 11.409 | 12 | 0.513 | 2 | 0.513 | 4.2 | 4.2 | 2048870 | 7 | 487826.1905 | 2.0499
619 | 619 | CL2-233 | LEITRIM | LEITRIM | SS-097 | Corderry 110kV Substation | EirGrid | 110000 |  |  | 8.369 | 9 | 0.104 | 2 | 0.104 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213
620 | 620 | CL2-234 | MAYO | MAYO | SS-234 | Crossmolina 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.452 | 10 | 0.149 | 2 | 0.149 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
621 | 621 | CL2-235 | MAYO | MAYO | SS-234 | Crossmolina 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.266 | 9 | 0.167 | 2 | 0.167 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
622 | 622 | CL2-236 | DONEGAL | DONEGAL | SS-698 | Binbane 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.433 | 2 | 0.288 | 2 | 0.288 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007
623 | 623 | CL2-237 | DONEGAL | DONEGAL | SS-102 | Binbane 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 4.317 | 5 | 0.091 | 2 | 0.091 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5
624 | 624 | CL2-238 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 2.458 | 3 | 0.1 | 2 | 0.1 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674
625 | 625 | CL2-239 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 1.606 | 2 | 0.188 | 2 | 0.188 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341
626 | 626 | CL2-240 | WATERFORD | WATERFORD | SS-354 | Twomilebridge 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.166 | 6 | 0.155 | 2 | 0.155 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
627 | 627 | CL2-241 | WATERFORD | WATERFORD | SS-205 | Dungarvan 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 10.171 | 11 | 0.329 | 2 | 0.329 | 4.2 | 4.2 | 1996170 | 7 | 475278.5714 | 2.104
628 | 628 | CL2-242 | CORK | CORK | SS-695 | Castlepook 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 4.594 | 5 | 0.316 | 2 | 0.316 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
629 | 629 | CL2-243 | CORK | CORK | SS-695 | Castlepook 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 5.101 | 6 | 0.189 | 2 | 0.189 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
630 | 630 | CL2-244 | LIMERICK | LIMERICK | SS-256 | Mitchelstown West 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.474 | 8 | 0.213 | 2 | 0.213 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
631 | 631 | CL2-245 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.582 | 14 | 0.11 | 2 | 0.11 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284
632 | 632 | CL2-246 | WATERFORD | WATERFORD | SS-016 | Portlaw 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.653 | 3 | 0.464 | 2 | 0.464 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
633 | 633 | CL2-247 | TIPPERARY | TIPPERARY | SS-692 | Hollyford 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.199 | 3 | 0.476 | 2 | 0.476 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
634 | 634 | CL2-248 | CARLOW | CARLOW | SS-368 | Gortahile 38kV Substation | ESB Networks | 38000 | low | 38000 | 9.017 | 10 | 0.378 | 2 | 0.378 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
635 | 635 | CL2-249 | OFFALY | OFFALY | SS-084 | Birr 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.639 | 12 | 0.154 | 2 | 0.154 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
636 | 636 | CL2-250 | CORK | CORK | SS-668 | Coomataggart 110 kV Substation | EirGrid | 110000 | low | 110000 | 8.509 | 9 | 0.225 | 2 | 0.225 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213
637 | 637 | CL2-251 | LIMERICK | LIMERICK | SS-069 | Garryspillane 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.348 | 9 | 0.211 | 2 | 0.211 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
638 | 638 | CL2-252 | LIMERICK | LIMERICK | SS-695 | Castlepook 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 8.884 | 9 | 0.347 | 2 | 0.347 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
639 | 639 | CL2-253 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.565 | 9 | 0.201 | 2 | 0.201 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
640 | 640 | CL2-254 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.54 | 9 | 0.099 | 2 | 0.099 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
641 | 641 | CL2-255 | CORK | CORK | SS-197 | Midleton 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 7.187 | 8 | 0.104 | 2 | 0.104 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285
642 | 642 | CL2-256 | WATERFORD | WATERFORD | SS-622 | Barranafaddock 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.004 | 5 | 0.105 | 2 | 0.105 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
643 | 643 | CL2-257 | KILKENNY | KILKENNY | SS-489 | Ballyhale 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.903 | 3 | 0.09 | 2 | 0.09 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
644 | 644 | CL2-258 | WICKLOW | WICKLOW | SS-591 | Shillelagh 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.038 | 7 | 0.227 | 2 | 0.227 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
645 | 645 | CL2-259 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.431 | 5 | 0.123 | 2 | 0.123 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
646 | 646 | CL2-260 | CORK | CORK | SS-406 | Kanturk 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.163 | 7 | 0.146 | 2 | 0.146 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
647 | 647 | CL2-261 | LAOIS | LAOIS | SS-486 | Castlecomer 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.156 | 13 | 0.326 | 2 | 0.326 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718
648 | 648 | CL2-262 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 13.313 | 14 | 0.094 | 2 | 0.094 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284
649 | 649 | CL2-263 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 14.175 | 15 | 0.227 | 2 | 0.227 | 4.2 | 4.2 | 1650640 | 1 | 393009.5238 | 2.5445
650 | 650 | CL2-264 | TIPPERARY | TIPPERARY | SS-347 | Glengoole 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.388 | 6 | 0.124 | 2 | 0.124 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
651 | 651 | CL2-265 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.166 | 8 | 0.387 | 2 | 0.387 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
652 | 652 | CL2-266 | TIPPERARY | TIPPERARY | SS-585 | Kilross Road 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.344 | 6 | 0.287 | 2 | 0.287 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
653 | 653 | CL2-267 | WEXFORD | WEXFORD | SS-033 | Ballywater 110kV Substation | EirGrid | 110000 | low | 110000 | 3.45 | 4 | 0.421 | 2 | 0.421 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581
654 | 654 | CL2-268 | DONEGAL | DONEGAL | SS-610 | Milford (North) 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.511 | 8 | 0.203 | 2 | 0.203 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
655 | 655 | CL2-269 | DONEGAL | DONEGAL | SS-610 | Milford (North) 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.345 | 7 | 0.198 | 2 | 0.198 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
656 | 656 | CL2-270 | DONEGAL | DONEGAL | SS-610 | Milford (North) 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.562 | 8 | 0.494 | 2 | 0.494 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
657 | 657 | CL2-271 | DONEGAL | DONEGAL | SS-138 | Creeslough 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.954 | 7 | 0.176 | 2 | 0.176 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
658 | 658 | CL2-272 | GALWAY | GALWAY | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 10.861 | 11 | 0.265 | 2 | 0.265 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
659 | 659 | CL2-273 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 24.442 | 25 | 0.246 | 2 | 0.246 | 4.2 | 4.2 | 2733970 | 7 | 650945.2381 | 1.5362
660 | 660 | CL2-274 | SLIGO | SLIGO | SS-206 | Boyle 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 10.978 | 11 | 0.175 | 2 | 0.175 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
661 | 661 | CL2-275 | MAYO | MAYO | SS-203 | Foxford 38kV Substation | ESB Networks | 38000 |  |  | 7.233 | 8 | 0.185 | 2 | 0.185 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
662 | 662 | CL2-276 | ROSCOMMON | SLIGO | SS-206 | Boyle 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 5.549 | 6 | 0.167 | 2 | 0.167 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
663 | 663 | CL2-277 | GALWAY | GALWAY | SS-598 | Glennamaddy 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.923 | 5 | 0.545 | 2 | 0.545 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
664 | 664 | CL2-278 | MAYO | MAYO | SS-203 | Foxford 38kV Substation | ESB Networks | 38000 |  |  | 4.731 | 5 | 0.215 | 2 | 0.215 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
665 | 665 | CL2-279 | WESTMEATH | WESTMEATH | SS-246 | Loughanalla 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 5.824 | 6 | 0.202 | 2 | 0.202 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
666 | 666 | CL2-280 | WESTMEATH | WESTMEATH | SS-517 | Delvin 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.091 | 4 | 0.612 | 2 | 0.459 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
667 | 667 | CL2-281 | MEATH | MEATH | SS-388 | Oldcastle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.07 | 5 | 0.284 | 2 | 0.284 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
668 | 668 | CL2-282 | GALWAY | GALWAY | SS-109 | Cloon 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.626 | 9 | 0.457 | 2 | 0.457 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213
669 | 669 | CL2-283 | MAYO | MAYO | SS-640 | Ballinrobe 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.053 | 5 | 0.119 | 2 | 0.119 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
670 | 670 | CL2-284 | DONEGAL | DONEGAL | SS-117 | Crockahenny 38kV Substation | ESB Networks | 38000 | low | 38000 | 5.614 | 6 | 0.14 | 2 | 0.14 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
671 | 671 | CL2-285 | DONEGAL | DONEGAL | SS-239 | Moville 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.258 | 5 | 0.315 | 2 | 0.315 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
672 | 672 | CL2-286 | DONEGAL | DONEGAL | SS-117 | Crockahenny 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.215 | 4 | 7.249 | 2 | 5.4367 | 67.2 | 67.2 | 1761700 | 11 | 26215.7738 | 38.145
673 | 673 | CL2-287 | DONEGAL | DONEGAL | SS-690 | Stranrolar 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.433 | 8 | 1.678 | 2 | 1.2585 | 12.6 | 12.6 | 909950 | 4 | 72218.254 | 13.8469
674 | 674 | CL2-288 | DONEGAL | DONEGAL | SS-083 | Golagh 110kV Substation | EirGrid | 110000 | 38000 | 110000 | 4.239 | 5 | 8.595 | 2 | 6.4463 | 79.8 | 79.8 | 1972510 | 11 | 24718.1704 | 40.4561
675 | 675 | CL2-289 | DONEGAL | DONEGAL | SS-690 | Stranrolar 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.111 | 8 | 0.832 | 2 | 0.624 | 8.4 | 8.4 | 909950 | 4 | 108327.381 | 9.2313
676 | 676 | CL2-290 | DONEGAL | DONEGAL | SS-617 | Mulreavy 110kV Substation | EirGrid | 110000 | 33000 | 110000 | 6.22 | 7 | 3.117 | 2 | 2.3377 | 25.2 | 25.2 | 2575660 | 9 | 102208.7302 | 9.7839
677 | 677 | CL2-291 | DONEGAL | DONEGAL | SS-617 | Mulreavy 110kV Substation | EirGrid | 110000 | 33000 | 110000 | 11.976 | 12 | 2.83 | 2 | 2.1225 | 25.2 | 25.2 | 3019810 | 9 | 119833.7302 | 8.3449
678 | 678 | CL2-292 | DONEGAL | DONEGAL | SS-617 | Mulreavy 110kV Substation | EirGrid | 110000 | 33000 | 110000 | 8.888 | 9 | 12.212 | 2 | 9.159 | 113.4 | 113.4 | 2815750 | 11 | 24830.2469 | 40.2735
679 | 679 | CL2-293 | DONEGAL | DONEGAL | SS-617 | Mulreavy 110kV Substation | EirGrid | 110000 | 33000 | 110000 | 3.834 | 4 | 12.925 | 2 | 9.6938 | 117.6 | 117.6 | 1761700 | 11 | 14980.4422 | 66.7537
680 | 680 | CL2-294 | DONEGAL | DONEGAL | SS-083 | Golagh 110kV Substation | EirGrid | 110000 | 38000 | 110000 | 11.56 | 12 | 9.009 | 2 | 6.7568 | 84 | 84 | 3448180 | 11 | 41049.7619 | 24.3607
681 | 681 | CL2-295 | DONEGAL | DONEGAL | SS-087 | Cliff 110kV Substation | EirGrid | 110000 | low | 110000 | 10.692 | 11 | 3.2 | 2 | 2.4 | 29.4 | 29.4 | 2930980 | 9 | 99693.1973 | 10.0308
682 | 682 | CL2-296 | DONEGAL | DONEGAL | SS-083 | Golagh 110kV Substation | EirGrid | 110000 | 38000 | 110000 | 15.523 | 16 | 0.849 | 2 | 0.63675 | 8.4 | 8.4 | 2259670 | 7 | 269008.3333 | 3.7174
683 | 683 | CL2-297 | DONEGAL | DONEGAL | SS-087 | Cliff 110kV Substation | EirGrid | 110000 | low | 110000 | 4.515 | 5 | 1.499 | 2 | 1.1242 | 12.6 | 12.6 | 1679970 | 7 | 133330.9524 | 7.5001
684 | 684 | CL2-298 | DONEGAL | DONEGAL | SS-087 | Cliff 110kV Substation | EirGrid | 110000 | low | 110000 | 5.378 | 6 | 1.796 | 2 | 1.347 | 12.6 | 12.6 | 1732670 | 7 | 137513.4921 | 7.272
685 | 685 | CL2-299 | DONEGAL | DONEGAL | SS-617 | Mulreavy 110kV Substation | EirGrid | 110000 | 33000 | 110000 | 1.486 | 2 | 1.813 | 2 | 1.3598 | 16.8 | 16.8 | 1340080 | 11 | 79766.6667 | 12.5366
686 | 686 | CL2-300 | CAVAN | CAVAN | SS-110 | Corraclassy 110kV Substation | EirGrid | 110000 |  |  | 15.501 | 16 | 0.978 | 2 | 0.7335 | 8.4 | 8.4 | 2259670 | 7 | 269008.3333 | 3.7174
687 | 687 | CL2-301 | CAVAN | CAVAN | SS-110 | Corraclassy 110kV Substation | EirGrid | 110000 |  |  | 9.916 | 10 | 4.855 | 2 | 3.6413 | 42 | 42 | 3066450 | 10 | 73010.7143 | 13.6966
688 | 688 | CL2-302 | CAVAN | CAVAN | SS-110 | Corraclassy 110kV Substation | EirGrid | 110000 |  |  | 5.003 | 6 | 6.143 | 2 | 4.6072 | 54.6 | 54.6 | 2183320 | 11 | 39987.5458 | 25.0078
689 | 689 | CL2-303 | CAVAN | MEATH | SS-111 | Gortawee 110kV Station | EirGrid | 110000 | 110000 | low | 4.966 | 5 | 5.016 | 2 | 3.762 | 46.2 | 46.2 | 1972510 | 11 | 42695.0216 | 23.4219
690 | 690 | CL2-304 | LOUTH | LOUTH | SS-650 | Ballymascanlan 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.2 | 6 | 0.96 | 2 | 0.72 | 8.4 | 8.4 | 769410 | 4 | 91596.4286 | 10.9175
691 | 691 | CL2-305 | LOUTH | LOUTH | SS-650 | Ballymascanlan 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.84 | 6 | 0.534 | 2 | 0.534 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
692 | 692 | CL2-306 | LOUTH | LOUTH | SS-650 | Ballymascanlan 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.469 | 5 | 4.021 | 2 | 3.0157 | 33.6 | 33.6 | 904090 | 6 | 26907.4405 | 37.1644
693 | 693 | CL2-307 | LOUTH | LOUTH | SS-650 | Ballymascanlan 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.443 | 9 | 0.963 | 2 | 0.72225 | 8.4 | 8.4 | 1379800 | 2 | 164261.9048 | 6.0878
694 | 694 | CL2-308 | WEXFORD | WEXFORD | SS-314 | Richfield 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.174 | 4 | 0.844 | 2 | 0.633 | 8.4 | 8.4 | 628870 | 4 | 74865.4762 | 13.3573
695 | 695 | CL2-309 | CORK | CORK | SS-253 | Ballydehob 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.485 | 12 | 0.605 | 2 | 0.605 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
696 | 696 | CL2-310 | CORK | CORK | SS-254 | Glanta Commons 38kV Station | ESB Networks | 38000 |  |  | 5.551 | 6 | 0.625 | 2 | 0.46875 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
697 | 697 | CL2-311 | CORK | CORK | SS-254 | Glanta Commons 38kV Station | ESB Networks | 38000 |  |  | 2.882 | 3 | 0.69 | 2 | 0.5175 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
698 | 698 | CL2-312 | CORK | CORK | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.833 | 6 | 1.042 | 2 | 0.7815 | 8.4 | 8.4 | 769410 | 4 | 91596.4286 | 10.9175
699 | 699 | CL2-313 | CORK | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.385 | 12 | 9.018 | 2 | 6.7635 | 84 | 84 | 3448180 | 11 | 41049.7619 | 24.3607
700 | 700 | CL2-314 | CORK | CORK | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 13.904 | 14 | 2.259 | 2 | 1.6942 | 21 | 21 | 1331570 | 4 | 63408.0952 | 15.7709
701 | 701 | CL2-315 | KERRY | KERRY | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 14.198 | 15 | 1.14 | 2 | 0.855 | 8.4 | 8.4 | 1696000 | 2 | 201904.7619 | 4.9528
702 | 702 | CL2-316 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 13.903 | 14 | 1.794 | 2 | 1.3455 | 12.6 | 12.6 | 1680350 | 3 | 133361.1111 | 7.4984
703 | 703 | CL2-317 | CORK | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.126 | 9 | 7.779 | 2 | 5.8342 | 71.4 | 71.4 | 2815750 | 11 | 39436.2745 | 25.3574
704 | 704 | CL2-318 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.671 | 11 | 0.831 | 2 | 0.62325 | 8.4 | 8.4 | 1485200 | 2 | 176809.5238 | 5.6558
705 | 705 | CL2-319 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.388 | 11 | 0.743 | 2 | 0.55725 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
706 | 706 | CL2-320 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.47 | 9 | 0.881 | 2 | 0.66075 | 8.4 | 8.4 | 1379800 | 2 | 164261.9048 | 6.0878
707 | 707 | CL2-321 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.847 | 11 | 0.653 | 2 | 0.48975 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
708 | 708 | CL2-322 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.551 | 11 | 3.338 | 2 | 2.5035 | 29.4 | 29.4 | 1324920 | 5 | 45065.3061 | 22.19
709 | 709 | CL2-323 | CORK | KERRY | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 3.988 | 4 | 5.645 | 2 | 4.2337 | 50.4 | 50.4 | 1761700 | 11 | 34954.3651 | 28.6087
710 | 710 | CL2-324 | CORK | KERRY | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.151 | 7 | 4.207 | 2 | 3.1552 | 37.8 | 37.8 | 1126610 | 6 | 29804.4974 | 33.552
711 | 711 | CL2-325 | CORK | KERRY | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.789 | 10 | 2.449 | 2 | 1.8367 | 21 | 21 | 1050490 | 4 | 50023.3333 | 19.9907
712 | 712 | CL2-326 | KERRY | KERRY | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.716 | 10 | 1.335 | 2 | 1.0012 | 8.4 | 8.4 | 1432500 | 2 | 170535.7143 | 5.8639
713 | 713 | CL2-327 | KERRY | KERRY | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.683 | 10 | 0.46 | 2 | 0.46 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
714 | 714 | CL2-328 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 17.138 | 18 | 2.312 | 2 | 1.734 | 21 | 21 | 1612650 | 4 | 76792.8571 | 13.022
715 | 715 | CL2-329 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 15.665 | 16 | 0.252 | 2 | 0.252 | 4.2 | 4.2 | 1703340 | 1 | 405557.1429 | 2.4657
716 | 716 | CL2-330 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 15.771 | 16 | 0.451 | 2 | 0.451 | 4.2 | 4.2 | 1703340 | 1 | 405557.1429 | 2.4657
717 | 717 | CL2-331 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 15.333 | 16 | 1.488 | 2 | 1.116 | 12.6 | 12.6 | 1785750 | 3 | 141726.1905 | 7.0559
718 | 718 | CL2-332 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 14.295 | 15 | 2.288 | 2 | 1.716 | 21 | 21 | 1401840 | 4 | 66754.2857 | 14.9803
719 | 719 | CL2-333 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 12.313 | 13 | 3.128 | 2 | 2.346 | 25.2 | 25.2 | 1502580 | 5 | 59626.1905 | 16.7712
720 | 720 | CL2-334 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 11.695 | 12 | 12.491 | 2 | 9.3682 | 113.4 | 113.4 | 3448180 | 11 | 30407.231 | 32.8869
721 | 721 | CL2-335 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 15.603 | 16 | 12.868 | 2 | 9.651 | 117.6 | 117.6 | 4291420 | 11 | 36491.6667 | 27.4035
722 | 722 | CL2-336 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 12.315 | 13 | 0.405 | 2 | 0.405 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718
723 | 723 | CL2-337 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.756 | 11 | 2.849 | 2 | 2.1368 | 25.2 | 25.2 | 1324920 | 5 | 52576.1905 | 19.02
724 | 724 | CL2-338 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 17.133 | 18 | 1.444 | 2 | 1.083 | 12.6 | 12.6 | 1891150 | 3 | 150091.2698 | 6.6626
725 | 725 | CL2-339 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.416 | 12 | 3.178 | 2 | 2.3835 | 29.4 | 29.4 | 1413750 | 5 | 48086.7347 | 20.7958
726 | 726 | CL2-340 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 16.462 | 17 | 0.493 | 2 | 0.493 | 4.2 | 4.2 | 1756040 | 1 | 418104.7619 | 2.3917
727 | 727 | CL2-341 | KERRY | KERRY | SS-321 | Milltown 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 15.486 | 16 | 3.494 | 2 | 2.6205 | 29.4 | 29.4 | 1769070 | 5 | 60172.449 | 16.6189
728 | 728 | CL2-342 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 18.593 | 19 | 1 | 2 | 0.75 | 8.4 | 8.4 | 1906800 | 2 | 227000 | 4.4053
729 | 729 | CL2-343 | KERRY | KERRY | SS-157 | Oughtragh 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 13.653 | 14 | 5.252 | 2 | 3.939 | 46.2 | 46.2 | 3869800 | 11 | 83761.9048 | 11.9386
730 | 730 | CL2-344 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.314 | 14 | 5.042 | 2 | 3.7815 | 46.2 | 46.2 | 3869800 | 11 | 83761.9048 | 11.9386
731 | 731 | CL2-345 | KERRY | KERRY | SS-637 | Kilgarvan 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.353 | 5 | 1.31 | 2 | 0.9825 | 8.4 | 8.4 | 699140 | 4 | 83230.9524 | 12.0148
732 | 732 | CL2-346 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.799 | 6 | 4.905 | 2 | 3.6787 | 42 | 42 | 1015350 | 6 | 24175 | 41.365
733 | 733 | CL2-347 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.137 | 7 | 0.445 | 2 | 0.445 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
734 | 734 | CL2-348 | KERRY | KERRY | SS-637 | Kilgarvan 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.611 | 7 | 22.834 | 2 | 17.1255 | 210 | 210 | 7158040 | 12 | 34085.9048 | 29.3376
735 | 735 | CL2-349 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.422 | 6 | 1.176 | 2 | 0.882 | 8.4 | 8.4 | 769410 | 4 | 91596.4286 | 10.9175
736 | 736 | CL2-350 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.583 | 16 | 2.727 | 2 | 2.0452 | 25.2 | 25.2 | 1769070 | 5 | 70201.1905 | 14.2448
737 | 737 | CL2-351 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 7.63 | 8 | 0.527 | 2 | 0.527 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
738 | 738 | CL2-352 | KERRY | KERRY | SS-636 | Garranebane 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.985 | 7 | 0.45 | 2 | 0.45 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
739 | 739 | CL2-353 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 9.092 | 10 | 1.297 | 2 | 0.97275 | 8.4 | 8.4 | 1432500 | 2 | 170535.7143 | 5.8639
740 | 740 | CL2-354 | KERRY | KERRY | SS-636 | Garranebane 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.516 | 6 | 0.977 | 2 | 0.73275 | 8.4 | 8.4 | 769410 | 4 | 91596.4286 | 10.9175
741 | 741 | CL2-355 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 9.204 | 10 | 4.029 | 2 | 3.0217 | 33.6 | 33.6 | 1460390 | 6 | 43463.9881 | 23.0076
742 | 742 | CL2-356 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 15.202 | 16 | 2.145 | 2 | 1.6088 | 16.8 | 16.8 | 1472110 | 4 | 87625.5952 | 11.4122
743 | 743 | CL2-357 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 12.386 | 13 | 5.754 | 2 | 4.3155 | 50.4 | 50.4 | 3658990 | 11 | 72599.0079 | 13.7743
744 | 744 | CL2-358 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 8.772 | 9 | 1.86 | 2 | 1.395 | 16.8 | 16.8 | 980220 | 4 | 58346.4286 | 17.139
745 | 745 | CL2-359 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.2 | 5 | 4.781 | 2 | 3.5857 | 42 | 42 | 904090 | 6 | 21525.9524 | 46.4556
746 | 746 | CL2-360 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 6.55 | 7 | 1.419 | 2 | 1.0642 | 12.6 | 12.6 | 839680 | 4 | 66641.2698 | 15.0057
747 | 747 | CL2-361 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 9.046 | 10 | 2.388 | 2 | 1.791 | 21 | 21 | 1050490 | 4 | 50023.3333 | 19.9907
748 | 748 | CL2-362 | KERRY | KERRY | SS-321 | Milltown 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 14.441 | 15 | 3.954 | 2 | 2.9655 | 33.6 | 33.6 | 2016690 | 6 | 60020.5357 | 16.661
749 | 749 | CL2-363 | CORK | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.893 | 7 | 26.94 | 2 | 20.205 | 247.8 | 247.8 | 7158040 | 12 | 28886.36 | 34.6184
750 | 750 | CL2-364 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.684 | 12 | 3.695 | 2 | 2.7712 | 33.6 | 33.6 | 1682910 | 6 | 50086.6071 | 19.9654
751 | 751 | CL2-365 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.048 | 10 | 3.714 | 2 | 2.7855 | 33.6 | 33.6 | 1460390 | 6 | 43463.9881 | 23.0076
752 | 752 | CL2-366 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.115 | 6 | 1.496 | 2 | 1.122 | 12.6 | 12.6 | 769410 | 4 | 61064.2857 | 16.3762
753 | 753 | CL2-367 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 2.639 | 3 | 1.152 | 2 | 0.864 | 8.4 | 8.4 | 558600 | 4 | 66500 | 15.0376
754 | 754 | CL2-368 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.933 | 5 | 0.755 | 2 | 0.56625 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
755 | 755 | CL2-369 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.296 | 8 | 1.256 | 2 | 0.942 | 8.4 | 8.4 | 909950 | 4 | 108327.381 | 9.2313
756 | 756 | CL2-370 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.988 | 10 | 1.839 | 2 | 1.3792 | 16.8 | 16.8 | 1050490 | 4 | 62529.1667 | 15.9925
757 | 757 | CL2-371 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.22 | 10 | 0.981 | 2 | 0.73575 | 8.4 | 8.4 | 1432500 | 2 | 170535.7143 | 5.8639
758 | 758 | CL2-372 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.912 | 5 | 5.159 | 2 | 3.8693 | 46.2 | 46.2 | 1972510 | 11 | 42695.0216 | 23.4219
759 | 759 | CL2-373 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 2.385 | 3 | 0.672 | 2 | 0.504 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
760 | 760 | CL2-374 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.86 | 10 | 12.005 | 2 | 9.0038 | 109.2 | 109.2 | 3026560 | 11 | 27715.7509 | 36.0806
761 | 761 | CL2-375 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.104 | 10 | 2.273 | 2 | 1.7048 | 21 | 21 | 1050490 | 4 | 50023.3333 | 19.9907
762 | 762 | CL2-376 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.168 | 6 | 0.348 | 2 | 0.348 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
763 | 763 | CL2-377 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.606 | 11 | 0.39 | 2 | 0.39 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
764 | 764 | CL2-378 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.385 | 9 | 16.042 | 2 | 12.0315 | 147 | 147 | 4339180 | 12 | 29518.2313 | 33.8774
765 | 765 | CL2-379 | KERRY | KERRY | SS-667 | Ballyrickard 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 9.573 | 10 | 0.937 | 2 | 0.70275 | 8.4 | 8.4 | 1432500 | 2 | 170535.7143 | 5.8639
766 | 766 | CL2-380 | KERRY | KERRY | SS-667 | Ballyrickard 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.925 | 8 | 0.769 | 2 | 0.57675 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
767 | 767 | CL2-381 | KERRY | KERRY | SS-140 | Ballyard 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 6.463 | 7 | 2.428 | 2 | 1.821 | 21 | 21 | 839680 | 4 | 39984.7619 | 25.0095
768 | 768 | CL2-382 | KERRY | KERRY | SS-140 | Ballyard 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 4.535 | 5 | 2.451 | 2 | 1.8382 | 21 | 21 | 699140 | 4 | 33292.381 | 30.0369
769 | 769 | CL2-383 | KERRY | KERRY | SS-147 | Smearla 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.052 | 9 | 0.708 | 2 | 0.531 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
770 | 770 | CL2-384 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.054 | 15 | 0.716 | 2 | 0.537 | 4.2 | 4.2 | 1650640 | 1 | 393009.5238 | 2.5445
771 | 771 | CL2-385 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.529 | 16 | 0.484 | 2 | 0.484 | 4.2 | 4.2 | 1703340 | 1 | 405557.1429 | 2.4657
772 | 772 | CL2-386 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 21.77 | 22 | 1.206 | 2 | 0.9045 | 8.4 | 8.4 | 2064900 | 2 | 245821.4286 | 4.068
773 | 773 | CL2-387 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 19.238 | 20 | 11.965 | 2 | 8.9737 | 109.2 | 109.2 | 5134660 | 11 | 47020.696 | 21.2672
774 | 774 | CL2-388 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.059 | 14 | 5.511 | 2 | 4.1333 | 50.4 | 50.4 | 3869800 | 11 | 76781.746 | 13.0239
775 | 775 | CL2-389 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 16.726 | 17 | 2.986 | 2 | 2.2395 | 25.2 | 25.2 | 1857900 | 5 | 73726.1905 | 13.5637
776 | 776 | CL2-390 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.488 | 9 | 0.929 | 2 | 0.69675 | 8.4 | 8.4 | 1379800 | 2 | 164261.9048 | 6.0878
777 | 777 | CL2-391 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 16.672 | 17 | 0.555 | 2 | 0.555 | 4.2 | 4.2 | 1756040 | 1 | 418104.7619 | 2.3917
778 | 778 | CL2-392 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.941 | 12 | 3.141 | 2 | 2.3558 | 25.2 | 25.2 | 1413750 | 5 | 56101.1905 | 17.8249
779 | 779 | CL2-393 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.869 | 14 | 0.886 | 2 | 0.6645 | 8.4 | 8.4 | 1643300 | 2 | 195630.9524 | 5.1117
780 | 780 | CL2-394 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.01 | 14 | 0.314 | 2 | 0.314 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284
781 | 781 | CL2-395 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.669 | 10 | 0.475 | 2 | 0.475 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
782 | 782 | CL2-396 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.002 | 6 | 4.355 | 2 | 3.2663 | 37.8 | 37.8 | 1015350 | 6 | 26861.1111 | 37.2285
783 | 783 | CL2-397 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.067 | 6 | 1.898 | 2 | 1.4235 | 16.8 | 16.8 | 769410 | 4 | 45798.2143 | 21.8349
784 | 784 | CL2-398 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.896 | 7 | 2.687 | 2 | 2.0152 | 21 | 21 | 839680 | 4 | 39984.7619 | 25.0095
785 | 785 | CL2-399 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.839 | 5 | 14.672 | 2 | 11.004 | 134.4 | 134.4 | 2818860 | 12 | 20973.6607 | 47.6788
786 | 786 | CL2-400 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.144 | 11 | 1.064 | 2 | 0.798 | 8.4 | 8.4 | 1485200 | 2 | 176809.5238 | 5.6558
787 | 787 | CL2-401 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.586 | 11 | 5.715 | 2 | 4.2862 | 50.4 | 50.4 | 3237370 | 11 | 64233.5317 | 15.5682
788 | 788 | CL2-402 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.771 | 13 | 0.617 | 2 | 0.46275 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718
789 | 789 | CL2-403 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.806 | 15 | 0.55 | 2 | 0.55 | 4.2 | 4.2 | 1650640 | 1 | 393009.5238 | 2.5445
790 | 790 | CL2-404 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.069 | 14 | 3.074 | 2 | 2.3055 | 25.2 | 25.2 | 1591410 | 5 | 63151.1905 | 15.835
791 | 791 | CL2-405 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.819 | 12 | 7.286 | 2 | 5.4645 | 67.2 | 67.2 | 3448180 | 11 | 51312.2024 | 19.4885
792 | 792 | CL2-406 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.307 | 12 | 0.668 | 2 | 0.501 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
793 | 793 | CL2-407 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.886 | 9 | 2.332 | 2 | 1.749 | 21 | 21 | 980220 | 4 | 46677.1429 | 21.4238
794 | 794 | CL2-408 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.63 | 12 | 1.894 | 2 | 1.4205 | 16.8 | 16.8 | 1191030 | 4 | 70894.6429 | 14.1054
795 | 795 | CL2-409 | MAYO | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 18.431 | 19 | 8.176 | 2 | 6.132 | 75.6 | 75.6 | 4923850 | 11 | 65130.291 | 15.3538
796 | 796 | CL2-410 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 18.316 | 19 | 1.301 | 2 | 0.97575 | 8.4 | 8.4 | 1906800 | 2 | 227000 | 4.4053
797 | 797 | CL2-411 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 16.39 | 17 | 10.796 | 2 | 8.097 | 96.6 | 96.6 | 4502230 | 11 | 46606.9358 | 21.456
798 | 798 | CL2-412 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 14.798 | 15 | 0.436 | 2 | 0.436 | 4.2 | 4.2 | 1650640 | 1 | 393009.5238 | 2.5445
799 | 799 | CL2-413 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 12.93 | 13 | 1.266 | 2 | 0.9495 | 8.4 | 8.4 | 1590600 | 2 | 189357.1429 | 5.281
800 | 800 | CL2-414 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 13.856 | 14 | 3.982 | 2 | 2.9865 | 33.6 | 33.6 | 1905430 | 6 | 56709.2262 | 17.6338
801 | 801 | CL2-415 | MAYO | MAYO | SS-640 | Ballinrobe 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.372 | 15 | 4.29 | 2 | 3.2175 | 37.8 | 37.8 | 2016690 | 6 | 53351.5873 | 18.7436
802 | 802 | CL2-416 | MAYO | MAYO | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 18.244 | 19 | 1.409 | 2 | 1.0568 | 12.6 | 12.6 | 1943850 | 3 | 154273.8095 | 6.482
803 | 803 | CL2-417 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 16.492 | 17 | 1.331 | 2 | 0.99825 | 8.4 | 8.4 | 1801400 | 2 | 214452.381 | 4.663
804 | 804 | CL2-418 | GALWAY | GALWAY | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 17.324 | 18 | 1.863 | 2 | 1.3973 | 16.8 | 16.8 | 1612650 | 4 | 95991.0714 | 10.4176
805 | 805 | CL2-419 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 16.325 | 17 | 1.005 | 2 | 0.75375 | 8.4 | 8.4 | 1801400 | 2 | 214452.381 | 4.663
806 | 806 | CL2-420 | GALWAY | GALWAY | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 15.186 | 16 | 0.842 | 2 | 0.6315 | 8.4 | 8.4 | 1748700 | 2 | 208178.5714 | 4.8036
807 | 807 | CL2-421 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 12.718 | 13 | 0.47 | 2 | 0.47 | 4.2 | 4.2 | 2101570 | 7 | 500373.8095 | 1.9985
808 | 808 | CL2-422 | GALWAY | GALWAY | SS-638 | Oughterard 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.117 | 9 | 4.259 | 2 | 3.1943 | 37.8 | 37.8 | 1349130 | 6 | 35691.2698 | 28.0181
809 | 809 | CL2-423 | GALWAY | GALWAY | SS-638 | Oughterard 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 11.242 | 12 | 2.266 | 2 | 1.6995 | 21 | 21 | 1191030 | 4 | 56715.7143 | 17.6318
810 | 810 | CL2-424 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 11.454 | 12 | 4.255 | 2 | 3.1913 | 37.8 | 37.8 | 3288970 | 10 | 87009.7884 | 11.493
811 | 811 | CL2-425 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.972 | 4 | 1.198 | 2 | 0.8985 | 8.4 | 8.4 | 628870 | 4 | 74865.4762 | 13.3573
812 | 812 | CL2-426 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 22.098 | 23 | 3.497 | 2 | 2.6227 | 29.4 | 29.4 | 2390880 | 5 | 81322.449 | 12.2967
813 | 813 | CL2-427 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 21.989 | 22 | 0.544 | 2 | 0.544 | 4.2 | 4.2 | 2575870 | 7 | 613302.381 | 1.6305
814 | 814 | CL2-428 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 20.436 | 21 | 3.046 | 2 | 2.2845 | 25.2 | 25.2 | 3819280 | 9 | 151558.7302 | 6.5981
815 | 815 | CL2-429 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 18.073 | 19 | 0.486 | 2 | 0.486 | 4.2 | 4.2 | 2417770 | 7 | 575659.5238 | 1.7371
816 | 816 | CL2-430 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 12.261 | 13 | 9.945 | 2 | 7.4588 | 92.4 | 92.4 | 3658990 | 11 | 39599.4589 | 25.2529
817 | 817 | CL2-431 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 11.499 | 12 | 0.986 | 2 | 0.7395 | 8.4 | 8.4 | 2048870 | 7 | 243913.0952 | 4.0998
818 | 818 | CL2-432 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 18.517 | 19 | 13.319 | 2 | 9.9893 | 121.8 | 121.8 | 4923850 | 11 | 40425.6979 | 24.7367
819 | 819 | CL2-433 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 18.616 | 19 | 1.505 | 2 | 1.1287 | 12.6 | 12.6 | 1943850 | 3 | 154273.8095 | 6.482
820 | 820 | CL2-434 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 16.54 | 17 | 6.782 | 2 | 5.0865 | 63 | 63 | 4502230 | 11 | 71463.9683 | 13.9931
821 | 821 | CL2-435 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 23.484 | 24 | 1.556 | 2 | 1.167 | 12.6 | 12.6 | 2681270 | 7 | 212799.2063 | 4.6993
822 | 822 | CL2-436 | MAYO | MAYO | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 21.148 | 22 | 3.306 | 2 | 2.4795 | 29.4 | 29.4 | 2302050 | 5 | 78301.0204 | 12.7712
823 | 823 | CL2-437 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 25.893 | 26 | 0.891 | 2 | 0.66825 | 8.4 | 8.4 | 2786670 | 7 | 331746.4286 | 3.0144
824 | 824 | CL2-438 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 28.367 | 29 | 8.563 | 2 | 6.4223 | 79.8 | 79.8 | 7031950 | 11 | 88119.6742 | 11.3482
825 | 825 | CL2-439 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 25.089 | 26 | 2.738 | 2 | 2.0535 | 25.2 | 25.2 | 4263430 | 9 | 169183.7302 | 5.9107
826 | 826 | CL2-440 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 30.995 | 31 | 1.41 | 2 | 1.0575 | 12.6 | 12.6 | 3050170 | 7 | 242076.9841 | 4.1309
827 | 827 | CL2-441 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.695 | 8 | 3.787 | 2 | 2.8403 | 33.6 | 33.6 | 1237870 | 6 | 36841.369 | 27.1434
828 | 828 | CL2-442 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.325 | 9 | 0.822 | 2 | 0.6165 | 8.4 | 8.4 | 1379800 | 2 | 164261.9048 | 6.0878
829 | 829 | CL2-443 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.476 | 10 | 1.059 | 2 | 0.79425 | 8.4 | 8.4 | 1432500 | 2 | 170535.7143 | 5.8639
830 | 830 | CL2-444 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.615 | 8 | 0.557 | 2 | 0.557 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
831 | 831 | CL2-445 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.35 | 6 | 1.76 | 2 | 1.32 | 12.6 | 12.6 | 769410 | 4 | 61064.2857 | 16.3762
832 | 832 | CL2-446 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.822 | 4 | 0.414 | 2 | 0.414 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
833 | 833 | CL2-447 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.532 | 4 | 6.396 | 2 | 4.797 | 58.8 | 58.8 | 1761700 | 11 | 29960.8844 | 33.3769
834 | 834 | CL2-448 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.041 | 12 | 0.318 | 2 | 0.318 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
835 | 835 | CL2-449 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.997 | 13 | 1.717 | 2 | 1.2877 | 12.6 | 12.6 | 1627650 | 3 | 129178.5714 | 7.7412
836 | 836 | CL2-450 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.216 | 11 | 23.799 | 2 | 17.8492 | 218.4 | 218.4 | 9068760 | 13 | 41523.6264 | 24.0827
837 | 837 | CL2-451 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.07 | 14 | 3.951 | 2 | 2.9632 | 33.6 | 33.6 | 1905430 | 6 | 56709.2262 | 17.6338
838 | 838 | CL2-452 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.914 | 8 | 3.146 | 2 | 2.3595 | 25.2 | 25.2 | 1058430 | 5 | 42001.1905 | 23.8088
839 | 839 | CL2-453 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 3.305 | 4 | 8.626 | 2 | 6.4695 | 79.8 | 79.8 | 1761700 | 11 | 22076.4411 | 45.2972
840 | 840 | CL2-454 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.038 | 11 | 10.877 | 2 | 8.1578 | 100.8 | 100.8 | 3237370 | 11 | 32116.7659 | 31.1364
841 | 841 | CL2-455 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.74 | 9 | 0.772 | 2 | 0.579 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
842 | 842 | CL2-456 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.907 | 6 | 36.21 | 2 | 27.1575 | 336 | 336 | 6397880 | 12 | 19041.3095 | 52.5174
843 | 843 | CL2-457 | MAYO | MAYO | SS-170 | Derrynadivva 38kV Substation | ESB Networks | 38000 | low | 38000 | 12.163 | 13 | 13.75 | 2 | 10.3125 | 126 | 126 | 5191820 | 13 | 41204.9206 | 24.2689
844 | 844 | CL2-458 | MAYO | MAYO | SS-317 | Newport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.974 | 12 | 5.964 | 2 | 4.473 | 54.6 | 54.6 | 3448180 | 11 | 63153.4799 | 15.8344
845 | 845 | CL2-459 | MAYO | MAYO | SS-317 | Newport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.521 | 10 | 3.132 | 2 | 2.349 | 25.2 | 25.2 | 1236090 | 5 | 49051.1905 | 20.3869
846 | 846 | CL2-460 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 12.335 | 13 | 4.208 | 2 | 3.156 | 37.8 | 37.8 | 3400230 | 10 | 89953.1746 | 11.1169
847 | 847 | CL2-461 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.302 | 5 | 0.437 | 2 | 0.437 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
848 | 848 | CL2-462 | MAYO | MAYO | SS-317 | Newport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.317 | 9 | 0.933 | 2 | 0.69975 | 8.4 | 8.4 | 1379800 | 2 | 164261.9048 | 6.0878
849 | 849 | CL2-463 | MAYO | MAYO | SS-317 | Newport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.864 | 12 | 1.173 | 2 | 0.87975 | 8.4 | 8.4 | 1537900 | 2 | 183083.3333 | 5.462
850 | 850 | CL2-464 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.931 | 6 | 4.211 | 2 | 3.1583 | 37.8 | 37.8 | 1015350 | 6 | 26861.1111 | 37.2285
851 | 851 | CL2-465 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.265 | 9 | 0.423 | 2 | 0.423 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
852 | 852 | CL2-466 | MAYO | MAYO | SS-498 | Belmullet 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.325 | 9 | 8.357 | 2 | 6.2677 | 75.6 | 75.6 | 2815750 | 11 | 37245.3704 | 26.849
853 | 853 | CL2-467 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.398 | 5 | 10.24 | 2 | 7.68 | 92.4 | 92.4 | 1972510 | 11 | 21347.5108 | 46.8439
854 | 854 | CL2-468 | MAYO | MAYO | SS-170 | Derrynadivva 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.75 | 4 | 2.651 | 2 | 1.9882 | 21 | 21 | 628870 | 4 | 29946.1905 | 33.3932
855 | 855 | CL2-469 | MAYO | MAYO | SS-317 | Newport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.862 | 5 | 3.095 | 2 | 2.3213 | 25.2 | 25.2 | 791940 | 5 | 31426.1905 | 31.8206
856 | 856 | CL2-470 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 16.685 | 17 | 5.317 | 2 | 3.9878 | 46.2 | 46.2 | 4502230 | 11 | 97450.8658 | 10.2616
857 | 857 | CL2-471 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.957 | 13 | 5.248 | 2 | 3.936 | 46.2 | 46.2 | 3658990 | 11 | 79198.9177 | 12.6264
858 | 858 | CL2-472 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 17.137 | 18 | 1.138 | 2 | 0.8535 | 8.4 | 8.4 | 1854100 | 2 | 220726.1905 | 4.5305
859 | 859 | CL2-473 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 19.07 | 20 | 1.675 | 2 | 1.2563 | 12.6 | 12.6 | 1996550 | 3 | 158456.3492 | 6.3109
860 | 860 | CL2-474 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 9.301 | 10 | 159.806 | 2 | 119.8545 | 1491 | 1491 | 42473340 | 999999999 | 28486.4789 | 35.1044
861 | 861 | CL2-475 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 16.595 | 17 | 4.189 | 2 | 3.1418 | 37.8 | 37.8 | 3845270 | 10 | 101726.7196 | 9.8303
862 | 862 | CL2-476 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.712 | 3 | 5.049 | 2 | 3.7868 | 46.2 | 46.2 | 1550890 | 11 | 33569.0476 | 29.7893
863 | 863 | CL2-477 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 19.323 | 20 | 2.882 | 2 | 2.1615 | 25.2 | 25.2 | 3730450 | 9 | 148033.7302 | 6.7552
864 | 864 | CL2-478 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.401 | 11 | 0.452 | 2 | 0.452 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
865 | 865 | CL2-479 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.639 | 8 | 0.668 | 2 | 0.501 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
866 | 866 | CL2-480 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.114 | 7 | 0.487 | 2 | 0.487 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
867 | 867 | CL2-481 | SLIGO | MAYO | SS-302 | Carrowleagh 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.405 | 5 | 51.771 | 2 | 38.8282 | 483 | 483 | 8456580 | 12 | 17508.4472 | 57.1153
868 | 868 | CL2-482 | SLIGO | SLIGO | SS-302 | Carrowleagh 38kV Substation | ESB Networks | 38000 | low | 38000 | 6.398 | 7 | 2.305 | 2 | 1.7288 | 21 | 21 | 839680 | 4 | 39984.7619 | 25.0095
869 | 869 | CL2-483 | SLIGO | SLIGO | SS-075 | Cunghill 110kV Substation | EirGrid | 110000 | 110000 | medium | 9.416 | 10 | 7.447 | 2 | 5.5853 | 67.2 | 67.2 | 3026560 | 11 | 45038.0952 | 22.2034
870 | 870 | CL2-484 | SLIGO | SLIGO | SS-075 | Cunghill 110kV Substation | EirGrid | 110000 | 110000 | medium | 7.276 | 8 | 6.104 | 2 | 4.578 | 54.6 | 54.6 | 2604940 | 11 | 47709.5238 | 20.9602
871 | 871 | CL2-485 | SLIGO | SLIGO | SS-075 | Cunghill 110kV Substation | EirGrid | 110000 | 110000 | medium | 10.159 | 11 | 1.568 | 2 | 1.176 | 12.6 | 12.6 | 1996170 | 7 | 158426.1905 | 6.3121
872 | 872 | CL2-486 | SLIGO | SLIGO | SS-075 | Cunghill 110kV Substation | EirGrid | 110000 | 110000 | medium | 8.513 | 9 | 0.41 | 2 | 0.41 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213
873 | 873 | CL2-487 | SLIGO | SLIGO | SS-074 | Tobercurry 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.784 | 9 | 0.503 | 2 | 0.503 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
874 | 874 | CL2-488 | SLIGO | SLIGO | SS-302 | Carrowleagh 38kV Substation | ESB Networks | 38000 | low | 38000 | 7.448 | 8 | 0.725 | 2 | 0.54375 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
875 | 875 | CL2-489 | SLIGO | SLIGO | SS-227 | Bundoran 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.552 | 12 | 0.733 | 2 | 0.54975 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
876 | 876 | CL2-490 | LEITRIM | LEITRIM | SS-227 | Bundoran 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.834 | 12 | 0.371 | 2 | 0.371 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
877 | 877 | CL2-491 | SLIGO | LEITRIM | SS-042 | Ballytivnan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 11.555 | 12 | 13.159 | 2 | 9.8693 | 121.8 | 121.8 | 3448180 | 11 | 28310.1806 | 35.323
878 | 878 | CL2-492 | SLIGO | SLIGO | SS-042 | Ballytivnan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.573 | 9 | 0.524 | 2 | 0.524 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
879 | 879 | CL2-493 | SLIGO | SLIGO | SS-042 | Ballytivnan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 10.85 | 11 | 0.288 | 2 | 0.288 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
880 | 880 | CL2-494 | SLIGO | SLIGO | SS-042 | Ballytivnan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.592 | 8 | 0.763 | 2 | 0.57225 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
881 | 881 | CL2-495 | SLIGO | SLIGO | SS-031 | Sligo 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 3.346 | 4 | 1.856 | 2 | 1.392 | 16.8 | 16.8 | 1875790 | 8 | 111654.1667 | 8.9562
882 | 882 | CL2-496 | SLIGO | SLIGO | SS-227 | Bundoran 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.34 | 14 | 0.414 | 2 | 0.414 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284
883 | 883 | CL2-497 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 9.054 | 10 | 2.989 | 2 | 2.2417 | 25.2 | 25.2 | 1236090 | 5 | 49051.1905 | 20.3869
884 | 884 | CL2-498 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 6.55 | 7 | 0.813 | 2 | 0.60975 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
885 | 885 | CL2-499 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 6.473 | 7 | 2.456 | 2 | 1.842 | 21 | 21 | 839680 | 4 | 39984.7619 | 25.0095
886 | 886 | CL2-500 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 12.155 | 13 | 2.956 | 2 | 2.217 | 25.2 | 25.2 | 1502580 | 5 | 59626.1905 | 16.7712
887 | 887 | CL2-501 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 12.862 | 13 | 1.308 | 2 | 0.981 | 8.4 | 8.4 | 1590600 | 2 | 189357.1429 | 5.281
888 | 888 | CL2-502 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 12.042 | 13 | 0.891 | 2 | 0.66825 | 8.4 | 8.4 | 1590600 | 2 | 189357.1429 | 5.281
889 | 889 | CL2-503 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 10.007 | 11 | 7.031 | 2 | 5.2732 | 63 | 63 | 3237370 | 11 | 51386.8254 | 19.4602
890 | 890 | CL2-504 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 9.795 | 10 | 2.469 | 2 | 1.8518 | 21 | 21 | 1050490 | 4 | 50023.3333 | 19.9907
891 | 891 | CL2-505 | DONEGAL | DONEGAL | SS-090 | Corkermore 38kV Substation | ESB Networks | 38000 | low | 38000 | 5.981 | 6 | 0.395 | 2 | 0.395 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
892 | 892 | CL2-506 | DONEGAL | DONEGAL | SS-090 | Corkermore 38kV Substation | ESB Networks | 38000 | low | 38000 | 5.979 | 6 | 1.277 | 2 | 0.95775 | 8.4 | 8.4 | 769410 | 4 | 91596.4286 | 10.9175
893 | 893 | CL2-507 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 4.969 | 5 | 18.342 | 2 | 13.7565 | 168 | 168 | 2818860 | 12 | 16778.9286 | 59.5986
895 | 895 | CL2-509 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 4.561 | 5 | 4.409 | 2 | 3.3068 | 37.8 | 37.8 | 2510150 | 10 | 66406.0847 | 15.0589
896 | 896 | CL2-510 | DONEGAL | DONEGAL | SS-089 | Loughderryduff 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.763 | 3 | 0.754 | 2 | 0.5655 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
897 | 897 | CL2-511 | DONEGAL | DONEGAL | SS-089 | Loughderryduff 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.216 | 3 | 2.367 | 2 | 1.7752 | 21 | 21 | 558600 | 4 | 26600 | 37.594
898 | 898 | CL2-512 | DONEGAL | DONEGAL | SS-089 | Loughderryduff 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.317 | 4 | 2.994 | 2 | 2.2455 | 25.2 | 25.2 | 703110 | 5 | 27901.1905 | 35.8408
899 | 899 | CL2-513 | DONEGAL | DONEGAL | SS-090 | Corkermore 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.749 | 4 | 0.387 | 2 | 0.387 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
900 | 900 | CL2-514 | DONEGAL | DONEGAL | SS-138 | Creeslough 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.386 | 8 | 0.645 | 2 | 0.48375 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
901 | 901 | CL2-515 | DONEGAL | DONEGAL | SS-610 | Milford (North) 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.811 | 10 | 0.503 | 2 | 0.503 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
902 | 902 | CL2-516 | DONEGAL | DONEGAL | SS-119 | Drumlough Hill (1) 38kV Substation | ESB Networks | 38000 | low | 38000 | 6.26 | 7 | 0.923 | 2 | 0.69225 | 8.4 | 8.4 | 839680 | 4 | 99961.9048 | 10.0038
903 | 903 | CL2-517 | DONEGAL | DONEGAL | SS-119 | Drumlough Hill (1) 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.36 | 4 | 3.142 | 2 | 2.3565 | 25.2 | 25.2 | 703110 | 5 | 27901.1905 | 35.8408
904 | 904 | CL2-518 | DONEGAL | DONEGAL | SS-272 | Carndonagh 38kV | ESB Networks | 38000 | 38000 | low | 8.796 | 9 | 1.285 | 2 | 0.96375 | 8.4 | 8.4 | 1379800 | 2 | 164261.9048 | 6.0878
905 | 905 | CL2-519 | DONEGAL | DONEGAL | SS-272 | Carndonagh 38kV | ESB Networks | 38000 | 38000 | low | 12.413 | 13 | 0.428 | 2 | 0.428 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718
906 | 906 | CL2-520 | DONEGAL | DONEGAL | SS-239 | Moville 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 3.779 | 4 | 1.344 | 2 | 1.008 | 8.4 | 8.4 | 628870 | 4 | 74865.4762 | 13.3573
907 | 907 | CL2-521 | DONEGAL | DONEGAL | SS-117 | Crockahenny 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.618 | 4 | 12.867 | 2 | 9.6502 | 117.6 | 117.6 | 1761700 | 11 | 14980.4422 | 66.7537
908 | 908 | CL2-522 | DONEGAL | DONEGAL | SS-118 | Sorne Hill 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 4.867 | 5 | 1.793 | 2 | 1.3447 | 12.6 | 12.6 | 1679970 | 7 | 133330.9524 | 7.5001
909 | 909 | CL2-523 | DONEGAL | DONEGAL | SS-125 | Drumlough Hill (2) 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.997 | 5 | 3.898 | 2 | 2.9235 | 33.6 | 33.6 | 904090 | 6 | 26907.4405 | 37.1644
910 | 910 | CL2-524 | DONEGAL | DONEGAL | SS-272 | Carndonagh 38kV | ESB Networks | 38000 | 38000 | low | 3.581 | 4 | 2.699 | 2 | 2.0242 | 21 | 21 | 628870 | 4 | 29946.1905 | 33.3932
911 | 911 | CL2-525 | DONEGAL | DONEGAL | SS-272 | Carndonagh 38kV | ESB Networks | 38000 | 38000 | low | 3.963 | 4 | 1.812 | 2 | 1.359 | 16.8 | 16.8 | 628870 | 4 | 37432.7381 | 26.7146
912 | 912 | CL2-526 | DONEGAL | DONEGAL | SS-689 |  | ESB Networks | 38000 |  |  | 3.007 | 4 | 3.248 | 2 | 2.436 | 29.4 | 29.4 | 703110 | 5 | 23915.3061 | 41.8142
913 | 913 | CL2-527 | DONEGAL | DONEGAL | SS-689 |  | ESB Networks | 38000 |  |  | 4.437 | 5 | 2.934 | 2 | 2.2005 | 25.2 | 25.2 | 791940 | 5 | 31426.1905 | 31.8206
914 | 914 | CL2-528 | DONEGAL | DONEGAL | SS-689 |  | ESB Networks | 38000 |  |  | 4.504 | 5 | 4.489 | 2 | 3.3667 | 37.8 | 37.8 | 904090 | 6 | 23917.7249 | 41.81
915 | 915 | CL2-529 | DONEGAL | DONEGAL | SS-689 |  | ESB Networks | 38000 |  |  | 1.533 | 2 | 1.435 | 2 | 1.0762 | 12.6 | 12.6 | 488330 | 4 | 38756.3492 | 25.8022
916 | 916 | CL2-530 | DONEGAL | DONEGAL | SS-689 |  | ESB Networks | 38000 |  |  | 3.465 | 4 | 5.323 | 2 | 3.9923 | 46.2 | 46.2 | 1761700 | 11 | 38132.0346 | 26.2247
917 | 917 | CL2-531 | DONEGAL | DONEGAL | SS-689 |  | ESB Networks | 38000 |  |  | 4.983 | 5 | 1.491 | 2 | 1.1183 | 12.6 | 12.6 | 699140 | 4 | 55487.3016 | 18.0221
918 | 918 | CL2-532 | DONEGAL | DONEGAL | SS-687 | Gweedore Wind Farm 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.545 | 4 | 0.84 | 2 | 0.63 | 8.4 | 8.4 | 628870 | 4 | 74865.4762 | 13.3573
919 | 919 | CL2-533 | DONEGAL | DONEGAL | SS-687 | Gweedore Wind Farm 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.401 | 5 | 2.551 | 2 | 1.9133 | 21 | 21 | 699140 | 4 | 33292.381 | 30.0369
920 | 920 | CL2-534 | DONEGAL | DONEGAL | SS-289 | Gweedore 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 2.179 | 3 | 2.11 | 2 | 1.5825 | 16.8 | 16.8 | 558600 | 4 | 33250 | 30.0752
921 | 921 | CL2-535 | DONEGAL | DONEGAL | SS-610 | Milford (North) 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.299 | 7 | 0.287 | 2 | 0.287 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
922 | 922 | CL2-536 | DONEGAL | DONEGAL | SS-610 | Milford (North) 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.896 | 5 | 0.622 | 2 | 0.4665 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
923 | 923 | CL2-537 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.387 | 8 | 0.474 | 2 | 0.474 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
924 | 924 | CL2-538 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.281 | 6 | 0.463 | 2 | 0.463 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
925 | 925 | CL2-539 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.054 | 9 | 0.312 | 2 | 0.312 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
926 | 926 | CL2-540 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.889 | 9 | 0.897 | 2 | 0.67275 | 8.4 | 8.4 | 1379800 | 2 | 164261.9048 | 6.0878
927 | 927 | CL2-541 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.507 | 9 | 0.832 | 2 | 0.624 | 8.4 | 8.4 | 1379800 | 2 | 164261.9048 | 6.0878
928 | 928 | CL2-542 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 20.452 | 21 | 0.389 | 2 | 0.389 | 4.2 | 4.2 | 1966840 | 1 | 468295.2381 | 2.1354
929 | 929 | CL2-543 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 17.134 | 18 | 1.083 | 2 | 0.81225 | 8.4 | 8.4 | 1854100 | 2 | 220726.1905 | 4.5305
930 | 930 | CL2-544 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 20.926 | 21 | 0.589 | 2 | 0.589 | 4.2 | 4.2 | 1966840 | 1 | 468295.2381 | 2.1354
931 | 931 | CL2-545 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 18.272 | 19 | 1.881 | 2 | 1.4107 | 16.8 | 16.8 | 1682920 | 4 | 100173.8095 | 9.9826
932 | 932 | CL2-546 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 13.482 | 14 | 0.579 | 2 | 0.579 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284
933 | 933 | CL2-547 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.018 | 5 | 0.564 | 2 | 0.564 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
934 | 934 | CL2-548 | KERRY | KERRY | SS-636 | Garranebane 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.46 | 12 | 0.605 | 2 | 0.605 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
935 | 935 | CL2-549 | SLIGO | SLIGO | SS-128 | Garvagh Glebe 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 4.232 | 5 | 2.734 | 2 | 2.0505 | 25.2 | 25.2 | 2398000 | 9 | 95158.7302 | 10.5088
936 | 936 | CL2-550 | SLIGO | LEITRIM | SS-128 | Garvagh Glebe 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 3.932 | 4 | 2.619 | 2 | 1.9643 | 21 | 21 | 1875790 | 8 | 89323.3333 | 11.1953
937 | 937 | CL2-551 | ROSCOMMON | SLIGO | SS-304 | Arigna 110kV Substation | EirGrid | 110000 | 110000 | 20000 | 5.774 | 6 | 1.88 | 2 | 1.41 | 16.8 | 16.8 | 2016330 | 8 | 120019.6429 | 8.332
938 | 938 | CL2-552 | WEXFORD | WEXFORD | SS-481 | Castledockrell 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 7.399 | 8 | 2.082 | 2 | 1.5615 | 16.8 | 16.8 | 2156870 | 8 | 128385.119 | 7.7891
939 | 939 | CL2-553 | CARLOW | CARLOW | SS-494 | Bunclody 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.802 | 10 | 3.337 | 2 | 2.5028 | 29.4 | 29.4 | 1236090 | 5 | 42043.8776 | 23.7847
940 | 940 | CL2-554 | CARLOW | CARLOW | SS-487 | Bagenalstown 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.734 | 12 | 0.537 | 2 | 0.537 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
941 | 941 | CL2-555 | CARLOW | CARLOW | SS-481 | Castledockrell 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 11.413 | 12 | 0.456 | 2 | 0.456 | 4.2 | 4.2 | 2048870 | 7 | 487826.1905 | 2.0499
942 | 942 | CL2-556 | CARLOW | WEXFORD | SS-481 | Castledockrell 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 9.519 | 10 | 4.49 | 2 | 3.3675 | 37.8 | 37.8 | 3066450 | 10 | 81123.0159 | 12.327
943 | 943 | CL2-557 | WICKLOW | WICKLOW | SS-222 | Poulaphouca 110kV Substation | EirGrid | 110000 | low | 110000 | 12.857 | 13 | 0.172 | 2 | 0.172 | 4.2 | 4.2 | 2101570 | 7 | 500373.8095 | 1.9985
944 | 944 | CL2-558 | WICKLOW | WICKLOW | SS-062 | Stratford 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 6.613 | 7 | 1.519 | 2 | 1.1392 | 12.6 | 12.6 | 1785370 | 7 | 141696.0317 | 7.0574
945 | 945 | CL2-559 | WICKLOW | WICKLOW | SS-062 | Stratford 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 7.608 | 8 | 3.499 | 2 | 2.6242 | 29.4 | 29.4 | 2664490 | 9 | 90628.9116 | 11.034
946 | 946 | CL2-560 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.807 | 7 | 2.474 | 2 | 1.8555 | 21 | 21 | 839680 | 4 | 39984.7619 | 25.0095
947 | 947 | CL2-561 | WICKLOW | WICKLOW | SS-062 | Stratford 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.588 | 9 | 1.55 | 2 | 1.1625 | 12.6 | 12.6 | 1890770 | 7 | 150061.1111 | 6.664
948 | 948 | CL2-562 | WICKLOW | WICKLOW | SS-062 | Stratford 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 6.829 | 7 | 0.64 | 2 | 0.48 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525
949 | 949 | CL2-563 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.118 | 9 | 5.919 | 2 | 4.4392 | 54.6 | 54.6 | 2815750 | 11 | 51570.5128 | 19.3909
950 | 950 | CL2-564 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.439 | 11 | 6.841 | 2 | 5.1307 | 63 | 63 | 3237370 | 11 | 51386.8254 | 19.4602
951 | 951 | CL2-565 | WICKLOW | WICKLOW | SS-699 | Ballycumber 38kV Substation | ESB Networks | 38000 | low | 38000 | 10.708 | 11 | 2.331 | 2 | 1.7483 | 21 | 21 | 1120760 | 4 | 53369.5238 | 18.7373
952 | 952 | CL2-566 | WICKLOW | WICKLOW | SS-699 | Ballycumber 38kV Substation | ESB Networks | 38000 | low | 38000 | 11.326 | 12 | 2.922 | 2 | 2.1915 | 25.2 | 25.2 | 1413750 | 5 | 56101.1905 | 17.8249
953 | 953 | CL2-567 | WICKLOW | WICKLOW | SS-062 | Stratford 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 10.335 | 11 | 0.6 | 2 | 0.6 | 4.2 | 4.2 | 1996170 | 7 | 475278.5714 | 2.104
954 | 954 | CL2-568 | WICKLOW | WICKLOW | SS-222 | Poulaphouca 110kV Substation | EirGrid | 110000 | low | 110000 | 13.099 | 14 | 3.656 | 2 | 2.742 | 33.6 | 33.6 | 3511490 | 10 | 104508.631 | 9.5686
955 | 955 | CL2-569 | WICKLOW | WICKLOW | SS-222 | Poulaphouca 110kV Substation | EirGrid | 110000 | low | 110000 | 9.239 | 10 | 1.742 | 2 | 1.3065 | 12.6 | 12.6 | 1943470 | 7 | 154243.6508 | 6.4832
956 | 956 | CL2-570 | WICKLOW | WICKLOW | SS-209 | Blessington 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.499 | 10 | 0.939 | 2 | 0.70425 | 8.4 | 8.4 | 1432500 | 2 | 170535.7143 | 5.8639
957 | 957 | CL2-571 | DUBLIN | DUBLIN | SS-018 | Old Bawn 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.663 | 9 | 1.216 | 2 | 0.912 | 8.4 | 8.4 | 1379800 | 2 | 164261.9048 | 6.0878
958 | 958 | CL2-572 | WICKLOW | WICKLOW | SS-570 | Kilcoole 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.873 | 14 | 0.866 | 2 | 0.6495 | 8.4 | 8.4 | 1643300 | 2 | 195630.9524 | 5.1117
959 | 959 | CL2-573 | WEXFORD | WICKLOW | SS-616 | Ballinvally 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 3.179 | 4 | 2.376 | 2 | 1.782 | 21 | 21 | 628870 | 4 | 29946.1905 | 33.3932
960 | 960 | CL2-574 | WICKLOW | WICKLOW | SS-616 | Ballinvally 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 2.41 | 3 | 0.773 | 2 | 0.57975 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
961 | 961 | CL2-575 | CORK | CORK | SS-261 | Milane Hill 38kV Station | ESB Networks | 38000 |  |  | 2.085 | 3 | 0.2 | 2 | 0.2 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
962 | 962 | CL2-576 | CORK | KERRY | SS-668 | Coomataggart 110 kV Substation | EirGrid | 110000 | low | 110000 | 5.555 | 6 | 5.051 | 2 | 3.7883 | 46.2 | 46.2 | 2183320 | 11 | 47258.0087 | 21.1604
963 | 963 | CL2-577 | KERRY | KERRY | SS-668 | Coomataggart 110 kV Substation | EirGrid | 110000 | low | 110000 | 2.323 | 3 | 7.915 | 2 | 5.9363 | 71.4 | 71.4 | 1550890 | 11 | 21721.1485 | 46.0381
964 | 964 | CL2-578 | CORK | CORK | SS-668 | Coomataggart 110 kV Substation | EirGrid | 110000 | low | 110000 | 2.107 | 3 | 1.287 | 2 | 0.96525 | 8.4 | 8.4 | 1574570 | 7 | 187448.8095 | 5.3348
965 | 965 | CL2-579 | CORK | KERRY | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.211 | 4 | 1.54 | 2 | 1.155 | 12.6 | 12.6 | 628870 | 4 | 49910.3175 | 20.0359
966 | 966 | CL2-580 | CORK | CORK | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.449 | 3 | 1.569 | 2 | 1.1767 | 12.6 | 12.6 | 558600 | 4 | 44333.3333 | 22.5564
967 | 967 | CL2-581 | CORK | CORK | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.953 | 5 | 6.746 | 2 | 5.0595 | 58.8 | 58.8 | 1972510 | 11 | 33546.0884 | 29.8097
968 | 968 | CL2-582 | KERRY | KERRY | SS-071 | Coomagearlahy Substation | EirGrid | 110000 | medium-low | 110000 | 1.84 | 2 | 0.8 | 2 | 0.6 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341
969 | 969 | CL2-583 | KERRY | KERRY | SS-071 | Coomagearlahy Substation | EirGrid | 110000 | medium-low | 110000 | 3.81 | 4 | 1.026 | 2 | 0.7695 | 8.4 | 8.4 | 1627270 | 7 | 193722.619 | 5.162
970 | 970 | CL2-584 | CORK | CORK | SS-070 | Glanlee 110kV Substation | EirGrid | 110000 | low | 110000 | 5.903 | 6 | 2.744 | 2 | 2.058 | 25.2 | 25.2 | 2486830 | 9 | 98683.7302 | 10.1334
971 | 971 | CL2-585 | CORK | KERRY | SS-668 | Coomataggart 110 kV Substation | EirGrid | 110000 | low | 110000 | 2.797 | 3 | 0.799 | 2 | 0.59925 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674
972 | 972 | CL2-586 | CORK | KERRY | SS-162 | Garrow 110kV Substation | EirGrid | 110000 | 38000 | 110000 | 6.116 | 7 | 9.38 | 2 | 7.035 | 84 | 84 | 2394130 | 11 | 28501.5476 | 35.0858
973 | 973 | CL2-587 | KERRY | KERRY | SS-072 | Clonkeen 110kV Substation | EirGrid | 110000 |  |  | 3.115 | 4 | 6.361 | 2 | 4.7707 | 58.8 | 58.8 | 1761700 | 11 | 29960.8844 | 33.3769
974 | 974 | CL2-588 | CORK | KERRY | SS-162 | Garrow 110kV Substation | EirGrid | 110000 | 38000 | 110000 | 5.282 | 6 | 7.26 | 2 | 5.445 | 67.2 | 67.2 | 2183320 | 11 | 32489.881 | 30.7788
975 | 975 | CL2-589 | CORK | CORK | SS-162 | Garrow 110kV Substation | EirGrid | 110000 | 38000 | 110000 | 2.505 | 3 | 1.42 | 2 | 1.065 | 12.6 | 12.6 | 1574570 | 7 | 124965.873 | 8.0022
976 | 976 | CL2-590 | CORK | CORK | SS-615 | Knockduff 110kv Substation | EirGrid | 110000 |  |  | 2.217 | 3 | 2.852 | 2 | 2.139 | 25.2 | 25.2 | 2220340 | 9 | 88108.7302 | 11.3496
977 | 977 | CL2-591 | CORK | CORK | SS-615 | Knockduff 110kv Substation | EirGrid | 110000 |  |  | 5.262 | 6 | 0.653 | 2 | 0.48975 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424
978 | 978 | CL2-592 | CORK | CORK | SS-394 | Kilberrihert 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.803 | 5 | 1.052 | 2 | 0.789 | 8.4 | 8.4 | 699140 | 4 | 83230.9524 | 12.0148
979 | 979 | CL2-593 | CORK | CORK | SS-615 | Knockduff 110kv Substation | EirGrid | 110000 |  |  | 6.156 | 7 | 0.531 | 2 | 0.531 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525
980 | 980 | CL2-594 | CORK | CORK | SS-096 | Boggeragh 110kV Substation | EirGrid | 110000 |  |  | 3.048 | 4 | 0.714 | 2 | 0.5355 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581
981 | 981 | CL2-595 | KERRY | KERRY | SS-387 | Coolcorcoran 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.706 | 7 | 0.695 | 2 | 0.52125 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
982 | 982 | CL2-596 | KILKENNY | LAOIS | SS-372 | Ballyconra 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.376 | 7 | 0.831 | 2 | 0.62325 | 8.4 | 8.4 | 839680 | 4 | 99961.9048 | 10.0038
983 | 983 | CL2-597 | CLARE | CLARE | SS-116 | Ardnacrusha 110kV Substation | EirGrid | 110000 | low | 110000 | 8.989 | 9 | 1.959 | 2 | 1.4693 | 16.8 | 16.8 | 2227140 | 8 | 132567.8571 | 7.5433
984 | 984 | CL2-598 | TIPPERARY | TIPPERARY | SS-645 | Toomevara 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.145 | 9 | 0.931 | 2 | 0.69825 | 8.4 | 8.4 | 1379800 | 2 | 164261.9048 | 6.0878
985 | 985 | CL2-599 | TIPPERARY | TIPPERARY | SS-540 | Templemore 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 6.733 | 7 | 1.102 | 2 | 0.8265 | 8.4 | 8.4 | 839680 | 4 | 99961.9048 | 10.0038
986 | 986 | CL2-600 | CLARE | CLARE | SS-155 | Booltiagh 110kV Substation | EirGrid | 110000 | low | 110000 | 4.293 | 5 | 2.98 | 2 | 2.235 | 25.2 | 25.2 | 2398000 | 9 | 95158.7302 | 10.5088
987 | 987 | CL2-601 | CLARE | CLARE | SS-700 | Letteragh 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.955 | 2 | 2.067 | 2 | 1.5503 | 16.8 | 16.8 | 488330 | 4 | 29067.2619 | 34.403
988 | 988 | CL2-602 | CLARE | CLARE | SS-700 | Letteragh 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.828 | 5 | 0.577 | 2 | 0.577 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
989 | 989 | CL2-603 | CLARE | CLARE | SS-700 | Letteragh 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.164 | 3 | 1.953 | 2 | 1.4647 | 16.8 | 16.8 | 558600 | 4 | 33250 | 30.0752
990 | 990 | CL2-604 | DONEGAL | DONEGAL | SS-289 | Gweedore 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 1.282 | 2 | 1.766 | 2 | 1.3245 | 12.6 | 12.6 | 488330 | 4 | 38756.3492 | 25.8022
991 | 991 | CL2-605 | DONEGAL | DONEGAL | SS-333 | Clady 38kV Substation | ESB Networks | 38000 |  |  | 4.944 | 5 | 0.706 | 2 | 0.5295 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
992 | 992 | CL2-606 | DONEGAL | DONEGAL | SS-195 | Cark 110kV Substation | EirGrid | 110000 | low | 110000 | 10.983 | 11 | 0.609 | 2 | 0.609 | 4.2 | 4.2 | 1996170 | 7 | 475278.5714 | 2.104
993 | 993 | CL2-607 | DONEGAL | DONEGAL | SS-195 | Cark 110kV Substation | EirGrid | 110000 | low | 110000 | 8.739 | 9 | 8.38 | 2 | 6.285 | 75.6 | 75.6 | 2815750 | 11 | 37245.3704 | 26.849
994 | 994 | CL2-608 | DONEGAL | DONEGAL | SS-196 | Culliagh 110kV Substation | EirGrid | 110000 | low | 110000 | 12.299 | 13 | 4.155 | 2 | 3.1162 | 37.8 | 37.8 | 3400230 | 10 | 89953.1746 | 11.1169
995 | 995 | CL2-609 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 6.119 | 7 | 8.275 | 2 | 6.2063 | 75.6 | 75.6 | 2394130 | 11 | 31668.3862 | 31.5772
996 | 996 | CL2-610 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 9.341 | 10 | 1.871 | 2 | 1.4032 | 16.8 | 16.8 | 2297410 | 8 | 136750.5952 | 7.3126
997 | 997 | CL2-611 | DONEGAL | DONEGAL | SS-686 | Dungloe 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.191 | 8 | 11.635 | 2 | 8.7263 | 105 | 105 | 2604940 | 11 | 24808.9524 | 40.308
998 | 998 | CL2-612 | DONEGAL | DONEGAL | SS-195 | Cark 110kV Substation | EirGrid | 110000 | low | 110000 | 3.781 | 4 | 5.213 | 2 | 3.9097 | 46.2 | 46.2 | 1761700 | 11 | 38132.0346 | 26.2247
999 | 999 | CL2-613 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 10.545 | 11 | 1.356 | 2 | 1.017 | 12.6 | 12.6 | 1996170 | 7 | 158426.1905 | 6.3121
1000 | 1000 | CL2-614 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 3.183 | 4 | 1.82 | 2 | 1.365 | 16.8 | 16.8 | 1875790 | 8 | 111654.1667 | 8.9562
1001 | 1001 | CL2-615 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 7.154 | 8 | 5.444 | 2 | 4.083 | 50.4 | 50.4 | 2604940 | 11 | 51685.3175 | 19.3479
1002 | 1002 | CL2-616 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.009 | 11 | 21.5 | 2 | 16.125 | 197.4 | 197.4 | 9068760 | 13 | 45941.0334 | 21.767
1003 | 1003 | CL2-617 | CAVAN | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.397 | 9 | 25.306 | 2 | 18.9795 | 235.2 | 235.2 | 8678360 | 12 | 36897.7891 | 27.1019
1004 | 1004 | CL2-618 | CAVAN | LEITRIM | SS-110 | Corraclassy 110kV Substation | EirGrid | 110000 |  |  | 8.632 | 9 | 22.242 | 2 | 16.6815 | 205.8 | 205.8 | 8678360 | 12 | 42168.9018 | 23.7142
1005 | 1005 | CL2-619 | LEITRIM | LEITRIM | SS-304 | Arigna 110kV Substation | EirGrid | 110000 | 110000 | 20000 | 7.203 | 8 | 13.323 | 2 | 9.9923 | 121.8 | 121.8 | 2604940 | 11 | 21387.0279 | 46.7573
1006 | 1006 | CL2-620 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.872 | 7 | 3.573 | 2 | 2.6797 | 29.4 | 29.4 | 969600 | 5 | 32979.5918 | 30.3218
1007 | 1007 | CL2-621 | SLIGO | MAYO | SS-078 | Glenree 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.174 | 6 | 9.971 | 2 | 7.4783 | 92.4 | 92.4 | 2183320 | 11 | 23629.0043 | 42.3209
1008 | 1008 | CL2-622 | MAYO | MAYO | SS-078 | Glenree 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 2.542 | 3 | 4.992 | 2 | 3.744 | 46.2 | 46.2 | 1550890 | 11 | 33569.0476 | 29.7893
1009 | 1009 | CL2-623 | MAYO | MAYO | SS-170 | Derrynadivva 38kV Substation | ESB Networks | 38000 | low | 38000 | 9.179 | 10 | 0.477 | 2 | 0.477 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
1010 | 1010 | CL2-624 | MAYO | MAYO | SS-170 | Derrynadivva 38kV Substation | ESB Networks | 38000 | low | 38000 | 6.597 | 7 | 3.673 | 2 | 2.7548 | 33.6 | 33.6 | 1126610 | 6 | 33530.0595 | 29.824
1011 | 1011 | CL2-625 | MAYO | MAYO | SS-234 | Crossmolina 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.711 | 11 | 0.922 | 2 | 0.6915 | 8.4 | 8.4 | 1485200 | 2 | 176809.5238 | 5.6558
1012 | 1012 | CL2-626 | MAYO | MAYO | SS-170 | Derrynadivva 38kV Substation | ESB Networks | 38000 | low | 38000 | 10.969 | 11 | 2.295 | 2 | 1.7212 | 21 | 21 | 1120760 | 4 | 53369.5238 | 18.7373
1013 | 1013 | CL2-627 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.839 | 9 | 7.082 | 2 | 5.3115 | 63 | 63 | 2815750 | 11 | 44694.4444 | 22.3741
1014 | 1014 | CL2-628 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.294 | 6 | 0.971 | 2 | 0.72825 | 8.4 | 8.4 | 1732670 | 7 | 206270.2381 | 4.848
1015 | 1015 | CL2-629 | DONEGAL | DONEGAL | SS-196 | Culliagh 110kV Substation | EirGrid | 110000 | low | 110000 | 2.449 | 3 | 10.191 | 2 | 7.6433 | 92.4 | 92.4 | 1550890 | 11 | 16784.5238 | 59.5787
1016 | 1016 | CL2-630 | DONEGAL | DONEGAL | SS-196 | Culliagh 110kV Substation | EirGrid | 110000 | low | 110000 | 6.576 | 7 | 6.468 | 2 | 4.851 | 58.8 | 58.8 | 2394130 | 11 | 40716.4966 | 24.5601
1017 | 1017 | CL2-631 | DONEGAL | DONEGAL | SS-688 | Clogher 110kV Substation | EirGrid | 110000 |  |  | 7.89 | 8 | 49.464 | 2 | 37.098 | 457.8 | 457.8 | 11877300 | 12 | 25944.2988 | 38.5441
1018 | 1018 | CL2-632 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 10.091 | 11 | 0.994 | 2 | 0.7455 | 8.4 | 8.4 | 1996170 | 7 | 237639.2857 | 4.2081
1019 | 1019 | CL2-633 | DONEGAL | DONEGAL | SS-102 | Binbane 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 6.975 | 7 | 1.135 | 2 | 0.85125 | 8.4 | 8.4 | 1785370 | 7 | 212544.0476 | 4.7049
1020 | 1020 | CL2-634 | DONEGAL | DONEGAL | SS-102 | Binbane 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 3.704 | 4 | 2.873 | 2 | 2.1547 | 25.2 | 25.2 | 2309170 | 9 | 91633.7302 | 10.913
1021 | 1021 | CL2-635 | DONEGAL | DONEGAL | SS-102 | Binbane 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 3.209 | 4 | 2.118 | 2 | 1.5885 | 16.8 | 16.8 | 1875790 | 8 | 111654.1667 | 8.9562
1022 | 1022 | CL2-636 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.028 | 6 | 3.464 | 2 | 2.598 | 29.4 | 29.4 | 2486830 | 9 | 84586.0544 | 11.8223
1023 | 1023 | CL2-637 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.277 | 9 | 1.055 | 2 | 0.79125 | 8.4 | 8.4 | 1890770 | 7 | 225091.6667 | 4.4426
1024 | 1024 | CL2-638 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 7.449 | 8 | 3.654 | 2 | 2.7405 | 33.6 | 33.6 | 2843930 | 10 | 84640.7738 | 11.8146
1025 | 1025 | CL2-639 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 10.709 | 11 | 2.414 | 2 | 1.8105 | 21 | 21 | 2367680 | 8 | 112746.6667 | 8.8694
1026 | 1026 | CL2-640 | DONEGAL | DONEGAL | SS-196 | Culliagh 110kV Substation | EirGrid | 110000 | low | 110000 | 10.584 | 11 | 0.63 | 2 | 0.4725 | 4.2 | 4.2 | 1996170 | 7 | 475278.5714 | 2.104
1027 | 1027 | CL2-641 | DONEGAL | DONEGAL | SS-572 | Glenties 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.042 | 4 | 0.771 | 2 | 0.57825 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1028 | 1028 | CL2-642 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 3.522 | 4 | 0.721 | 2 | 0.54075 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581
1029 | 1029 | CL2-643 | DONEGAL | DONEGAL | SS-196 | Culliagh 110kV Substation | EirGrid | 110000 | low | 110000 | 8.903 | 9 | 3.074 | 2 | 2.3055 | 25.2 | 25.2 | 2753320 | 9 | 109258.7302 | 9.1526
1030 | 1030 | CL2-644 | DONEGAL | DONEGAL | SS-196 | Culliagh 110kV Substation | EirGrid | 110000 | low | 110000 | 10.583 | 11 | 2.154 | 2 | 1.6155 | 16.8 | 16.8 | 2367680 | 8 | 140933.3333 | 7.0956
1031 | 1031 | CL2-645 | DONEGAL | DONEGAL | SS-690 | Stranrolar 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.448 | 9 | 2.303 | 2 | 1.7272 | 21 | 21 | 980220 | 4 | 46677.1429 | 21.4238
1032 | 1032 | CL2-646 | DONEGAL | DONEGAL | SS-015 | Letterkenny 110kV Station | EirGrid | 110000 | 110000 | 38000 | 3.357 | 4 | 0.839 | 2 | 0.62925 | 8.4 | 8.4 | 1627270 | 7 | 193722.619 | 5.162
1033 | 1033 | CL2-647 | GALWAY | GALWAY | SS-131 | Ros a Mh├¡l 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.701 | 3 | 19.051 | 2 | 14.2882 | 176.4 | 176.4 | 4117400 | 12 | 23341.2698 | 42.8426
1034 | 1034 | CL2-648 | GALWAY | GALWAY | SS-131 | Ros a Mh├¡l 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.584 | 5 | 1.251 | 2 | 0.93825 | 8.4 | 8.4 | 699140 | 4 | 83230.9524 | 12.0148
1035 | 1035 | CL2-649 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 4.45 | 5 | 1.682 | 2 | 1.2615 | 12.6 | 12.6 | 1679970 | 7 | 133330.9524 | 7.5001
1036 | 1036 | CL2-650 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 8.667 | 9 | 22.649 | 2 | 16.9868 | 210 | 210 | 8678360 | 12 | 41325.5238 | 24.1981
1037 | 1037 | CL2-651 | GALWAY | GALWAY | SS-662 | Cloosh 110kV Substation | EirGrid | 110000 | low | 110000 | 7.89 | 8 | 1.696 | 2 | 1.272 | 12.6 | 12.6 | 1838070 | 7 | 145878.5714 | 6.855
1038 | 1038 | CL2-652 | GALWAY | GALWAY | SS-623 | Uggool 110kV Substation | EirGrid | 110000 | 33000 | 110000 | 3.519 | 4 | 0.834 | 2 | 0.6255 | 8.4 | 8.4 | 1627270 | 7 | 193722.619 | 5.162
1039 | 1039 | CL2-653 | GALWAY | GALWAY | SS-662 | Cloosh 110kV Substation | EirGrid | 110000 | low | 110000 | 2.589 | 3 | 25.74 | 2 | 19.305 | 239.4 | 239.4 | 4117400 | 12 | 17198.8304 | 58.1435
1040 | 1040 | CL2-654 | GALWAY | GALWAY | SS-638 | Oughterard 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 3.329 | 4 | 1.197 | 2 | 0.89775 | 8.4 | 8.4 | 628870 | 4 | 74865.4762 | 13.3573
1041 | 1041 | CL2-655 | GALWAY | GALWAY | SS-130 | An Spid├®al 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.846 | 3 | 1.075 | 2 | 0.80625 | 8.4 | 8.4 | 558600 | 4 | 66500 | 15.0376
1042 | 1042 | CL2-656 | GALWAY | GALWAY | SS-130 | An Spid├®al 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.276 | 7 | 1.671 | 2 | 1.2532 | 12.6 | 12.6 | 839680 | 4 | 66641.2698 | 15.0057
1043 | 1043 | CL2-657 | GALWAY | GALWAY | SS-623 | Uggool 110kV Substation | EirGrid | 110000 | 33000 | 110000 | 3.961 | 4 | 1.133 | 2 | 0.84975 | 8.4 | 8.4 | 1627270 | 7 | 193722.619 | 5.162
1044 | 1044 | CL2-658 | GALWAY | GALWAY | SS-638 | Oughterard 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 4.181 | 5 | 1.274 | 2 | 0.9555 | 8.4 | 8.4 | 699140 | 4 | 83230.9524 | 12.0148
1045 | 1045 | CL2-659 | GALWAY | GALWAY | SS-638 | Oughterard 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 5.738 | 6 | 1.018 | 2 | 0.7635 | 8.4 | 8.4 | 769410 | 4 | 91596.4286 | 10.9175
1046 | 1046 | CL2-660 | GALWAY | GALWAY | SS-661 | Knockranny 110kV Substation | EirGrid | 110000 | low | 110000 | 5.111 | 6 | 0.555 | 2 | 0.555 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424
1047 | 1047 | CL2-661 | GALWAY | GALWAY | SS-038 | Salthill 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 7.797 | 8 | 3.942 | 2 | 2.9565 | 33.6 | 33.6 | 2843930 | 10 | 84640.7738 | 11.8146
1048 | 1048 | CL2-662 | GALWAY | GALWAY | SS-130 | An Spid├®al 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.215 | 5 | 1.224 | 2 | 0.918 | 8.4 | 8.4 | 699140 | 4 | 83230.9524 | 12.0148
1049 | 1049 | CL2-663 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.757 | 7 | 7.728 | 2 | 5.796 | 71.4 | 71.4 | 2394130 | 11 | 33531.2325 | 29.8229
1050 | 1050 | CL2-664 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 4.095 | 5 | 13.209 | 2 | 9.9067 | 121.8 | 121.8 | 1972510 | 11 | 16194.6634 | 61.7487
1051 | 1051 | CL2-665 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 7.269 | 8 | 0.419 | 2 | 0.419 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285
1052 | 1052 | CL2-666 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 10.046 | 11 | 0.154 | 2 | 0.154 | 4.2 | 4.2 | 1996170 | 7 | 475278.5714 | 2.104
1053 | 1053 | CL2-667 | MAYO | MAYO | SS-203 | Foxford 38kV Substation | ESB Networks | 38000 |  |  | 4.781 | 5 | 0.473 | 2 | 0.473 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1054 | 1054 | CL2-668 | KERRY | KERRY | SS-636 | Garranebane 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.964 | 5 | 1.081 | 2 | 0.81075 | 8.4 | 8.4 | 699140 | 4 | 83230.9524 | 12.0148
1055 | 1055 | CL2-669 | CORK | CORK | SS-192 | Ballylickey 110kV Station | EirGrid | 110000 | 110000 | 38000 | 7.155 | 8 | 0.423 | 2 | 0.423 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285
1056 | 1056 | CL2-670 | WATERFORD | WATERFORD | SS-507 | Kilcloher 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.327 | 10 | 1.745 | 2 | 1.3088 | 12.6 | 12.6 | 1469550 | 3 | 116630.9524 | 8.5741
1057 | 1057 | CL2-671 | TIPPERARY | WATERFORD | SS-455 | Ardfinnan 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.656 | 9 | 15.997 | 2 | 11.9977 | 147 | 147 | 4339180 | 12 | 29518.2313 | 33.8774
1058 | 1058 | CL2-672 | TIPPERARY | WATERFORD | SS-622 | Barranafaddock 38kV Substation | ESB Networks | 38000 | low | 38000 | 9.054 | 10 | 14.646 | 2 | 10.9845 | 134.4 | 134.4 | 4719260 | 12 | 35113.5417 | 28.479
1059 | 1059 | CL2-673 | WATERFORD | WATERFORD | SS-659 | Spa Road 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 9.227 | 10 | 27.254 | 2 | 20.4405 | 252 | 252 | 9438520 | 12 | 37454.4444 | 26.6991
1060 | 1060 | CL2-674 | WATERFORD | WATERFORD | SS-505 | Kilmacthomas 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.714 | 11 | 9.238 | 2 | 6.9285 | 84 | 84 | 3237370 | 11 | 38540.119 | 25.947
1061 | 1061 | CL2-675 | WATERFORD | WATERFORD | SS-205 | Dungarvan 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.189 | 9 | 2.043 | 2 | 1.5323 | 16.8 | 16.8 | 2227140 | 8 | 132567.8571 | 7.5433
1062 | 1062 | CL2-676 | WATERFORD | WATERFORD | SS-354 | Twomilebridge 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.045 | 5 | 0.938 | 2 | 0.7035 | 8.4 | 8.4 | 699140 | 4 | 83230.9524 | 12.0148
1063 | 1063 | CL2-677 | WATERFORD | WATERFORD | SS-205 | Dungarvan 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.544 | 6 | 1.893 | 2 | 1.4198 | 16.8 | 16.8 | 2016330 | 8 | 120019.6429 | 8.332
1064 | 1064 | CL2-678 | CORK | LIMERICK | SS-695 | Castlepook 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 2.769 | 3 | 3.638 | 2 | 2.7285 | 33.6 | 33.6 | 681570 | 6 | 20284.8214 | 49.2979
1065 | 1065 | CL2-679 | LIMERICK | LIMERICK | SS-695 | Castlepook 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 3.413 | 4 | 5.623 | 2 | 4.2172 | 50.4 | 50.4 | 1761700 | 11 | 34954.3651 | 28.6087
1066 | 1066 | CL2-680 | LIMERICK | LIMERICK | SS-257 | Kilshanny 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.997 | 9 | 0.988 | 2 | 0.741 | 8.4 | 8.4 | 1379800 | 2 | 164261.9048 | 6.0878
1067 | 1067 | CL2-681 | TIPPERARY | LIMERICK | SS-585 | Kilross Road 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.774 | 12 | 34.698 | 2 | 26.0235 | 323.4 | 323.4 | 9726200 | 13 | 30074.8299 | 33.2504
1068 | 1068 | CL2-682 | CORK | CORK | SS-583 | Castletownroche 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.658 | 6 | 8.344 | 2 | 6.258 | 75.6 | 75.6 | 2183320 | 11 | 28879.8942 | 34.6262
1069 | 1069 | CL2-683 | CARLOW | WEXFORD | SS-492 | Graigue 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.1 | 11 | 8.837 | 2 | 6.6277 | 79.8 | 79.8 | 3237370 | 11 | 40568.5464 | 24.6496
1070 | 1070 | CL2-684 | TIPPERARY | TIPPERARY | SS-645 | Toomevara 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.419 | 9 | 1.49 | 2 | 1.1175 | 12.6 | 12.6 | 1416850 | 3 | 112448.4127 | 8.893
1071 | 1071 | CL2-685 | CORK | CORK | SS-263 | Lake 38kV Station | ESB Networks | 38000 | 38000 | low | 9.744 | 10 | 0.921 | 2 | 0.69075 | 8.4 | 8.4 | 1432500 | 2 | 170535.7143 | 5.8639
1072 | 1072 | CL2-686 | KILKENNY | KILKENNY | SS-016 | Portlaw 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.135 | 10 | 1.193 | 2 | 0.89475 | 8.4 | 8.4 | 1432500 | 2 | 170535.7143 | 5.8639
1073 | 1073 | CL2-687 | CORK | CORK | SS-355 | Carrigcannon 38kV Substation | ESB Networks | 38000 | low | 38000 | 7.44 | 8 | 6.798 | 2 | 5.0985 | 63 | 63 | 2604940 | 11 | 41348.254 | 24.1848
1074 | 1074 | CL2-688 | KERRY | KERRY | SS-555 | Ballybunion 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.158 | 8 | 0.47 | 2 | 0.47 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1075 | 1075 | CL2-689 | KERRY | KERRY | SS-555 | Ballybunion 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.436 | 7 | 0.55 | 2 | 0.55 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1076 | 1076 | CL2-690 | TIPPERARY | TIPPERARY | SS-295 | Doon 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.204 | 9 | 8.931 | 2 | 6.6982 | 79.8 | 79.8 | 2815750 | 11 | 35285.0877 | 28.3406
1077 | 1077 | CL2-691 | WICKLOW | WICKLOW | SS-037 | Ballybeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.761 | 6 | 0.362 | 2 | 0.362 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424
1078 | 1078 | CL2-692 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 17.052 | 18 | 6.733 | 2 | 5.0497 | 58.8 | 58.8 | 4713040 | 11 | 80153.7415 | 12.476
1079 | 1079 | CL2-693 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.556 | 16 | 2.749 | 2 | 2.0617 | 25.2 | 25.2 | 1769070 | 5 | 70201.1905 | 14.2448
1080 | 1080 | CL2-694 | CORK | CORK | SS-668 | Coomataggart 110 kV Substation | EirGrid | 110000 | low | 110000 | 10.289 | 11 | 1.232 | 2 | 0.924 | 8.4 | 8.4 | 1996170 | 7 | 237639.2857 | 4.2081
1081 | 1081 | CL2-695 | CORK | CORK | SS-433 | Lee Bridge 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.377 | 13 | 0.49 | 2 | 0.49 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718
1082 | 1082 | CL2-696 | KILKENNY | KILKENNY | SS-538 | Galmoy 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.689 | 10 | 2.129 | 2 | 1.5968 | 16.8 | 16.8 | 1050490 | 4 | 62529.1667 | 15.9925
1083 | 1083 | CL2-697 | WICKLOW | WICKLOW | SS-699 | Ballycumber 38kV Substation | ESB Networks | 38000 | low | 38000 | 5.519 | 6 | 1.628 | 2 | 1.221 | 12.6 | 12.6 | 769410 | 4 | 61064.2857 | 16.3762
1084 | 1084 | CL2-698 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 3.63 | 4 | 1.1 | 2 | 0.825 | 8.4 | 8.4 | 628870 | 4 | 74865.4762 | 13.3573
1085 | 1085 | CL2-699 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.717 | 6 | 0.573 | 2 | 0.573 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1086 | 1086 | CL2-700 | CLARE | CLARE | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.867 | 15 | 0.84 | 2 | 0.63 | 8.4 | 8.4 | 1696000 | 2 | 201904.7619 | 4.9528
1087 | 1087 | CL2-701 | GALWAY | GALWAY | SS-103 | Claregalway 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.009 | 7 | 0.541 | 2 | 0.541 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1088 | 1088 | CL2-702 | KERRY | KERRY | SS-189 | Knockearagh 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.998 | 6 | 0.826 | 2 | 0.6195 | 8.4 | 8.4 | 1732670 | 7 | 206270.2381 | 4.848
1089 | 1089 | CL2-703 | WEXFORD | WEXFORD | SS-616 | Ballinvally 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 7.37 | 8 | 0.574 | 2 | 0.574 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1090 | 1090 | CL2-704 | CORK | CORK | SS-261 | Milane Hill 38kV Station | ESB Networks | 38000 |  |  | 6.406 | 7 | 3.164 | 2 | 2.373 | 29.4 | 29.4 | 969600 | 5 | 32979.5918 | 30.3218
1091 | 1091 | CL2-705 | CORK | CORK | SS-261 | Milane Hill 38kV Station | ESB Networks | 38000 |  |  | 5.394 | 6 | 1.154 | 2 | 0.8655 | 8.4 | 8.4 | 769410 | 4 | 91596.4286 | 10.9175
1092 | 1092 | CL2-706 | CLARE | CLARE | SS-155 | Booltiagh 110kV Substation | EirGrid | 110000 | low | 110000 | 7.941 | 8 | 0.66 | 2 | 0.495 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285
1093 | 1093 | CL2-707 | CLARE | CLARE | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.93 | 11 | 2.713 | 2 | 2.0347 | 25.2 | 25.2 | 1324920 | 5 | 52576.1905 | 19.02
1094 | 1094 | CL2-708 | GALWAY | CLARE | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.833 | 14 | 10.364 | 2 | 7.773 | 96.6 | 96.6 | 3869800 | 11 | 40060.0414 | 24.9625
1095 | 1095 | CL2-709 | CLARE | CLARE | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.536 | 15 | 1.257 | 2 | 0.94275 | 8.4 | 8.4 | 1696000 | 2 | 201904.7619 | 4.9528
1096 | 1096 | CL2-710 | CLARE | CLARE | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.802 | 15 | 0.588 | 2 | 0.588 | 4.2 | 4.2 | 1650640 | 1 | 393009.5238 | 2.5445
1097 | 1097 | CL2-711 | CLARE | CLARE | SS-595 | Kilkee 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.438 | 7 | 0.956 | 2 | 0.717 | 8.4 | 8.4 | 839680 | 4 | 99961.9048 | 10.0038
1098 | 1098 | CL2-712 | CORK | CORK | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.471 | 5 | 0.35 | 2 | 0.35 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1099 | 1099 | CL2-713 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 16.505 | 17 | 0.648 | 2 | 0.486 | 4.2 | 4.2 | 1756040 | 1 | 418104.7619 | 2.3917
1100 | 1100 | CL2-714 | KILKENNY | KILKENNY | SS-489 | Ballyhale 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.31 | 7 | 2.014 | 2 | 1.5105 | 16.8 | 16.8 | 839680 | 4 | 49980.9524 | 20.0076
1101 | 1101 | CL2-715 | KILKENNY | KILKENNY | SS-492 | Graigue 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.463 | 5 | 6.231 | 2 | 4.6732 | 54.6 | 54.6 | 1972510 | 11 | 36126.5568 | 27.6805
1102 | 1102 | CL2-716 | TIPPERARY | TIPPERARY | SS-692 | Hollyford 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.453 | 4 | 1.807 | 2 | 1.3552 | 16.8 | 16.8 | 628870 | 4 | 37432.7381 | 26.7146
1103 | 1103 | CL2-717 | WICKLOW | WICKLOW | SS-591 | Shillelagh 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.626 | 4 | 0.83 | 2 | 0.6225 | 8.4 | 8.4 | 628870 | 4 | 74865.4762 | 13.3573
1104 | 1104 | CL2-718 | CLARE | CLARE | SS-503 | Scariff 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.134 | 9 | 11.769 | 2 | 8.8268 | 109.2 | 109.2 | 2815750 | 11 | 25785.2564 | 38.7819
1105 | 1105 | CL2-719 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 19.151 | 20 | 0.572 | 2 | 0.572 | 4.2 | 4.2 | 1914140 | 1 | 455747.619 | 2.1942
1106 | 1106 | CL2-720 | WICKLOW | WICKLOW | SS-699 | Ballycumber 38kV Substation | ESB Networks | 38000 | low | 38000 | 5.256 | 6 | 1.15 | 2 | 0.8625 | 8.4 | 8.4 | 769410 | 4 | 91596.4286 | 10.9175
1107 | 1107 | CL2-721 | WICKLOW | WICKLOW | SS-699 | Ballycumber 38kV Substation | ESB Networks | 38000 | low | 38000 | 7.51 | 8 | 1.344 | 2 | 1.008 | 8.4 | 8.4 | 909950 | 4 | 108327.381 | 9.2313
1108 | 1108 | CL2-722 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.758 | 9 | 0.803 | 2 | 0.60225 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1109 | 1109 | CL2-723 | CORK | CORK | SS-032 | Mallow 110kV Substation | EirGrid | 110000 |  |  | 5.929 | 6 | 0.979 | 2 | 0.73425 | 8.4 | 8.4 | 1732670 | 7 | 206270.2381 | 4.848
1110 | 1110 | CL2-724 | LAOIS | LAOIS | SS-034 | Athy 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 9.25 | 10 | 0.67 | 2 | 0.5025 | 4.2 | 4.2 | 1943470 | 7 | 462730.9524 | 2.1611
1111 | 1111 | CL2-725 | TIPPERARY | TIPPERARY | SS-483 | Birdhill 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.118 | 9 | 2.535 | 2 | 1.9013 | 21 | 21 | 980220 | 4 | 46677.1429 | 21.4238
1112 | 1112 | CL2-726 | WICKLOW | WICKLOW | SS-602 | Avoca 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.08 | 8 | 1.021 | 2 | 0.76575 | 8.4 | 8.4 | 909950 | 4 | 108327.381 | 9.2313
1113 | 1113 | CL2-727 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.398 | 12 | 1.42 | 2 | 1.065 | 12.6 | 12.6 | 1574950 | 3 | 124996.0317 | 8.0003
1114 | 1114 | CL2-728 | CORK | CORK | SS-192 | Ballylickey 110kV Station | EirGrid | 110000 | 110000 | 38000 | 6.624 | 7 | 1.049 | 2 | 0.78675 | 8.4 | 8.4 | 1785370 | 7 | 212544.0476 | 4.7049
1115 | 1115 | CL2-729 | DONEGAL | DONEGAL | SS-087 | Cliff 110kV Substation | EirGrid | 110000 | low | 110000 | 8.224 | 9 | 0.9 | 2 | 0.675 | 8.4 | 8.4 | 1890770 | 7 | 225091.6667 | 4.4426
1116 | 1116 | CL2-730 | CLARE | CLARE | SS-669 | 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.823 | 4 | 0.771 | 2 | 0.57825 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1117 | 1117 | CL2-731 | DONEGAL | DONEGAL | SS-138 | Creeslough 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.05 | 8 | 5.658 | 2 | 4.2435 | 50.4 | 50.4 | 2604940 | 11 | 51685.3175 | 19.3479
1118 | 1118 | CL2-732 | DONEGAL | DONEGAL | SS-610 | Milford (North) 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.318 | 7 | 4.809 | 2 | 3.6067 | 42 | 42 | 1126610 | 6 | 26824.0476 | 37.28
1119 | 1119 | CL2-733 | DONEGAL | DONEGAL | SS-610 | Milford (North) 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.616 | 9 | 0.667 | 2 | 0.50025 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1120 | 1120 | CL2-734 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.84 | 9 | 7.362 | 2 | 5.5215 | 67.2 | 67.2 | 2815750 | 11 | 41901.0417 | 23.8658
1121 | 1121 | CL2-735 | GALWAY | GALWAY | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 9.976 | 10 | 0.556 | 2 | 0.556 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
1122 | 1122 | CL2-736 | MAYO | MAYO | SS-234 | Crossmolina 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.066 | 11 | 2.484 | 2 | 1.863 | 21 | 21 | 1120760 | 4 | 53369.5238 | 18.7373
1123 | 1123 | CL2-737 | DONEGAL | DONEGAL | SS-272 | Carndonagh 38kV | ESB Networks | 38000 | 38000 | low | 9.683 | 10 | 0.416 | 2 | 0.416 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
1124 | 1124 | CL2-738 | MAYO | MAYO | SS-710 | Tawnaghmore 110kV Substation | EirGrid | 110000 | low | 110000 | 9.218 | 10 | 1.607 | 2 | 1.2052 | 12.6 | 12.6 | 1943470 | 7 | 154243.6508 | 6.4832
1125 | 1125 | CL2-739 | MAYO | MAYO | SS-317 | Newport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.382 | 6 | 1.657 | 2 | 1.2428 | 12.6 | 12.6 | 769410 | 4 | 61064.2857 | 16.3762
1126 | 1126 | CL2-740 | MAYO | MAYO | SS-710 | Tawnaghmore 110kV Substation | EirGrid | 110000 | low | 110000 | 9.807 | 10 | 0.62 | 2 | 0.465 | 4.2 | 4.2 | 1943470 | 7 | 462730.9524 | 2.1611
1127 | 1127 | CL2-741 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.17 | 10 | 3.564 | 2 | 2.673 | 29.4 | 29.4 | 1236090 | 5 | 42043.8776 | 23.7847
1128 | 1128 | CL2-742 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 2.84 | 3 | 2.34 | 2 | 1.755 | 21 | 21 | 558600 | 4 | 26600 | 37.594
1129 | 1129 | CL2-743 | MAYO | MAYO | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 11.439 | 12 | 0.471 | 2 | 0.471 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
1130 | 1130 | CL2-744 | MAYO | MAYO | SS-431 | Knockaphunta 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.177 | 11 | 0.772 | 2 | 0.579 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
1131 | 1131 | CL2-745 | SLIGO | SLIGO | SS-206 | Boyle 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 9.975 | 10 | 1.502 | 2 | 1.1265 | 12.6 | 12.6 | 1469550 | 3 | 116630.9524 | 8.5741
1132 | 1132 | CL2-746 | SLIGO | SLIGO | SS-068 | Ballymote 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.068 | 9 | 1.061 | 2 | 0.79575 | 8.4 | 8.4 | 1379800 | 2 | 164261.9048 | 6.0878
1133 | 1133 | CL2-747 | MAYO | MAYO | SS-203 | Foxford 38kV Substation | ESB Networks | 38000 |  |  | 6.805 | 7 | 1.252 | 2 | 0.939 | 8.4 | 8.4 | 839680 | 4 | 99961.9048 | 10.0038
1134 | 1134 | CL2-748 | ROSCOMMON | SLIGO | SS-206 | Boyle 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 4.797 | 5 | 0.311 | 2 | 0.311 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1135 | 1135 | CL2-749 | SLIGO | LEITRIM | SS-042 | Ballytivnan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.937 | 9 | 8.012 | 2 | 6.009 | 71.4 | 71.4 | 2815750 | 11 | 39436.2745 | 25.3574
1136 | 1136 | CL2-750 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.145 | 5 | 1.036 | 2 | 0.777 | 8.4 | 8.4 | 699140 | 4 | 83230.9524 | 12.0148
1137 | 1137 | CL2-751 | SLIGO | SLIGO | SS-031 | Sligo 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.786 | 6 | 2.057 | 2 | 1.5427 | 16.8 | 16.8 | 2016330 | 8 | 120019.6429 | 8.332
1138 | 1138 | CL2-752 | MAYO | MAYO | SS-173 | Charlestown 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.582 | 4 | 0.339 | 2 | 0.339 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1139 | 1139 | CL2-753 | GALWAY | GALWAY | SS-109 | Cloon 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 12.167 | 13 | 0.426 | 2 | 0.426 | 4.2 | 4.2 | 2101570 | 7 | 500373.8095 | 1.9985
1140 | 1140 | CL2-754 | WESTMEATH | WESTMEATH | SS-246 | Loughanalla 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.019 | 9 | 0.8 | 2 | 0.6 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1141 | 1141 | CL2-755 | GALWAY | GALWAY | SS-598 | Glennamaddy 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.377 | 6 | 1.208 | 2 | 0.906 | 8.4 | 8.4 | 769410 | 4 | 91596.4286 | 10.9175
1142 | 1142 | CL2-756 | GALWAY | GALWAY | SS-598 | Glennamaddy 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.704 | 9 | 1.645 | 2 | 1.2338 | 12.6 | 12.6 | 1416850 | 3 | 112448.4127 | 8.893
1143 | 1143 | CL2-757 | GALWAY | GALWAY | SS-549 | Tuam North 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.078 | 9 | 0.562 | 2 | 0.562 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1144 | 1144 | CL2-758 | MAYO | MAYO | SS-431 | Knockaphunta 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.1 | 13 | 0.475 | 2 | 0.475 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718
1145 | 1145 | CL2-759 | MAYO | MAYO | SS-640 | Ballinrobe 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.264 | 12 | 0.182 | 2 | 0.182 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
1146 | 1146 | CL2-760 | DONEGAL | DONEGAL | SS-574 | Convoy 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.32 | 6 | 0.995 | 2 | 0.74625 | 8.4 | 8.4 | 769410 | 4 | 91596.4286 | 10.9175
1147 | 1147 | CL2-761 | DONEGAL | DONEGAL | SS-686 | Dungloe 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.467 | 4 | 0.775 | 2 | 0.58125 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1148 | 1148 | CL2-762 | DONEGAL | DONEGAL | SS-139 | Gortlee 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.034 | 7 | 0.65 | 2 | 0.4875 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1149 | 1149 | CL2-763 | DONEGAL | DONEGAL | SS-272 | Carndonagh 38kV | ESB Networks | 38000 | 38000 | low | 7.54 | 8 | 18.38 | 2 | 13.785 | 168 | 168 | 3959100 | 12 | 23566.0714 | 42.4339
1150 | 1150 | CL2-764 | DONEGAL | DONEGAL | SS-239 | Moville 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.28 | 9 | 0.229 | 2 | 0.229 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1151 | 1151 | CL2-765 | DONEGAL | DONEGAL | SS-138 | Creeslough 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.879 | 4 | 0.765 | 2 | 0.57375 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1152 | 1152 | CL2-766 | MAYO | MAYO | SS-419 | Bangor 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.391 | 3 | 0.399 | 2 | 0.399 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
1153 | 1153 | CL2-767 | MAYO | MAYO | SS-317 | Newport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.382 | 12 | 0.148 | 2 | 0.148 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
1154 | 1154 | CL3-001 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 13.336 | 14 | 0.147 | 3 | 0.147 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284
1155 | 1155 | CL3-002 | WICKLOW | WICKLOW | SS-597 | Kilmartin 38kV Substation | ESB Networks | 38000 | 38000 | low | 1.523 | 2 | 0.299 | 3 | 0.299 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007
1156 | 1156 | CL3-003 | WEXFORD | WEXFORD | SS-493 | Enniscorthy 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.388 | 7 | 0.165 | 3 | 0.165 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1158 | 1158 | CL3-005 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 8.094 | 9 | 0.146 | 3 | 0.146 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1159 | 1159 | CL3-006 | KERRY | KERRY | SS-321 | Milltown 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.111 | 8 | 0.202 | 3 | 0.202 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1160 | 1160 | CL3-007 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.183 | 7 | 0.101 | 3 | 0.101 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1161 | 1161 | CL3-008 | LIMERICK | LIMERICK | SS-144 | Monateen 110kV Substation | EirGrid | 110000 |  |  | 7.154 | 8 | 0.267 | 3 | 0.267 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285
1162 | 1162 | CL3-009 | CLARE | CLARE | SS-176 | Shannon 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.112 | 8 | 0.1 | 3 | 0.1 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1163 | 1163 | CL3-010 | CLARE | CLARE | SS-673 | Drumquin 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 1.467 | 2 | 0.116 | 3 | 0.116 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007
1164 | 1164 | CL3-011 | ROSCOMMON | ROSCOMMON | SS-206 | Boyle 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.361 | 9 | 0.099 | 3 | 0.099 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1165 | 1165 | CL3-012 | TIPPERARY | TIPPERARY | SS-300 | Lisheen 110kV Substation | EirGrid | 110000 | 110000 | low | 4.105 | 5 | 0.204 | 3 | 0.204 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5
1166 | 1166 | CL3-013 | KILKENNY | KILKENNY | SS-300 | Lisheen 110kV Substation | EirGrid | 110000 | 110000 | low | 4.596 | 5 | 0.181 | 3 | 0.181 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5
1167 | 1167 | CL3-014 | WATERFORD | WATERFORD | SS-016 | Portlaw 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.186 | 3 | 0.22 | 3 | 0.22 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
1168 | 1168 | CL3-015 | LIMERICK | LIMERICK | SS-590 | Bruff 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.331 | 6 | 0.354 | 3 | 0.354 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1169 | 1169 | CL3-016 | CLARE | CLARE | SS-116 | Ardnacrusha 110kV Substation | EirGrid | 110000 | low | 110000 | 6.578 | 7 | 0.134 | 3 | 0.134 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525
1170 | 1170 | CL3-017 | CLARE | CLARE | SS-141 | Ennis North 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 6.296 | 7 | 0.096 | 3 | 0.096 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1171 | 1171 | CL3-018 | CLARE | CLARE | SS-012 | Ennis 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 10.652 | 11 | 0.113 | 3 | 0.113 | 4.2 | 4.2 | 1996170 | 7 | 475278.5714 | 2.104
1172 | 1172 | CL3-019 | CLARE | CLARE | SS-483 | Birdhill 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.435 | 8 | 0.207 | 3 | 0.207 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1173 | 1173 | CL3-020 | GALWAY | GALWAY | SS-439 | Loughrea 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.188 | 7 | 0.306 | 3 | 0.306 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1174 | 1174 | CL3-021 | ROSCOMMON | ROSCOMMON | SS-502 | Ballinasloe 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 4.33 | 5 | 0.113 | 3 | 0.113 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1175 | 1175 | CL3-022 | GALWAY | GALWAY | SS-269 | Shannonbridge 110kV Substation | EirGrid | 110000 | low | 110000 | 4.203 | 5 | 0.103 | 3 | 0.103 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5
1176 | 1176 | CL3-023 | OFFALY | OFFALY | SS-269 | Shannonbridge 110kV Substation | EirGrid | 110000 | low | 110000 | 4.168 | 5 | 0.148 | 3 | 0.148 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5
1177 | 1177 | CL3-024 | ROSCOMMON | ROSCOMMON | SS-269 | Shannonbridge 110kV Substation | EirGrid | 110000 | low | 110000 | 1.979 | 2 | 0.121 | 3 | 0.121 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341
1178 | 1178 | CL3-025 | OFFALY | OFFALY | SS-269 | Shannonbridge 110kV Substation | EirGrid | 110000 | low | 110000 | 3.874 | 4 | 0.333 | 3 | 0.333 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581
1179 | 1179 | CL3-026 | OFFALY | OFFALY | SS-269 | Shannonbridge 110kV Substation | EirGrid | 110000 | low | 110000 | 10.09 | 11 | 0.146 | 3 | 0.146 | 4.2 | 4.2 | 1996170 | 7 | 475278.5714 | 2.104
1180 | 1180 | CL3-027 | MEATH | MEATH | SS-701 | Clarkstown 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.228 | 5 | 0.11 | 3 | 0.11 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1181 | 1181 | CL3-028 | LONGFORD | LONGFORD | SS-575 | Aghamore 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.431 | 5 | 0.117 | 3 | 0.117 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1182 | 1182 | CL3-029 | OFFALY | OFFALY | SS-084 | Birr 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.398 | 4 | 0.097 | 3 | 0.097 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1183 | 1183 | CL3-030 | KILDARE | OFFALY | SS-657 | Edenderry 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.316 | 3 | 0.121 | 3 | 0.121 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
1184 | 1184 | CL3-031 | KILDARE | KILDARE | SS-216 | Blake 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 6.153 | 7 | 0.244 | 3 | 0.244 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525
1185 | 1185 | CL3-032 | OFFALY | OFFALY | SS-657 | Edenderry 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.141 | 5 | 0.274 | 3 | 0.274 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1186 | 1186 | CL3-033 | OFFALY | OFFALY | SS-530 | Esker 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 2.329 | 3 | 0.246 | 3 | 0.246 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674
1187 | 1187 | CL3-034 | OFFALY | OFFALY | SS-168 | Derryiron 110kV Substation | EirGrid | 110000 |  |  | 4.344 | 5 | 0.23 | 3 | 0.23 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5
1188 | 1188 | CL3-035 | OFFALY | OFFALY | SS-168 | Derryiron 110kV Substation | EirGrid | 110000 |  |  | 4.892 | 5 | 0.249 | 3 | 0.249 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5
1189 | 1189 | CL3-036 | OFFALY | OFFALY | SS-530 | Esker 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 5.568 | 6 | 0.129 | 3 | 0.129 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424
1190 | 1190 | CL3-037 | TIPPERARY | TIPPERARY | SS-053 | Ikerrin 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 1.101 | 2 | 0.225 | 3 | 0.225 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341
1191 | 1191 | CL3-038 | KILDARE | MEATH | SS-228 | Dunfierth 110kV Substation | EirGrid | 110000 | 110000 | 20000 | 1.976 | 2 | 0.121 | 3 | 0.121 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341
1192 | 1192 | CL3-039 | MEATH | MEATH | SS-701 | Clarkstown 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.488 | 6 | 0.202 | 3 | 0.202 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1193 | 1193 | CL3-040 | LOUTH | LOUTH | SS-544 | Ballybailie 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.062 | 4 | 0.404 | 3 | 0.404 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1194 | 1194 | CL3-041 | DONEGAL | DONEGAL | SS-289 | Gweedore 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.141 | 6 | 0.181 | 3 | 0.181 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1195 | 1195 | CL3-042 | DONEGAL | DONEGAL | SS-689 |  | ESB Networks | 38000 |  |  | 9.314 | 10 | 0.125 | 3 | 0.125 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
1196 | 1196 | CL3-043 | GALWAY | GALWAY | SS-175 | Ballygar 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.664 | 7 | 0.222 | 3 | 0.222 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1197 | 1197 | CL3-044 | WESTMEATH | WESTMEATH | SS-229 | Mullingar 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.615 | 6 | 0.196 | 3 | 0.196 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424
1198 | 1198 | CL3-045 | SLIGO | SLIGO | SS-095 | Collooney 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 2.349 | 3 | 0.134 | 3 | 0.134 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
1199 | 1199 | CL3-046 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 7.184 | 8 | 0.142 | 3 | 0.142 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1200 | 1200 | CL3-047 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 7.082 | 8 | 0.145 | 3 | 0.145 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1201 | 1201 | CL3-048 | WATERFORD | WATERFORD | SS-064 | Ballydine 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 3.259 | 4 | 0.262 | 3 | 0.262 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581
1202 | 1202 | CL3-049 | TIPPERARY | TIPPERARY | SS-347 | Glengoole 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.042 | 6 | 0.193 | 3 | 0.193 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1203 | 1203 | CL3-050 | OFFALY | OFFALY | SS-551 | Dallow 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 2.951 | 3 | 0.292 | 3 | 0.292 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674
1204 | 1204 | CL3-051 | OFFALY | OFFALY | SS-551 | Dallow 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 3.801 | 4 | 0.203 | 3 | 0.203 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581
1205 | 1205 | CL3-052 | WESTMEATH | WESTMEATH | SS-652 | Garrycastle 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 5.346 | 6 | 0.091 | 3 | 0.091 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1206 | 1206 | CL3-053 | CLARE | CLARE | SS-141 | Ennis North 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 12.035 | 13 | 0.113 | 3 | 0.113 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718
1207 | 1207 | CL3-054 | CLARE | CLARE | SS-141 | Ennis North 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 5.235 | 6 | 0.366 | 3 | 0.366 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1208 | 1208 | CL3-055 | KILDARE | KILDARE | SS-034 | Athy 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.505 | 6 | 0.113 | 3 | 0.113 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424
1209 | 1209 | CL3-056 | KILDARE | KILDARE | SS-034 | Athy 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.41 | 6 | 0.223 | 3 | 0.223 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424
1210 | 1210 | CL3-057 | WATERFORD | WATERFORD | SS-532 | Woodhouse 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 6.67 | 7 | 0.1 | 3 | 0.1 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525
1211 | 1211 | CL3-058 | KILKENNY | KILKENNY | SS-098 | Callan 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.394 | 4 | 0.288 | 3 | 0.288 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1212 | 1212 | CL3-059 | LAOIS | LAOIS | SS-486 | Castlecomer 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.864 | 8 | 0.326 | 3 | 0.326 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1213 | 1213 | CL3-060 | TIPPERARY | TIPPERARY | SS-459 | Ballycrossaun 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.053 | 14 | 0.31 | 3 | 0.31 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284
1214 | 1214 | CL3-061 | TIPPERARY | TIPPERARY | SS-325 | Kyleeragh 38kV Substation | ESB Networks | 38000 | 38000 | low | 16.259 | 17 | 0.114 | 3 | 0.114 | 4.2 | 4.2 | 1756040 | 1 | 418104.7619 | 2.3917
1215 | 1215 | CL3-062 | CLARE | CLARE | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.444 | 12 | 0.372 | 3 | 0.372 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
1216 | 1216 | CL3-063 | TIPPERARY | TIPPERARY | SS-325 | Kyleeragh 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.841 | 11 | 0.12 | 3 | 0.12 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
1217 | 1217 | CL3-064 | KILDARE | KILDARE | SS-216 | Blake 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 4.437 | 5 | 0.119 | 3 | 0.119 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5
1218 | 1218 | CL3-065 | KILDARE | KILDARE | SS-216 | Blake 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 2.978 | 3 | 0.164 | 3 | 0.164 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674
1219 | 1219 | CL3-066 | GALWAY | GALWAY | SS-236 | Creagh 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.488 | 11 | 0.092 | 3 | 0.092 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
1220 | 1220 | CL3-067 | TIPPERARY | TIPPERARY | SS-594 | Kill Hill 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 6.45 | 7 | 0.238 | 3 | 0.238 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525
1221 | 1221 | CL3-068 | LAOIS | LAOIS | SS-372 | Ballyconra 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.53 | 9 | 0.123 | 3 | 0.123 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1222 | 1222 | CL3-069 | LAOIS | LAOIS | SS-372 | Ballyconra 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.216 | 9 | 0.093 | 3 | 0.093 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1223 | 1223 | CL3-070 | LAOIS | LAOIS | SS-464 | Rathdowney 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.529 | 9 | 0.405 | 3 | 0.405 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1224 | 1224 | CL3-071 | CLARE | CLARE | SS-141 | Ennis North 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 11.773 | 12 | 0.2 | 3 | 0.2 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
1225 | 1225 | CL3-072 | GALWAY | GALWAY | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.114 | 5 | 0.18 | 3 | 0.18 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1226 | 1226 | CL3-073 | OFFALY | OFFALY | SS-231 | Lumcloon 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.559 | 11 | 0.157 | 3 | 0.157 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
1227 | 1227 | CL3-074 | OFFALY | OFFALY | SS-231 | Lumcloon 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.69 | 11 | 0.135 | 3 | 0.135 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
1228 | 1228 | CL3-075 | GALWAY | GALWAY | SS-104 | Athenry 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.999 | 16 | 0.142 | 3 | 0.142 | 4.2 | 4.2 | 1703340 | 1 | 405557.1429 | 2.4657
1229 | 1229 | CL3-076 | GALWAY | GALWAY | SS-104 | Athenry 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.184 | 16 | 0.161 | 3 | 0.161 | 4.2 | 4.2 | 1703340 | 1 | 405557.1429 | 2.4657
1230 | 1230 | CL3-077 | LIMERICK | LIMERICK | SS-402 | Rathgoggan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 6.449 | 7 | 0.43 | 3 | 0.43 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1231 | 1231 | CL3-078 | ROSCOMMON | ROSCOMMON | SS-269 | Shannonbridge 110kV Substation | EirGrid | 110000 | low | 110000 | 6.415 | 7 | 0.112 | 3 | 0.112 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525
1232 | 1232 | CL3-079 | TIPPERARY | TIPPERARY | SS-645 | Toomevara 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.234 | 7 | 0.248 | 3 | 0.248 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1233 | 1233 | CL3-080 | OFFALY | OFFALY | SS-084 | Birr 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.054 | 7 | 0.109 | 3 | 0.109 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1234 | 1234 | CL3-081 | GALWAY | GALWAY | SS-235 | Lisheeny 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.8 | 3 | 0.096 | 3 | 0.096 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
1235 | 1235 | CL3-082 | WESTMEATH | WESTMEATH | SS-052 | Moate 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 4.841 | 5 | 0.198 | 3 | 0.198 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1236 | 1236 | CL3-083 | ROSCOMMON | ROSCOMMON | SS-236 | Creagh 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.018 | 7 | 0.305 | 3 | 0.305 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1237 | 1237 | CL3-084 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.618 | 12 | 0.097 | 3 | 0.097 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
1238 | 1238 | CL3-085 | CORK | CORK | SS-032 | Mallow 110kV Substation | EirGrid | 110000 |  |  | 2.048 | 3 | 0.13 | 3 | 0.13 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674
1239 | 1239 | CL3-086 | CLARE | CLARE | SS-149 | Tulla 38kV Substation | ESB Networks | 38000 |  |  | 6.536 | 7 | 0.221 | 3 | 0.221 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1240 | 1240 | CL3-087 | GALWAY | GALWAY | SS-439 | Loughrea 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.561 | 9 | 0.156 | 3 | 0.156 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1241 | 1241 | CL3-088 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.895 | 10 | 0.235 | 3 | 0.235 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
1242 | 1242 | CL3-089 | CORK | CORK | SS-581 | Coolcarron 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.74 | 5 | 0.117 | 3 | 0.117 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1243 | 1243 | CL3-090 | KILKENNY | KILKENNY | SS-098 | Callan 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.899 | 8 | 0.356 | 3 | 0.356 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1244 | 1244 | CL3-091 | OFFALY | OFFALY | SS-541 | Roscrea 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.025 | 7 | 0.144 | 3 | 0.144 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1245 | 1245 | CL3-092 | TIPPERARY | TIPPERARY | SS-098 | Callan 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.028 | 11 | 0.184 | 3 | 0.184 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
1246 | 1246 | CL3-093 | OFFALY | OFFALY | SS-468 | Clara 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.664 | 5 | 0.255 | 3 | 0.255 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1247 | 1247 | CL3-094 | CORK | CORK | SS-606 | Castlelyons 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.353 | 6 | 0.113 | 3 | 0.113 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1248 | 1248 | CL3-095 | CORK | CORK | SS-583 | Castletownroche 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.325 | 10 | 0.221 | 3 | 0.221 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
1249 | 1249 | CL3-096 | TIPPERARY | LAOIS | SS-666 | 38kV Substation | ESB Networks | 38000 | low | 38000 | 6.79 | 7 | 0.154 | 3 | 0.154 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1250 | 1250 | CL3-097 | WICKLOW | WICKLOW | SS-699 | Ballycumber 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.057 | 4 | 0.201 | 3 | 0.201 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1251 | 1251 | CL3-098 | OFFALY | OFFALY | SS-469 | Portarlington 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.033 | 3 | 0.125 | 3 | 0.125 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
1252 | 1252 | CL3-099 | KILDARE | KILDARE | SS-228 | Dunfierth 110kV Substation | EirGrid | 110000 | 110000 | 20000 | 2.799 | 3 | 0.209 | 3 | 0.209 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674
1253 | 1253 | CL3-100 | LAOIS | LAOIS | SS-035 | Athy South 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.602 | 9 | 0.115 | 3 | 0.115 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1254 | 1254 | CL3-101 | LAOIS | LAOIS | SS-034 | Athy 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.048 | 9 | 0.325 | 3 | 0.325 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213
1255 | 1255 | CL3-102 | OFFALY | OFFALY | SS-231 | Lumcloon 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.115 | 14 | 0.195 | 3 | 0.195 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284
1256 | 1256 | CL3-103 | OFFALY | LAOIS | SS-311 | Clonminch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 12.322 | 13 | 0.183 | 3 | 0.183 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718
1257 | 1257 | CL3-104 | GALWAY | GALWAY | SS-236 | Creagh 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.69 | 7 | 0.262 | 3 | 0.262 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1258 | 1258 | CL3-105 | CLARE | CLARE | SS-149 | Tulla 38kV Substation | ESB Networks | 38000 |  |  | 4.44 | 5 | 0.326 | 3 | 0.326 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1259 | 1259 | CL3-106 | WICKLOW | WICKLOW | SS-699 | Ballycumber 38kV Substation | ESB Networks | 38000 | low | 38000 | 8.256 | 9 | 0.108 | 3 | 0.108 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1260 | 1260 | CL3-107 | KILDARE | LAOIS | SS-469 | Portarlington 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.83 | 10 | 0.122 | 3 | 0.122 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
1261 | 1261 | CL3-108 | OFFALY | OFFALY | SS-311 | Clonminch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.463 | 8 | 0.149 | 3 | 0.149 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1262 | 1262 | CL3-109 | CORK | CORK | SS-255 | Cloonlough 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.688 | 7 | 0.12 | 3 | 0.12 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1263 | 1263 | CL3-110 | WICKLOW | WICKLOW | SS-320 |  | EirGrid | 110000 | 110000 | low | 2.265 | 3 | 0.149 | 3 | 0.149 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674
1264 | 1264 | CL3-111 | TIPPERARY | TIPPERARY | SS-325 | Kyleeragh 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.48 | 13 | 0.117 | 3 | 0.117 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718
1265 | 1265 | CL3-112 | GALWAY | GALWAY | SS-175 | Ballygar 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.942 | 13 | 0.125 | 3 | 0.125 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718
1266 | 1266 | CL3-113 | TIPPERARY | TIPPERARY | SS-459 | Ballycrossaun 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.285 | 15 | 0.095 | 3 | 0.095 | 4.2 | 4.2 | 1650640 | 1 | 393009.5238 | 2.5445
1267 | 1267 | CL3-114 | OFFALY | OFFALY | SS-468 | Clara 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.286 | 3 | 0.25 | 3 | 0.25 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
1268 | 1268 | CL3-115 | TIPPERARY | TIPPERARY | SS-540 | Templemore 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 2.651 | 3 | 0.261 | 3 | 0.261 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
1269 | 1269 | CL3-116 | LAOIS | LAOIS | SS-372 | Ballyconra 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.306 | 11 | 0.263 | 3 | 0.263 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
1270 | 1270 | CL3-117 | OFFALY | OFFALY | SS-541 | Roscrea 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.204 | 9 | 0.238 | 3 | 0.238 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1271 | 1271 | CL3-118 | ROSCOMMON | ROSCOMMON | SS-683 | Monksland 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.976 | 3 | 0.175 | 3 | 0.175 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
1272 | 1272 | CL3-119 | WESTMEATH | WESTMEATH | SS-066 | Thornsberry 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 11.121 | 12 | 0.199 | 3 | 0.199 | 4.2 | 4.2 | 2048870 | 7 | 487826.1905 | 2.0499
1273 | 1273 | CL3-120 | WEXFORD | WEXFORD | SS-495 | New Ross (West) 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.339 | 6 | 0.151 | 3 | 0.151 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1274 | 1274 | CL3-121 | LIMERICK | LIMERICK | SS-402 | Rathgoggan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 13.118 | 14 | 0.154 | 3 | 0.154 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284
1275 | 1275 | CL3-122 | ROSCOMMON | ROSCOMMON | SS-236 | Creagh 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 3.877 | 4 | 0.148 | 3 | 0.148 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1276 | 1276 | CL3-123 | LAOIS | LAOIS | SS-217 | Port Laoise 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.646 | 9 | 0.292 | 3 | 0.292 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213
1277 | 1277 | CL3-124 | LAOIS | LAOIS | SS-275 | Mountrath ESB Telecoms 38kV Radio Site | ESB Networks | 38000 | 38000 | low | 6.611 | 7 | 0.109 | 3 | 0.109 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1278 | 1278 | CL3-125 | OFFALY | OFFALY | SS-084 | Birr 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.984 | 5 | 0.32 | 3 | 0.32 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1279 | 1279 | CL3-126 | OFFALY | OFFALY | SS-244 | Cartrontroy 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.739 | 8 | 0.161 | 3 | 0.161 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1280 | 1280 | CL3-127 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.053 | 5 | 0.11 | 3 | 0.11 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1281 | 1281 | CL3-128 | CARLOW | CARLOW | SS-368 | Gortahile 38kV Substation | ESB Networks | 38000 | low | 38000 | 6.399 | 7 | 0.17 | 3 | 0.17 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1282 | 1282 | CL3-129 | CLARE | CLARE | SS-503 | Scariff 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 5.043 | 6 | 0.162 | 3 | 0.162 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1283 | 1283 | CL3-130 | LAOIS | LAOIS | SS-469 | Portarlington 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.711 | 12 | 0.235 | 3 | 0.235 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
1284 | 1284 | CL3-131 | CORK | LIMERICK | SS-340 | Milford 38kV Substation | ESB Networks | 38000 | 38000 | low | 1.659 | 2 | 0.109 | 3 | 0.109 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007
1285 | 1285 | CL3-132 | WATERFORD | LAOIS | SS-537 | Monaincha 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 3.572 | 4 | 0.121 | 3 | 0.121 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1286 | 1286 | CL3-133 | LAOIS | LAOIS | SS-275 | Mountrath ESB Telecoms 38kV Radio Site | ESB Networks | 38000 | 38000 | low | 8.995 | 9 | 0.156 | 3 | 0.156 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1287 | 1287 | CL3-134 | CORK | CORK | SS-433 | Lee Bridge 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.297 | 11 | 0.11 | 3 | 0.11 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
1288 | 1288 | CL3-135 | TIPPERARY | TIPPERARY | SS-348 | Furle 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.478 | 9 | 0.202 | 3 | 0.202 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1289 | 1289 | CL3-136 | TIPPERARY | TIPPERARY | SS-040 | Deerpark 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.171 | 11 | 0.096 | 3 | 0.096 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
1290 | 1290 | CL3-137 | KILKENNY | KILKENNY | SS-489 | Ballyhale 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.892 | 9 | 0.251 | 3 | 0.251 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1291 | 1291 | CL3-138 | LAOIS | LAOIS | SS-486 | Castlecomer 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.951 | 11 | 0.135 | 3 | 0.135 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
1292 | 1292 | CL3-139 | TIPPERARY | TIPPERARY | SS-594 | Kill Hill 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 2.688 | 3 | 0.113 | 3 | 0.113 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674
1293 | 1293 | CL3-140 | LAOIS | LAOIS | SS-537 | Monaincha 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 8.657 | 9 | 0.203 | 3 | 0.203 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1294 | 1294 | CL3-141 | KERRY | KERRY | SS-706 | Scartaglin 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.845 | 2 | 0.153 | 3 | 0.153 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007
1295 | 1295 | CL3-142 | KERRY | KERRY | SS-189 | Knockearagh 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 4.5 | 5 | 0.109 | 3 | 0.109 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5
1296 | 1296 | CL3-143 | CAVAN | CAVAN | SS-304 | Arigna 110kV Substation | EirGrid | 110000 | 110000 | 20000 | 12.611 | 13 | 0.181 | 3 | 0.181 | 4.2 | 4.2 | 2101570 | 7 | 500373.8095 | 1.9985
1297 | 1297 | CL3-144 | CAVAN | CAVAN | SS-110 | Corraclassy 110kV Substation | EirGrid | 110000 |  |  | 15.879 | 16 | 0.305 | 3 | 0.305 | 4.2 | 4.2 | 2259670 | 7 | 538016.6667 | 1.8587
1298 | 1298 | CL3-145 | GALWAY | GALWAY | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 6.137 | 7 | 0.107 | 3 | 0.107 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1299 | 1299 | CL3-146 | GALWAY | GALWAY | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 6.923 | 7 | 0.14 | 3 | 0.14 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1300 | 1300 | CL3-147 | LEITRIM | LEITRIM | SS-304 | Arigna 110kV Substation | EirGrid | 110000 | 110000 | 20000 | 7.277 | 8 | 0.221 | 3 | 0.221 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285
1301 | 1301 | CL3-148 | SLIGO | SLIGO | SS-075 | Cunghill 110kV Substation | EirGrid | 110000 | 110000 | medium | 1.907 | 2 | 0.184 | 3 | 0.184 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341
1302 | 1302 | CL3-149 | SLIGO | SLIGO | SS-075 | Cunghill 110kV Substation | EirGrid | 110000 | 110000 | medium | 3.389 | 4 | 0.185 | 3 | 0.185 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581
1303 | 1303 | CL3-150 | ROSCOMMON | ROSCOMMON | SS-206 | Boyle 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 13.482 | 14 | 0.137 | 3 | 0.137 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284
1304 | 1304 | CL3-151 | ROSCOMMON | ROSCOMMON | SS-206 | Boyle 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 11.242 | 12 | 0.201 | 3 | 0.201 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
1305 | 1305 | CL3-152 | ROSCOMMON | ROSCOMMON | SS-171 | Castlerea 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.11 | 7 | 0.132 | 3 | 0.132 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1306 | 1306 | CL3-153 | ROSCOMMON | ROSCOMMON | SS-171 | Castlerea 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.934 | 7 | 0.134 | 3 | 0.134 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1307 | 1307 | CL3-154 | LEITRIM | LEITRIM | SS-048 | Roosky 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.946 | 4 | 0.331 | 3 | 0.331 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1308 | 1308 | CL3-155 | ROSCOMMON | ROSCOMMON | SS-158 | Gilra 110kV Substation | EirGrid | 110000 | 110000 | low | 8.035 | 9 | 0.282 | 3 | 0.282 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213
1309 | 1309 | CL3-156 | ROSCOMMON | ROSCOMMON | SS-206 | Boyle 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 4.66 | 5 | 0.167 | 3 | 0.167 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1310 | 1310 | CL3-157 | SLIGO | LEITRIM | SS-031 | Sligo 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.438 | 9 | 0.174 | 3 | 0.174 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213
1311 | 1311 | CL3-158 | MAYO | MAYO | SS-202 | Kiltimagh 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.57 | 7 | 0.234 | 3 | 0.234 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1312 | 1312 | CL3-159 | ROSCOMMON | ROSCOMMON | SS-171 | Castlerea 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.313 | 13 | 0.145 | 3 | 0.145 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718
1313 | 1313 | CL3-160 | ROSCOMMON | ROSCOMMON | SS-175 | Ballygar 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.522 | 11 | 0.17 | 3 | 0.17 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
1314 | 1314 | CL3-161 | MAYO | MAYO | SS-208 | Ballyhaunis 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.381 | 6 | 0.104 | 3 | 0.104 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1315 | 1315 | CL3-162 | ROSCOMMON | ROSCOMMON | SS-048 | Roosky 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.486 | 4 | 0.206 | 3 | 0.206 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1316 | 1316 | CL3-163 | LONGFORD | LONGFORD | SS-563 | Ballymahon 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.878 | 6 | 0.102 | 3 | 0.102 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1317 | 1317 | CL3-164 | LONGFORD | LONGFORD | SS-563 | Ballymahon 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.661 | 3 | 0.097 | 3 | 0.097 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
1318 | 1318 | CL3-165 | LONGFORD | LONGFORD | SS-563 | Ballymahon 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.457 | 4 | 0.108 | 3 | 0.108 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1319 | 1319 | CL3-166 | WESTMEATH | WESTMEATH | SS-563 | Ballymahon 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.889 | 6 | 0.141 | 3 | 0.141 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1320 | 1320 | CL3-167 | LONGFORD | LONGFORD | SS-563 | Ballymahon 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.17 | 7 | 0.44 | 3 | 0.44 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1321 | 1321 | CL3-168 | ROSCOMMON | ROSCOMMON | SS-124 | Roscommon 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.464 | 7 | 0.13 | 3 | 0.13 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1322 | 1322 | CL3-169 | LONGFORD | LONGFORD | SS-563 | Ballymahon 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.96 | 7 | 0.166 | 3 | 0.166 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1323 | 1323 | CL3-170 | WEXFORD | LONGFORD | SS-247 | Edgeworthstown 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.559 | 7 | 0.168 | 3 | 0.168 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1324 | 1324 | CL3-171 | WESTMEATH | WESTMEATH | SS-229 | Mullingar 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 9.016 | 10 | 0.198 | 3 | 0.198 | 4.2 | 4.2 | 1943470 | 7 | 462730.9524 | 2.1611
1325 | 1325 | CL3-172 | WESTMEATH | WESTMEATH | SS-563 | Ballymahon 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.183 | 13 | 0.103 | 3 | 0.103 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718
1326 | 1326 | CL3-173 | WESTMEATH | WESTMEATH | SS-246 | Loughanalla 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.462 | 9 | 0.091 | 3 | 0.091 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1327 | 1327 | CL3-174 | LONGFORD | LONGFORD | SS-067 | Finnea 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.578 | 7 | 0.272 | 3 | 0.272 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1328 | 1328 | CL3-175 | WESTMEATH | WESTMEATH | SS-246 | Loughanalla 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.602 | 9 | 0.154 | 3 | 0.154 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1329 | 1329 | CL3-176 | WESTMEATH | WESTMEATH | SS-246 | Loughanalla 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 3.665 | 4 | 0.176 | 3 | 0.176 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1330 | 1330 | CL3-177 | WESTMEATH | WESTMEATH | SS-067 | Finnea 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.728 | 6 | 0.109 | 3 | 0.109 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1331 | 1331 | CL3-178 | WEXFORD | LONGFORD | SS-247 | Edgeworthstown 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.924 | 6 | 0.231 | 3 | 0.231 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1332 | 1332 | CL3-179 | WESTMEATH | WESTMEATH | SS-052 | Moate 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 14.539 | 15 | 0.133 | 3 | 0.133 | 4.2 | 4.2 | 1650640 | 1 | 393009.5238 | 2.5445
1333 | 1333 | CL3-180 | LONGFORD | LONGFORD | SS-543 | Lisnamuck 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.528 | 5 | 0.144 | 3 | 0.144 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1334 | 1334 | CL3-181 | CAVAN | CAVAN | SS-081 | Killeshandra 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.122 | 6 | 0.116 | 3 | 0.116 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1335 | 1335 | CL3-182 | MONAGHAN | MONAGHAN | SS-428 | Clones 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.214 | 7 | 0.137 | 3 | 0.137 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1336 | 1336 | CL3-183 | WESTMEATH | WESTMEATH | SS-526 | Newbrook 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.405 | 8 | 0.139 | 3 | 0.139 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1337 | 1337 | CL3-184 | WESTMEATH | WESTMEATH | SS-526 | Newbrook 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 4.434 | 5 | 0.306 | 3 | 0.306 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1338 | 1338 | CL3-185 | WESTMEATH | WESTMEATH | SS-517 | Delvin 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.828 | 8 | 0.115 | 3 | 0.115 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1339 | 1339 | CL3-186 | MEATH | MEATH | SS-375 | Kells Business Park 38kV Substation | ESB Networks | 38000 | 38000 |  | 5.912 | 6 | 0.348 | 3 | 0.348 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1340 | 1340 | CL3-187 | MEATH | MEATH | SS-521 | Kingscourt 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.125 | 9 | 0.095 | 3 | 0.095 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1341 | 1341 | CL3-188 | WESTMEATH | MEATH | SS-517 | Delvin 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.032 | 8 | 0.132 | 3 | 0.132 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1342 | 1342 | CL3-189 | MEATH | MEATH | SS-460 | Julianstown 38kV Substation | ESB Networks | 38000 | 38000 | low | 1.865 | 2 | 0.279 | 3 | 0.279 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007
1343 | 1343 | CL3-190 | MEATH | MEATH | SS-518 | Athboy 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.902 | 4 | 0.241 | 3 | 0.241 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1344 | 1344 | CL3-191 | LONGFORD | LONGFORD | SS-044 | Richmond 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 4.627 | 5 | 0.107 | 3 | 0.107 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5
1345 | 1345 | CL3-192 | ROSCOMMON | ROSCOMMON | SS-175 | Ballygar 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.858 | 5 | 0.212 | 3 | 0.212 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1346 | 1346 | CL3-193 | KILDARE | KILDARE | SS-034 | Athy 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 6.726 | 7 | 0.113 | 3 | 0.113 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525
1347 | 1347 | CL3-194 | KILDARE | KILDARE | SS-216 | Blake 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 6.36 | 7 | 0.106 | 3 | 0.106 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525
1348 | 1348 | CL3-195 | GALWAY | GALWAY | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 6.469 | 7 | 0.145 | 3 | 0.145 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1349 | 1349 | CL3-196 | LONGFORD | LONGFORD | SS-575 | Aghamore 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.254 | 11 | 0.248 | 3 | 0.248 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
1350 | 1350 | CL3-197 | LONGFORD | LONGFORD | SS-268 | Lanesborough 110kV Substation | EirGrid | 110000 |  |  | 6.45 | 7 | 0.203 | 3 | 0.203 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525
1351 | 1351 | CL3-198 | MONAGHAN | MONAGHAN | SS-547 | Emyvale 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.675 | 5 | 0.115 | 3 | 0.115 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1352 | 1352 | CL3-199 | OFFALY | OFFALY | SS-084 | Birr 38kV Substation | ESB Networks | 38000 | 38000 | low | 16.731 | 17 | 0.133 | 3 | 0.133 | 4.2 | 4.2 | 1756040 | 1 | 418104.7619 | 2.3917
1353 | 1353 | CL3-200 | OFFALY | OFFALY | SS-084 | Birr 38kV Substation | ESB Networks | 38000 | 38000 | low | 16.649 | 17 | 0.153 | 3 | 0.153 | 4.2 | 4.2 | 1756040 | 1 | 418104.7619 | 2.3917
1354 | 1354 | CL3-201 | LIMERICK | LIMERICK | SS-596 | Cappamore 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.426 | 8 | 0.201 | 3 | 0.201 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1355 | 1355 | CL3-202 | MONAGHAN | MONAGHAN | SS-428 | Clones 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.941 | 8 | 0.226 | 3 | 0.226 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1356 | 1356 | CL3-203 | WATERFORD | WATERFORD | SS-622 | Barranafaddock 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.898 | 2 | 0.148 | 3 | 0.148 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007
1357 | 1357 | CL3-204 | TIPPERARY | TIPPERARY | SS-459 | Ballycrossaun 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.934 | 5 | 0.299 | 3 | 0.299 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1358 | 1358 | CL3-205 | OFFALY | OFFALY | SS-311 | Clonminch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 3.173 | 4 | 0.392 | 3 | 0.392 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1359 | 1359 | CL3-206 | OFFALY | OFFALY | SS-168 | Derryiron 110kV Substation | EirGrid | 110000 |  |  | 5.659 | 6 | 0.302 | 3 | 0.302 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424
1360 | 1360 | CL3-207 | TIPPERARY | TIPPERARY | SS-537 | Monaincha 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 1.991 | 2 | 0.424 | 3 | 0.424 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007
1361 | 1361 | CL3-208 | OFFALY | LAOIS | SS-231 | Lumcloon 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.782 | 14 | 0.422 | 3 | 0.422 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284
1362 | 1362 | CL3-209 | CORK | WATERFORD | SS-607 | Curraglass 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.633 | 8 | 0.103 | 3 | 0.103 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1363 | 1363 | CL3-210 | KILKENNY | KILKENNY | SS-492 | Graigue 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.244 | 6 | 0.104 | 3 | 0.104 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1364 | 1364 | CL3-211 | TIPPERARY | TIPPERARY | SS-347 | Glengoole 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.452 | 7 | 0.338 | 3 | 0.338 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1365 | 1365 | CL3-212 | ROSCOMMON | ROSCOMMON | SS-236 | Creagh 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 1.677 | 2 | 0.261 | 3 | 0.261 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007
1366 | 1366 | CL3-213 | SLIGO | SLIGO | SS-075 | Cunghill 110kV Substation | EirGrid | 110000 | 110000 | medium | 4.558 | 5 | 0.422 | 3 | 0.422 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5
1367 | 1367 | CL3-214 | ROSCOMMON | ROSCOMMON | SS-236 | Creagh 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.334 | 12 | 0.1 | 3 | 0.1 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
1368 | 1368 | CL3-215 | WESTMEATH | WESTMEATH | SS-232 | Bushfield 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.831 | 7 | 0.143 | 3 | 0.143 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1369 | 1369 | CL3-216 | WESTMEATH | WESTMEATH | SS-052 | Moate 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.363 | 8 | 0.457 | 3 | 0.457 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1370 | 1370 | CL3-217 | DONEGAL | DONEGAL | SS-117 | Crockahenny 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.528 | 2 | 0.529 | 3 | 0.529 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007
1371 | 1371 | CL3-218 | DONEGAL | DONEGAL | SS-083 | Golagh 110kV Substation | EirGrid | 110000 | 38000 | 110000 | 9.304 | 10 | 0.277 | 3 | 0.277 | 4.2 | 4.2 | 1943470 | 7 | 462730.9524 | 2.1611
1372 | 1372 | CL3-219 | DONEGAL | DONEGAL | SS-690 | Stranrolar 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.66 | 11 | 0.091 | 3 | 0.091 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
1373 | 1373 | CL3-220 | DONEGAL | DONEGAL | SS-083 | Golagh 110kV Substation | EirGrid | 110000 | 38000 | 110000 | 5.41 | 6 | 0.291 | 3 | 0.291 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424
1374 | 1374 | CL3-221 | DONEGAL | DONEGAL | SS-617 | Mulreavy 110kV Substation | EirGrid | 110000 | 33000 | 110000 | 7.02 | 8 | 0.312 | 3 | 0.312 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285
1375 | 1375 | CL3-222 | DONEGAL | DONEGAL | SS-617 | Mulreavy 110kV Substation | EirGrid | 110000 | 33000 | 110000 | 7.728 | 8 | 0.096 | 3 | 0.096 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285
1376 | 1376 | CL3-223 | DONEGAL | DONEGAL | SS-087 | Cliff 110kV Substation | EirGrid | 110000 | low | 110000 | 13.498 | 14 | 0.125 | 3 | 0.125 | 4.2 | 4.2 | 2154270 | 7 | 512921.4286 | 1.9496
1377 | 1377 | CL3-224 | CAVAN | CAVAN | SS-110 | Corraclassy 110kV Substation | EirGrid | 110000 |  |  | 3.382 | 4 | 0.124 | 3 | 0.124 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581
1378 | 1378 | CL3-225 | LOUTH | LOUTH | SS-650 | Ballymascanlan 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.283 | 7 | 0.242 | 3 | 0.242 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1379 | 1379 | CL3-226 | CORK | CORK | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.004 | 12 | 0.226 | 3 | 0.226 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
1380 | 1380 | CL3-227 | CORK | CORK | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 13.888 | 14 | 0.216 | 3 | 0.216 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284
1381 | 1381 | CL3-228 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 13.213 | 14 | 0.155 | 3 | 0.155 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284
1382 | 1382 | CL3-229 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.492 | 8 | 0.21 | 3 | 0.21 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1383 | 1383 | CL3-230 | CORK | CORK | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.461 | 9 | 0.268 | 3 | 0.268 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1384 | 1384 | CL3-231 | CORK | KERRY | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.144 | 8 | 0.66 | 3 | 0.66 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1385 | 1385 | CL3-232 | KERRY | KERRY | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.939 | 10 | 0.101 | 3 | 0.101 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
1386 | 1386 | CL3-233 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.091 | 12 | 0.419 | 3 | 0.419 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
1387 | 1387 | CL3-234 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.447 | 10 | 0.346 | 3 | 0.346 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
1388 | 1388 | CL3-235 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.443 | 7 | 0.557 | 3 | 0.557 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1389 | 1389 | CL3-236 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.179 | 8 | 0.313 | 3 | 0.313 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1390 | 1390 | CL3-237 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.71 | 6 | 0.162 | 3 | 0.162 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1391 | 1391 | CL3-238 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 17.786 | 18 | 0.167 | 3 | 0.167 | 4.2 | 4.2 | 1808740 | 1 | 430652.381 | 2.3221
1392 | 1392 | CL3-239 | KERRY | KERRY | SS-387 | Coolcorcoran 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.356 | 9 | 0.319 | 3 | 0.319 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1393 | 1393 | CL3-240 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.154 | 15 | 0.12 | 3 | 0.12 | 4.2 | 4.2 | 1650640 | 1 | 393009.5238 | 2.5445
1394 | 1394 | CL3-241 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.258 | 12 | 0.29 | 3 | 0.29 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
1395 | 1395 | CL3-242 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.096 | 12 | 0.212 | 3 | 0.212 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
1396 | 1396 | CL3-243 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.798 | 9 | 0.129 | 3 | 0.129 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1397 | 1397 | CL3-244 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.896 | 15 | 0.511 | 3 | 0.511 | 4.2 | 4.2 | 1650640 | 1 | 393009.5238 | 2.5445
1398 | 1398 | CL3-245 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 12.36 | 13 | 0.23 | 3 | 0.23 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718
1399 | 1399 | CL3-246 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.957 | 13 | 0.276 | 3 | 0.276 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718
1400 | 1400 | CL3-247 | KERRY | KERRY | SS-321 | Milltown 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 12.639 | 13 | 0.101 | 3 | 0.101 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718
1401 | 1401 | CL3-248 | KERRY | KERRY | SS-157 | Oughtragh 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 13.446 | 14 | 0.392 | 3 | 0.392 | 4.2 | 4.2 | 2154270 | 7 | 512921.4286 | 1.9496
1402 | 1402 | CL3-249 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 15.864 | 16 | 0.111 | 3 | 0.111 | 4.2 | 4.2 | 1703340 | 1 | 405557.1429 | 2.4657
1403 | 1403 | CL3-250 | KERRY | KERRY | SS-072 | Clonkeen 110kV Substation | EirGrid | 110000 |  |  | 5.546 | 6 | 0.197 | 3 | 0.197 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424
1404 | 1404 | CL3-251 | KERRY | KERRY | SS-071 | Coomagearlahy Substation | EirGrid | 110000 | medium-low | 110000 | 5.191 | 6 | 0.376 | 3 | 0.376 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424
1405 | 1405 | CL3-252 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.158 | 5 | 0.344 | 3 | 0.344 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1406 | 1406 | CL3-253 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.165 | 16 | 0.397 | 3 | 0.397 | 4.2 | 4.2 | 1703340 | 1 | 405557.1429 | 2.4657
1407 | 1407 | CL3-254 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 11.758 | 12 | 0.091 | 3 | 0.091 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
1408 | 1408 | CL3-255 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 8.735 | 9 | 0.319 | 3 | 0.319 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1409 | 1409 | CL3-256 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.637 | 2 | 0.128 | 3 | 0.128 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007
1410 | 1410 | CL3-257 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 6.326 | 7 | 0.444 | 3 | 0.444 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1411 | 1411 | CL3-258 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.644 | 4 | 0.227 | 3 | 0.227 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1412 | 1412 | CL3-259 | CORK | CORK | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 5.364 | 6 | 0.42 | 3 | 0.42 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1413 | 1413 | CL3-260 | CORK | CORK | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 6.022 | 7 | 0.401 | 3 | 0.401 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1414 | 1414 | CL3-261 | CORK | CORK | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 2.547 | 3 | 0.117 | 3 | 0.117 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
1415 | 1415 | CL3-262 | KERRY | KERRY | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 7.907 | 8 | 0.626 | 3 | 0.626 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1416 | 1416 | CL3-263 | KERRY | KERRY | SS-637 | Kilgarvan 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.44 | 6 | 0.454 | 3 | 0.454 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1417 | 1417 | CL3-264 | KERRY | KERRY | SS-321 | Milltown 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 3.471 | 4 | 0.387 | 3 | 0.387 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1418 | 1418 | CL3-265 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.78 | 5 | 0.276 | 3 | 0.276 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1419 | 1419 | CL3-266 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.286 | 8 | 0.239 | 3 | 0.239 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1420 | 1420 | CL3-267 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.716 | 9 | 0.644 | 3 | 0.644 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1421 | 1421 | CL3-268 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.044 | 6 | 0.173 | 3 | 0.173 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1422 | 1422 | CL3-269 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.267 | 5 | 0.103 | 3 | 0.103 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1423 | 1423 | CL3-270 | KERRY | KERRY | SS-140 | Ballyard 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.087 | 8 | 0.305 | 3 | 0.305 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1424 | 1424 | CL3-271 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.612 | 6 | 0.2 | 3 | 0.2 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1425 | 1425 | CL3-272 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.93 | 8 | 0.106 | 3 | 0.106 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1426 | 1426 | CL3-273 | CLARE | CLARE | SS-176 | Drumquin 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 6.337 | 7 | 0.177 | 3 | 0.177 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1427 | 1427 | CL3-274 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.58 | 16 | 0.099 | 3 | 0.099 | 4.2 | 4.2 | 1703340 | 1 | 405557.1429 | 2.4657
1428 | 1428 | CL3-275 | CLARE | CLARE | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 18.161 | 19 | 0.27 | 3 | 0.27 | 4.2 | 4.2 | 1861440 | 1 | 443200 | 2.2563
1429 | 1429 | CL3-276 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 18.143 | 19 | 0.115 | 3 | 0.115 | 4.2 | 4.2 | 1861440 | 1 | 443200 | 2.2563
1430 | 1430 | CL3-277 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.266 | 13 | 0.09 | 3 | 0.09 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718
1431 | 1431 | CL3-278 | GALWAY | GALWAY | SS-106 | Clifden 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.705 | 13 | 0.148 | 3 | 0.148 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718
1432 | 1432 | CL3-279 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.965 | 10 | 0.114 | 3 | 0.114 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
1433 | 1433 | CL3-280 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.948 | 12 | 0.156 | 3 | 0.156 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
1434 | 1434 | CL3-281 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.137 | 11 | 0.497 | 3 | 0.497 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
1435 | 1435 | CL3-282 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.583 | 3 | 0.148 | 3 | 0.148 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
1436 | 1436 | CL3-283 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.359 | 15 | 0.537 | 3 | 0.537 | 4.2 | 4.2 | 1650640 | 1 | 393009.5238 | 2.5445
1437 | 1437 | CL3-284 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.732 | 13 | 0.252 | 3 | 0.252 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718
1438 | 1438 | CL3-285 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.105 | 14 | 0.386 | 3 | 0.386 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284
1439 | 1439 | CL3-286 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 10.603 | 11 | 0.24 | 3 | 0.24 | 4.2 | 4.2 | 1996170 | 7 | 475278.5714 | 2.104
1440 | 1440 | CL3-287 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 17.082 | 18 | 0.273 | 3 | 0.273 | 4.2 | 4.2 | 1808740 | 1 | 430652.381 | 2.3221
1441 | 1441 | CL3-288 | GALWAY | GALWAY | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 17.598 | 18 | 0.119 | 3 | 0.119 | 4.2 | 4.2 | 1808740 | 1 | 430652.381 | 2.3221
1442 | 1442 | CL3-289 | MAYO | MAYO | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 17.635 | 18 | 0.55 | 3 | 0.55 | 4.2 | 4.2 | 1808740 | 1 | 430652.381 | 2.3221
1443 | 1443 | CL3-290 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 11.291 | 12 | 0.365 | 3 | 0.365 | 4.2 | 4.2 | 2048870 | 7 | 487826.1905 | 2.0499
1444 | 1444 | CL3-291 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.205 | 7 | 0.344 | 3 | 0.344 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1445 | 1445 | CL3-292 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 18.421 | 19 | 0.093 | 3 | 0.093 | 4.2 | 4.2 | 1861440 | 1 | 443200 | 2.2563
1446 | 1446 | CL3-293 | MAYO | MAYO | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 20.746 | 21 | 0.336 | 3 | 0.336 | 4.2 | 4.2 | 1966840 | 1 | 468295.2381 | 2.1354
1447 | 1447 | CL3-294 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 26.37 | 27 | 0.354 | 3 | 0.354 | 4.2 | 4.2 | 2839370 | 7 | 676040.4762 | 1.4792
1448 | 1448 | CL3-295 | MAYO | MAYO | SS-317 | Newport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 13.796 | 14 | 0.593 | 3 | 0.593 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284
1449 | 1449 | CL3-296 | MAYO | MAYO | SS-317 | Newport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 13.25 | 14 | 0.132 | 3 | 0.132 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284
1450 | 1450 | CL3-297 | MAYO | MAYO | SS-170 | Derrynadivva 38kV Substation | ESB Networks | 38000 | low | 38000 | 9.007 | 10 | 0.408 | 3 | 0.408 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
1451 | 1451 | CL3-298 | MAYO | MAYO | SS-170 | Derrynadivva 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.193 | 5 | 0.22 | 3 | 0.22 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1452 | 1452 | CL3-299 | SLIGO | SLIGO | SS-302 | Carrowleagh 38kV Substation | ESB Networks | 38000 | low | 38000 | 7.029 | 8 | 0.213 | 3 | 0.213 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1453 | 1453 | CL3-300 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.192 | 11 | 0.166 | 3 | 0.166 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
1454 | 1454 | CL3-301 | SLIGO | SLIGO | SS-042 | Ballytivnan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.747 | 9 | 0.171 | 3 | 0.171 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1455 | 1455 | CL3-302 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 4.011 | 5 | 0.326 | 3 | 0.326 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1456 | 1456 | CL3-303 | DONEGAL | DONEGAL | SS-252 | Killybegs 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 3.463 | 4 | 0.339 | 3 | 0.339 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1457 | 1457 | CL3-304 | DONEGAL | DONEGAL | SS-090 | Corkermore 38kV Substation | ESB Networks | 38000 | low | 38000 | 5.462 | 6 | 0.199 | 3 | 0.199 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1458 | 1458 | CL3-305 | DONEGAL | DONEGAL | SS-090 | Corkermore 38kV Substation | ESB Networks | 38000 | low | 38000 | 5.873 | 6 | 0.361 | 3 | 0.361 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1459 | 1459 | CL3-306 | DONEGAL | DONEGAL | SS-119 | Drumlough Hill (1) 38kV Substation | ESB Networks | 38000 | low | 38000 | 6.548 | 7 | 0.178 | 3 | 0.178 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1460 | 1460 | CL3-307 | ROSCOMMON | ROSCOMMON | SS-384 | Largan Hill 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.759 | 5 | 0.497 | 3 | 0.497 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1461 | 1461 | CL3-308 | ROSCOMMON | SLIGO | SS-384 | Largan Hill 38kV Substation | ESB Networks | 38000 | low | 38000 | 7.588 | 8 | 0.347 | 3 | 0.347 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1462 | 1462 | CL3-309 | WEXFORD | WEXFORD | SS-481 | Castledockrell 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 7.617 | 8 | 0.121 | 3 | 0.121 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285
1463 | 1463 | CL3-310 | CARLOW | CARLOW | SS-481 | Castledockrell 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 11.255 | 12 | 0.498 | 3 | 0.498 | 4.2 | 4.2 | 2048870 | 7 | 487826.1905 | 2.0499
1464 | 1464 | CL3-311 | CARLOW | CARLOW | SS-494 | Bunclody 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.445 | 10 | 0.608 | 3 | 0.608 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
1465 | 1465 | CL3-312 | WICKLOW | WICKLOW | SS-062 | Stratford 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 6.497 | 7 | 0.318 | 3 | 0.318 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525
1466 | 1466 | CL3-313 | WICKLOW | WICKLOW | SS-062 | Stratford 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 6.941 | 7 | 0.267 | 3 | 0.267 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525
1467 | 1467 | CL3-314 | WICKLOW | WICKLOW | SS-062 | Stratford 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.76 | 9 | 0.243 | 3 | 0.243 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213
1468 | 1468 | CL3-315 | WICKLOW | WICKLOW | SS-699 | Ballycumber 38kV Substation | ESB Networks | 38000 | low | 38000 | 11.14 | 12 | 0.402 | 3 | 0.402 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
1469 | 1469 | CL3-316 | WICKLOW | WICKLOW | SS-062 | Stratford 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 9.598 | 10 | 0.129 | 3 | 0.129 | 4.2 | 4.2 | 1943470 | 7 | 462730.9524 | 2.1611
1470 | 1470 | CL3-317 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.73 | 9 | 0.091 | 3 | 0.091 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1471 | 1471 | CL3-318 | WICKLOW | WICKLOW | SS-062 | Stratford 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 11.428 | 12 | 0.646 | 3 | 0.646 | 4.2 | 4.2 | 2048870 | 7 | 487826.1905 | 2.0499
1472 | 1472 | CL3-319 | WICKLOW | WICKLOW | SS-209 | Blessington 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.429 | 10 | 0.555 | 3 | 0.555 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
1473 | 1473 | CL3-320 | WICKLOW | WICKLOW | SS-570 | Kilcoole 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.644 | 14 | 0.346 | 3 | 0.346 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284
1474 | 1474 | CL3-321 | WEXFORD | WICKLOW | SS-616 | Ballinvally 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 3.755 | 4 | 0.126 | 3 | 0.126 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1475 | 1475 | CL3-322 | KERRY | KERRY | SS-668 | Coomataggart 110 kV Substation | EirGrid | 110000 | low | 110000 | 3.933 | 4 | 0.316 | 3 | 0.316 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581
1476 | 1476 | CL3-323 | CORK | CORK | SS-668 | Coomataggart 110 kV Substation | EirGrid | 110000 | low | 110000 | 2.789 | 3 | 0.234 | 3 | 0.234 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674
1477 | 1477 | CL3-324 | CORK | CORK | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.518 | 3 | 0.17 | 3 | 0.17 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
1478 | 1478 | CL3-325 | CORK | CORK | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.933 | 4 | 0.224 | 3 | 0.224 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1479 | 1479 | CL3-326 | CORK | CORK | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.805 | 4 | 0.119 | 3 | 0.119 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1480 | 1480 | CL3-327 | KERRY | KERRY | SS-071 | Coomagearlahy Substation | EirGrid | 110000 | medium-low | 110000 | 1.825 | 2 | 0.585 | 3 | 0.585 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341
1481 | 1481 | CL3-328 | KERRY | KERRY | SS-070 | Glanlee 110kV Substation | EirGrid | 110000 | low | 110000 | 4.099 | 5 | 0.371 | 3 | 0.371 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5
1482 | 1482 | CL3-329 | CORK | CORK | SS-070 | Glanlee 110kV Substation | EirGrid | 110000 | low | 110000 | 4.155 | 5 | 0.09 | 3 | 0.09 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5
1483 | 1483 | CL3-330 | CORK | CORK | SS-615 | Knockduff 110kv Substation | EirGrid | 110000 |  |  | 3.355 | 4 | 0.144 | 3 | 0.144 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581
1484 | 1484 | CL3-331 | CORK | CORK | SS-615 | Knockduff 110kv Substation | EirGrid | 110000 |  |  | 2.224 | 3 | 0.119 | 3 | 0.119 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674
1485 | 1485 | CL3-332 | CORK | CORK | SS-096 | Boggeragh 110kV Substation | EirGrid | 110000 |  |  | 3.674 | 4 | 0.133 | 3 | 0.133 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581
1486 | 1486 | CL3-333 | KILKENNY | KILKENNY | SS-495 | New Ross (West) 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.603 | 11 | 0.148 | 3 | 0.148 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
1487 | 1487 | CL3-334 | TIPPERARY | TIPPERARY | SS-540 | Templemore 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.665 | 9 | 0.185 | 3 | 0.185 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1488 | 1488 | CL3-335 | TIPPERARY | TIPPERARY | SS-540 | Templemore 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.728 | 8 | 0.28 | 3 | 0.28 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1489 | 1489 | CL3-336 | OFFALY | OFFALY | SS-168 | Derryiron 110kV Substation | EirGrid | 110000 |  |  | 6.071 | 7 | 0.536 | 3 | 0.536 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525
1490 | 1490 | CL3-337 | CLARE | CLARE | SS-708 |  | EirGrid | 110000 | medium | 110000 | 3.067 | 4 | 0.216 | 3 | 0.216 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581
1491 | 1491 | CL3-338 | DONEGAL | DONEGAL | SS-686 | Dungloe 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.182 | 13 | 0.113 | 3 | 0.113 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718
1492 | 1492 | CL3-339 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 11.803 | 12 | 0.09 | 3 | 0.09 | 4.2 | 4.2 | 2048870 | 7 | 487826.1905 | 2.0499
1493 | 1493 | CL3-340 | CAVAN | CAVAN | SS-097 | Corderry 110kV Substation | EirGrid | 110000 |  |  | 13.683 | 14 | 0.218 | 3 | 0.218 | 4.2 | 4.2 | 2154270 | 7 | 512921.4286 | 1.9496
1494 | 1494 | CL3-341 | LEITRIM | LEITRIM | SS-097 | Corderry 110kV Substation | EirGrid | 110000 |  |  | 8.587 | 9 | 0.21 | 3 | 0.21 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213
1495 | 1495 | CL3-342 | CAVAN | CAVAN | SS-110 | Corraclassy 110kV Substation | EirGrid | 110000 |  |  | 7.812 | 8 | 0.289 | 3 | 0.289 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285
1496 | 1496 | CL3-343 | LEITRIM | LEITRIM | SS-304 | Arigna 110kV Substation | EirGrid | 110000 | 110000 | 20000 | 10.843 | 11 | 0.264 | 3 | 0.264 | 4.2 | 4.2 | 1996170 | 7 | 475278.5714 | 2.104
1497 | 1497 | CL3-344 | CAVAN | CAVAN | SS-110 | Corraclassy 110kV Substation | EirGrid | 110000 |  |  | 4.169 | 5 | 0.236 | 3 | 0.236 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5
1498 | 1498 | CL3-345 | DONEGAL | DONEGAL | SS-086 | Meentycat 110kV Substation | EirGrid | 110000 | low | 110000 | 2.675 | 3 | 0.403 | 3 | 0.403 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674
1499 | 1499 | CL3-346 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 12.127 | 13 | 0.168 | 3 | 0.168 | 4.2 | 4.2 | 2101570 | 7 | 500373.8095 | 1.9985
1500 | 1500 | CL3-347 | DONEGAL | DONEGAL | SS-690 | Stranrolar 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.626 | 9 | 0.092 | 3 | 0.092 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1501 | 1501 | CL3-348 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 10.274 | 11 | 0.334 | 3 | 0.334 | 4.2 | 4.2 | 1996170 | 7 | 475278.5714 | 2.104
1502 | 1502 | CL3-349 | DONEGAL | DONEGAL | SS-102 | Binbane 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 3.858 | 4 | 0.446 | 3 | 0.446 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581
1503 | 1503 | CL3-350 | GALWAY | GALWAY | SS-623 | Uggool 110kV Substation | EirGrid | 110000 | 33000 | 110000 | 1.45 | 2 | 0.22 | 3 | 0.22 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341
1504 | 1504 | CL3-351 | WATERFORD | WATERFORD | SS-455 | Ardfinnan 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.521 | 11 | 0.502 | 3 | 0.502 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
1505 | 1505 | CL3-352 | WATERFORD | WATERFORD | SS-659 | Spa Road 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 5.23 | 6 | 0.146 | 3 | 0.146 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1506 | 1506 | CL3-353 | WATERFORD | WATERFORD | SS-064 | Ballydine 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 9.301 | 10 | 0.299 | 3 | 0.299 | 4.2 | 4.2 | 1943470 | 7 | 462730.9524 | 2.1611
1507 | 1507 | CL3-354 | WATERFORD | WATERFORD | SS-064 | Ballydine 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.591 | 9 | 0.133 | 3 | 0.133 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213
1508 | 1508 | CL3-355 | WATERFORD | WATERFORD | SS-064 | Ballydine 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 9.748 | 10 | 0.364 | 3 | 0.364 | 4.2 | 4.2 | 1943470 | 7 | 462730.9524 | 2.1611
1509 | 1509 | CL3-356 | WATERFORD | WATERFORD | SS-205 | Dungarvan 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.268 | 9 | 0.51 | 3 | 0.51 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213
1510 | 1510 | CL3-357 | WATERFORD | WATERFORD | SS-659 | Spa Road 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 12.408 | 13 | 0.167 | 3 | 0.167 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718
1511 | 1511 | CL3-358 | WATERFORD | WATERFORD | SS-659 | Spa Road 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 11.469 | 12 | 0.133 | 3 | 0.133 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
1512 | 1512 | CL3-359 | WATERFORD | WATERFORD | SS-505 | Kilmacthomas 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.436 | 10 | 0.217 | 3 | 0.217 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
1513 | 1513 | CL3-360 | WATERFORD | WATERFORD | SS-064 | Ballydine 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.448 | 6 | 0.282 | 3 | 0.282 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424
1514 | 1514 | CL3-361 | WATERFORD | WATERFORD | SS-205 | Dungarvan 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 4.755 | 5 | 0.16 | 3 | 0.16 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5
1515 | 1515 | CL3-362 | CORK | LIMERICK | SS-695 | Castlepook 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 2.432 | 3 | 0.213 | 3 | 0.213 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
1516 | 1516 | CL3-363 | LIMERICK | LIMERICK | SS-257 | Kilshanny 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.122 | 12 | 0.207 | 3 | 0.207 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
1517 | 1517 | CL3-364 | TIPPERARY | LIMERICK | SS-585 | Kilross Road 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.536 | 11 | 0.186 | 3 | 0.186 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
1518 | 1518 | CL3-365 | TIPPERARY | TIPPERARY | SS-315 | Cahir 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 4.593 | 5 | 0.439 | 3 | 0.439 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1519 | 1519 | CL3-366 | TIPPERARY | TIPPERARY | SS-257 | Kilshanny 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.753 | 10 | 0.206 | 3 | 0.206 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
1520 | 1520 | CL3-367 | CORK | CORK | SS-583 | Castletownroche 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.691 | 5 | 0.359 | 3 | 0.359 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1521 | 1521 | CL3-368 | CORK | CORK | SS-583 | Castletownroche 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.841 | 4 | 0.1 | 3 | 0.1 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1522 | 1522 | CL3-369 | CARLOW | CARLOW | SS-492 | Graigue 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.958 | 9 | 0.187 | 3 | 0.187 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1523 | 1523 | CL3-370 | CARLOW | CARLOW | SS-492 | Graigue 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.859 | 9 | 0.116 | 3 | 0.116 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1524 | 1524 | CL3-371 | WEXFORD | WEXFORD | SS-492 | Graigue 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.913 | 10 | 0.115 | 3 | 0.115 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
1525 | 1525 | CL3-372 | TIPPERARY | TIPPERARY | SS-692 | Hollyford 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.806 | 2 | 0.182 | 3 | 0.182 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007
1526 | 1526 | CL3-373 | TIPPERARY | TIPPERARY | SS-692 | Hollyford 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.848 | 3 | 0.497 | 3 | 0.497 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
1527 | 1527 | CL3-374 | TIPPERARY | TIPPERARY | SS-692 | Hollyford 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.929 | 3 | 0.109 | 3 | 0.109 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
1528 | 1528 | CL3-375 | CLARE | CLARE | SS-653 | Cranny 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 2.652 | 3 | 0.553 | 3 | 0.553 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
1529 | 1529 | CL3-376 | TIPPERARY | TIPPERARY | SS-551 | Dallow 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 3.595 | 4 | 0.414 | 3 | 0.414 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581
1530 | 1530 | CL3-377 | KILKENNY | KILKENNY | SS-016 | Portlaw 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.636 | 9 | 0.117 | 3 | 0.117 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1531 | 1531 | CL3-378 | TIPPERARY | TIPPERARY | SS-295 | Doon 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.135 | 6 | 0.303 | 3 | 0.303 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424
1532 | 1532 | CL3-379 | TIPPERARY | TIPPERARY | SS-295 | Doon 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 9.363 | 10 | 0.143 | 3 | 0.143 | 4.2 | 4.2 | 1943470 | 7 | 462730.9524 | 2.1611
1533 | 1533 | CL3-380 | TIPPERARY | TIPPERARY | SS-295 | Doon 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 10.211 | 11 | 0.127 | 3 | 0.127 | 4.2 | 4.2 | 1996170 | 7 | 475278.5714 | 2.104
1534 | 1534 | CL3-381 | TIPPERARY | TIPPERARY | SS-459 | Ballycrossaun 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.279 | 9 | 0.535 | 3 | 0.535 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1535 | 1535 | CL3-382 | LAOIS | LAOIS | SS-275 | Mountrath ESB Telecoms 38kV Radio Site | ESB Networks | 38000 | 38000 | low | 9.596 | 10 | 0.266 | 3 | 0.266 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
1536 | 1536 | CL3-383 | LAOIS | LAOIS | SS-275 | Mountrath ESB Telecoms 38kV Radio Site | ESB Networks | 38000 | 38000 | low | 11.076 | 12 | 0.321 | 3 | 0.321 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
1537 | 1537 | CL3-384 | OFFALY | OFFALY | SS-084 | Birr 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.522 | 12 | 0.103 | 3 | 0.103 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
1538 | 1538 | CL3-385 | GALWAY | GALWAY | SS-175 | Ballygar 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.088 | 11 | 0.115 | 3 | 0.115 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
1539 | 1539 | CL3-386 | GALWAY | GALWAY | SS-175 | Ballygar 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.87 | 8 | 0.43 | 3 | 0.43 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1540 | 1540 | CL3-387 | CORK | CORK | SS-668 | Coomataggart 110 kV Substation | EirGrid | 110000 | low | 110000 | 11.217 | 12 | 0.109 | 3 | 0.109 | 4.2 | 4.2 | 2048870 | 7 | 487826.1905 | 2.0499
1541 | 1541 | CL3-388 | KILKENNY | KILKENNY | SS-538 | Galmoy 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.085 | 11 | 0.388 | 3 | 0.388 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
1542 | 1542 | CL3-389 | LIMERICK | LIMERICK | SS-069 | Garryspillane 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.922 | 8 | 0.255 | 3 | 0.255 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1543 | 1543 | CL3-390 | LAOIS | LAOIS | SS-470 | Mountmellick 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.019 | 6 | 0.292 | 3 | 0.292 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1544 | 1544 | CL3-391 | KILDARE | KILDARE | SS-657 | Edenderry 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.097 | 5 | 0.417 | 3 | 0.417 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1545 | 1545 | CL3-392 | WEXFORD | WEXFORD | SS-616 | Ballinvally 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 7.429 | 8 | 0.205 | 3 | 0.205 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1546 | 1546 | CL3-393 | CORK | CORK | SS-197 | Midleton 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.157 | 9 | 0.279 | 3 | 0.279 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213
1547 | 1547 | CL3-394 | CLARE | CLARE | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.397 | 11 | 0.515 | 3 | 0.515 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
1548 | 1548 | CL3-395 | CLARE | CLARE | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.042 | 12 | 0.22 | 3 | 0.22 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
1549 | 1549 | CL3-396 | WATERFORD | WATERFORD | SS-622 | Barranafaddock 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.997 | 5 | 0.145 | 3 | 0.145 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1550 | 1550 | CL3-397 | KILKENNY | KILKENNY | SS-194 | Kilkenny 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.551 | 11 | 0.222 | 3 | 0.222 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
1551 | 1551 | CL3-398 | KILKENNY | KILKENNY | SS-489 | Ballyhale 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.257 | 3 | 0.38 | 3 | 0.38 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
1552 | 1552 | CL3-399 | KILKENNY | KILKENNY | SS-489 | Ballyhale 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.835 | 8 | 0.156 | 3 | 0.156 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1553 | 1553 | CL3-400 | GALWAY | GALWAY | SS-459 | Ballycrossaun 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.617 | 5 | 0.359 | 3 | 0.359 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1554 | 1554 | CL3-401 | CLARE | CLARE | SS-503 | Scariff 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 4.989 | 5 | 0.725 | 3 | 0.725 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1555 | 1555 | CL3-402 | CLARE | CLARE | SS-503 | Scariff 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.306 | 8 | 0.265 | 3 | 0.265 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1556 | 1556 | CL3-403 | CLARE | CLARE | SS-483 | Birdhill 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.14 | 8 | 0.239 | 3 | 0.239 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1557 | 1557 | CL3-404 | TIPPERARY | LIMERICK | SS-585 | Kilross Road 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.512 | 10 | 0.215 | 3 | 0.215 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
1558 | 1558 | CL3-405 | LAOIS | LAOIS | SS-034 | Athy 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 12.085 | 13 | 0.214 | 3 | 0.214 | 4.2 | 4.2 | 2101570 | 7 | 500373.8095 | 1.9985
1559 | 1559 | CL3-406 | WESTMEATH | WESTMEATH | SS-467 | Clara 38kV Substation | ESB Networks | 38000 | 38000 | 20000;10000 | 6.219 | 7 | 0.549 | 3 | 0.549 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1560 | 1560 | CL3-407 | KILDARE | KILDARE | SS-228 | Dunfierth 110kV Substation | EirGrid | 110000 | 110000 | 20000 | 7.812 | 8 | 0.262 | 3 | 0.262 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285
1561 | 1561 | CL3-408 | MAYO | MAYO | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 12.217 | 13 | 0.091 | 3 | 0.091 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718
1562 | 1562 | CL3-409 | SLIGO | SLIGO | SS-074 | Tobercurry 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.502 | 6 | 0.424 | 3 | 0.424 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1563 | 1563 | CL3-410 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.811 | 6 | 0.097 | 3 | 0.097 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1564 | 1564 | CL3-411 | GALWAY | GALWAY | SS-175 | Ballygar 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.493 | 9 | 0.211 | 3 | 0.211 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1565 | 1565 | CL3-412 | WESTMEATH | WESTMEATH | SS-246 | Loughanalla 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 5.828 | 6 | 0.105 | 3 | 0.105 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1566 | 1566 | CL3-413 | CAVAN | CAVAN | SS-081 | Killeshandra 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.7 | 4 | 0.307 | 3 | 0.307 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1567 | 1567 | CL3-414 | CAVAN | CAVAN | SS-081 | Killeshandra 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.527 | 5 | 0.283 | 3 | 0.283 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1568 | 1568 | CL3-415 | MEATH | MEATH | SS-059 | Kinnegad 110kV | EirGrid | 110000 |  |  | 8.002 | 9 | 0.142 | 3 | 0.142 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213
1569 | 1569 | CL3-416 | ROSCOMMON | ROSCOMMON | SS-457 | Cloondara 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.065 | 3 | 0.497 | 3 | 0.497 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
1570 | 1570 | CL3-417 | WESTMEATH | WESTMEATH | SS-232 | Bushfield 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.043 | 10 | 0.536 | 3 | 0.536 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
1571 | 1571 | CL3-418 | DONEGAL | DONEGAL | SS-118 | Sorne Hill 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 3.486 | 4 | 3.659 | 3 | 2.7443 | 16.8 | 16.8 | 1875790 | 8 | 111654.1667 | 8.9562
1572 | 1572 | CL3-419 | DONEGAL | DONEGAL | SS-690 | Stranrolar 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.945 | 9 | 1.018 | 3 | 1.018 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1573 | 1573 | CL3-420 | DONEGAL | DONEGAL | SS-690 | Stranrolar 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.768 | 9 | 0.485 | 3 | 0.485 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1574 | 1574 | CL3-421 | DONEGAL | DONEGAL | SS-083 | Golagh 110kV Substation | EirGrid | 110000 | 38000 | 110000 | 6.614 | 7 | 0.737 | 3 | 0.737 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525
1575 | 1575 | CL3-422 | DONEGAL | DONEGAL | SS-083 | Golagh 110kV Substation | EirGrid | 110000 | 38000 | 110000 | 4.88 | 5 | 0.603 | 3 | 0.603 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5
1576 | 1576 | CL3-423 | DONEGAL | DONEGAL | SS-617 | Mulreavy 110kV Substation | EirGrid | 110000 | 33000 | 110000 | 6.757 | 7 | 4.484 | 3 | 3.363 | 21 | 21 | 2086600 | 8 | 99361.9048 | 10.0642
1577 | 1577 | CL3-424 | DONEGAL | DONEGAL | SS-617 | Mulreavy 110kV Substation | EirGrid | 110000 | 33000 | 110000 | 11.409 | 12 | 2.52 | 3 | 1.89 | 12.6 | 12.6 | 2048870 | 7 | 162608.7302 | 6.1497
1578 | 1578 | CL3-425 | DONEGAL | DONEGAL | SS-087 | Cliff 110kV Substation | EirGrid | 110000 | low | 110000 | 3.306 | 4 | 1.921 | 3 | 1.4407 | 8.4 | 8.4 | 1627270 | 7 | 193722.619 | 5.162
1579 | 1579 | CL3-426 | CAVAN | CAVAN | SS-110 | Corraclassy 110kV Substation | EirGrid | 110000 |  |  | 4.611 | 5 | 2.859 | 3 | 2.1442 | 12.6 | 12.6 | 1679970 | 7 | 133330.9524 | 7.5001
1580 | 1580 | CL3-427 | CAVAN | CAVAN | SS-110 | Corraclassy 110kV Substation | EirGrid | 110000 |  |  | 8.743 | 9 | 2.396 | 3 | 1.797 | 12.6 | 12.6 | 1890770 | 7 | 150061.1111 | 6.664
1581 | 1581 | CL3-428 | CAVAN | CAVAN | SS-111 | Gortawee 110kV Station | EirGrid | 110000 | 110000 | low | 3.454 | 4 | 0.968 | 3 | 0.968 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581
1582 | 1582 | CL3-429 | CAVAN | CAVAN | SS-110 | Corraclassy 110kV Substation | EirGrid | 110000 |  |  | 5.225 | 6 | 3.936 | 3 | 2.952 | 21 | 21 | 2016330 | 8 | 96015.7143 | 10.415
1583 | 1583 | CL3-430 | LOUTH | LOUTH | SS-650 | Ballymascanlan 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.384 | 5 | 1.336 | 3 | 1.002 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1584 | 1584 | CL3-431 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 12.561 | 13 | 3.33 | 3 | 2.4975 | 16.8 | 16.8 | 1261300 | 4 | 75077.381 | 13.3196
1585 | 1585 | CL3-432 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 12.402 | 13 | 2.196 | 3 | 1.647 | 8.4 | 8.4 | 1590600 | 2 | 189357.1429 | 5.281
1586 | 1586 | CL3-433 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 13.715 | 14 | 0.983 | 3 | 0.983 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284
1587 | 1587 | CL3-434 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.518 | 11 | 0.941 | 3 | 0.941 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
1588 | 1588 | CL3-435 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.278 | 11 | 0.332 | 3 | 0.332 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
1589 | 1589 | CL3-436 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.018 | 8 | 0.58 | 3 | 0.58 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1590 | 1590 | CL3-437 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.851 | 9 | 1.702 | 3 | 1.2765 | 8.4 | 8.4 | 1379800 | 2 | 164261.9048 | 6.0878
1591 | 1591 | CL3-438 | CORK | CORK | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.711 | 9 | 1.142 | 3 | 1.142 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1592 | 1592 | CL3-439 | CORK | CORK | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.059 | 8 | 2.992 | 3 | 2.244 | 12.6 | 12.6 | 909950 | 4 | 72218.254 | 13.8469
1593 | 1593 | CL3-440 | KERRY | KERRY | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.349 | 10 | 1.558 | 3 | 1.1685 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
1594 | 1594 | CL3-441 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 12.241 | 13 | 0.768 | 3 | 0.768 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718
1595 | 1595 | CL3-442 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.199 | 5 | 0.791 | 3 | 0.791 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1596 | 1596 | CL3-443 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 3.997 | 4 | 0.612 | 3 | 0.612 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1597 | 1597 | CL3-444 | CORK | CORK | SS-273 | Castletownbere 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.65 | 7 | 0.922 | 3 | 0.922 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1598 | 1598 | CL3-445 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 9.908 | 10 | 1.197 | 3 | 1.197 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
1599 | 1599 | CL3-446 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 13.387 | 14 | 4.108 | 3 | 3.081 | 21 | 21 | 1331570 | 4 | 63408.0952 | 15.7709
1600 | 1600 | CL3-447 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 18.146 | 19 | 1.993 | 3 | 1.4948 | 8.4 | 8.4 | 1906800 | 2 | 227000 | 4.4053
1601 | 1601 | CL3-448 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.718 | 16 | 3.601 | 3 | 2.7008 | 16.8 | 16.8 | 1472110 | 4 | 87625.5952 | 11.4122
1602 | 1602 | CL3-449 | KERRY | KERRY | SS-321 | Milltown 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 17.503 | 18 | 1.262 | 3 | 0.9465 | 4.2 | 4.2 | 1808740 | 1 | 430652.381 | 2.3221
1603 | 1603 | CL3-450 | KERRY | KERRY | SS-321 | Milltown 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 17.597 | 18 | 1.096 | 3 | 1.096 | 4.2 | 4.2 | 1808740 | 1 | 430652.381 | 2.3221
1604 | 1604 | CL3-451 | KERRY | KERRY | SS-387 | Coolcorcoran 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.51 | 12 | 1.123 | 3 | 1.123 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
1605 | 1605 | CL3-452 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.58 | 14 | 0.767 | 3 | 0.767 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284
1606 | 1606 | CL3-453 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.536 | 14 | 0.504 | 3 | 0.504 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284
1607 | 1607 | CL3-454 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 13.622 | 14 | 1.884 | 3 | 1.413 | 8.4 | 8.4 | 1643300 | 2 | 195630.9524 | 5.1117
1608 | 1608 | CL3-455 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.408 | 10 | 2.99 | 3 | 2.2425 | 12.6 | 12.6 | 1469550 | 3 | 116630.9524 | 8.5741
1609 | 1609 | CL3-456 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.75 | 13 | 0.615 | 3 | 0.615 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718
1610 | 1610 | CL3-457 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.814 | 10 | 0.858 | 3 | 0.858 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
1611 | 1611 | CL3-458 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.334 | 13 | 0.337 | 3 | 0.337 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718
1612 | 1612 | CL3-459 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 16.18 | 17 | 2.277 | 3 | 1.7078 | 8.4 | 8.4 | 1801400 | 2 | 214452.381 | 4.663
1613 | 1613 | CL3-460 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 17.927 | 18 | 1.725 | 3 | 1.2938 | 8.4 | 8.4 | 1854100 | 2 | 220726.1905 | 4.5305
1614 | 1614 | CL3-461 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 17.832 | 18 | 0.482 | 3 | 0.482 | 4.2 | 4.2 | 1808740 | 1 | 430652.381 | 2.3221
1615 | 1615 | CL3-462 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 16.211 | 17 | 0.976 | 3 | 0.976 | 4.2 | 4.2 | 1756040 | 1 | 418104.7619 | 2.3917
1616 | 1616 | CL3-463 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 15.74 | 16 | 2.156 | 3 | 1.617 | 8.4 | 8.4 | 1748700 | 2 | 208178.5714 | 4.8036
1617 | 1617 | CL3-464 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 12.906 | 13 | 7.55 | 3 | 5.6625 | 37.8 | 37.8 | 1794170 | 6 | 47464.8148 | 21.0682
1618 | 1618 | CL3-465 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 12.709 | 13 | 1.795 | 3 | 1.3462 | 8.4 | 8.4 | 1590600 | 2 | 189357.1429 | 5.281
1619 | 1619 | CL3-466 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 13.119 | 14 | 1.102 | 3 | 1.102 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284
1620 | 1620 | CL3-467 | KERRY | KERRY | SS-321 | Milltown 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 15.274 | 16 | 1.035 | 3 | 1.035 | 4.2 | 4.2 | 1703340 | 1 | 405557.1429 | 2.4657
1621 | 1621 | CL3-468 | KERRY | KERRY | SS-157 | Oughtragh 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 14.717 | 15 | 2.795 | 3 | 2.0962 | 12.6 | 12.6 | 2206970 | 7 | 175156.3492 | 5.7092
1622 | 1622 | CL3-469 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 13.176 | 14 | 0.502 | 3 | 0.502 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284
1623 | 1623 | CL3-470 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 12.147 | 13 | 8.363 | 3 | 6.2722 | 42 | 42 | 1794170 | 6 | 42718.3333 | 23.4092
1624 | 1624 | CL3-471 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 10.162 | 11 | 0.812 | 3 | 0.812 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
1625 | 1625 | CL3-472 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 9.951 | 10 | 2.419 | 3 | 1.8142 | 12.6 | 12.6 | 1469550 | 3 | 116630.9524 | 8.5741
1626 | 1626 | CL3-473 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 9.19 | 10 | 1.219 | 3 | 0.91425 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
1627 | 1627 | CL3-474 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 10.49 | 11 | 5.228 | 3 | 3.921 | 25.2 | 25.2 | 1324920 | 5 | 52576.1905 | 19.02
1628 | 1628 | CL3-475 | KERRY | KERRY | SS-072 | Clonkeen 110kV Substation | EirGrid | 110000 |  |  | 7.558 | 8 | 2.816 | 3 | 2.112 | 12.6 | 12.6 | 1838070 | 7 | 145878.5714 | 6.855
1629 | 1629 | CL3-476 | KERRY | KERRY | SS-637 | Kilgarvan 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.399 | 7 | 1.865 | 3 | 1.3987 | 8.4 | 8.4 | 839680 | 4 | 99961.9048 | 10.0038
1630 | 1630 | CL3-477 | KERRY | KERRY | SS-637 | Kilgarvan 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.591 | 6 | 0.913 | 3 | 0.913 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1631 | 1631 | CL3-478 | KERRY | KERRY | SS-637 | Kilgarvan 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.427 | 7 | 2.819 | 3 | 2.1143 | 12.6 | 12.6 | 839680 | 4 | 66641.2698 | 15.0057
1632 | 1632 | CL3-479 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.489 | 5 | 1.066 | 3 | 1.066 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1633 | 1633 | CL3-480 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.458 | 6 | 1.827 | 3 | 1.3702 | 8.4 | 8.4 | 769410 | 4 | 91596.4286 | 10.9175
1634 | 1634 | CL3-481 | KERRY | KERRY | SS-160 | Woodford 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.96 | 8 | 2.69 | 3 | 2.0175 | 12.6 | 12.6 | 909950 | 4 | 72218.254 | 13.8469
1635 | 1635 | CL3-482 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.93 | 5 | 2.304 | 3 | 1.728 | 8.4 | 8.4 | 699140 | 4 | 83230.9524 | 12.0148
1636 | 1636 | CL3-483 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 14.024 | 15 | 1.44 | 3 | 1.08 | 4.2 | 4.2 | 1650640 | 1 | 393009.5238 | 2.5445
1637 | 1637 | CL3-484 | KERRY | KERRY | SS-151 | Kenmare 38kV Substation | ESB Networks | 38000 | 38000 | low | 16.668 | 17 | 2.46 | 3 | 1.845 | 12.6 | 12.6 | 1838450 | 3 | 145908.7302 | 6.8536
1638 | 1638 | CL3-485 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 15.478 | 16 | 1.197 | 3 | 1.197 | 4.2 | 4.2 | 1703340 | 1 | 405557.1429 | 2.4657
1639 | 1639 | CL3-486 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 12.104 | 13 | 4.149 | 3 | 3.1117 | 21 | 21 | 1261300 | 4 | 60061.9048 | 16.6495
1640 | 1640 | CL3-487 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 8.316 | 9 | 2.383 | 3 | 1.7873 | 12.6 | 12.6 | 1416850 | 3 | 112448.4127 | 8.893
1641 | 1641 | CL3-488 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 10.915 | 11 | 1.394 | 3 | 1.0455 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
1642 | 1642 | CL3-489 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 9.185 | 10 | 2.781 | 3 | 2.0857 | 12.6 | 12.6 | 1469550 | 3 | 116630.9524 | 8.5741
1643 | 1643 | CL3-490 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 9.868 | 10 | 1.379 | 3 | 1.0343 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
1644 | 1644 | CL3-491 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 7.454 | 8 | 0.451 | 3 | 0.451 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1645 | 1645 | CL3-492 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 6.495 | 7 | 1.267 | 3 | 0.95025 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1646 | 1646 | CL3-493 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.824 | 4 | 2.088 | 3 | 1.566 | 8.4 | 8.4 | 628870 | 4 | 74865.4762 | 13.3573
1647 | 1647 | CL3-494 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.359 | 5 | 2.119 | 3 | 1.5893 | 8.4 | 8.4 | 699140 | 4 | 83230.9524 | 12.0148
1648 | 1648 | CL3-495 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.577 | 2 | 1.265 | 3 | 0.94875 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007
1649 | 1649 | CL3-496 | CORK | CORK | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 7.131 | 8 | 0.595 | 3 | 0.595 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1650 | 1650 | CL3-497 | CORK | CORK | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.166 | 5 | 1.736 | 3 | 1.302 | 8.4 | 8.4 | 699140 | 4 | 83230.9524 | 12.0148
1651 | 1651 | CL3-498 | CORK | CORK | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 2.783 | 3 | 1.013 | 3 | 1.013 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
1652 | 1652 | CL3-499 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.849 | 5 | 1.557 | 3 | 1.1677 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1653 | 1653 | CL3-500 | KERRY | KERRY | SS-362 | Glengarriff 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.871 | 7 | 1.557 | 3 | 1.1677 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1654 | 1654 | CL3-501 | KERRY | KERRY | SS-637 | Kilgarvan 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.637 | 9 | 0.897 | 3 | 0.897 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1655 | 1655 | CL3-502 | KERRY | KERRY | SS-637 | Kilgarvan 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.071 | 8 | 1.803 | 3 | 1.3522 | 8.4 | 8.4 | 909950 | 4 | 108327.381 | 9.2313
1656 | 1656 | CL3-503 | KERRY | KERRY | SS-321 | Milltown 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 3.149 | 4 | 0.577 | 3 | 0.577 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1657 | 1657 | CL3-504 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.308 | 6 | 3.904 | 3 | 2.928 | 21 | 21 | 769410 | 4 | 36638.5714 | 27.2936
1658 | 1658 | CL3-505 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.163 | 8 | 3.114 | 3 | 2.3355 | 16.8 | 16.8 | 909950 | 4 | 54163.6905 | 18.4626
1659 | 1659 | CL3-506 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.321 | 9 | 3.456 | 3 | 2.592 | 16.8 | 16.8 | 980220 | 4 | 58346.4286 | 17.139
1660 | 1660 | CL3-507 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.517 | 8 | 0.884 | 3 | 0.884 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1661 | 1661 | CL3-508 | KERRY | KERRY | SS-635 | Dingle 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.021 | 10 | 1.764 | 3 | 1.323 | 8.4 | 8.4 | 1432500 | 2 | 170535.7143 | 5.8639
1662 | 1662 | CL3-509 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.152 | 6 | 2.335 | 3 | 1.7512 | 8.4 | 8.4 | 769410 | 4 | 91596.4286 | 10.9175
1663 | 1663 | CL3-510 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.852 | 10 | 2.262 | 3 | 1.6965 | 8.4 | 8.4 | 1432500 | 2 | 170535.7143 | 5.8639
1664 | 1664 | CL3-511 | KERRY | KERRY | SS-321 | Milltown 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.104 | 9 | 1.605 | 3 | 1.2037 | 8.4 | 8.4 | 1379800 | 2 | 164261.9048 | 6.0878
1665 | 1665 | CL3-512 | KERRY | KERRY | SS-321 | Milltown 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.488 | 10 | 0.871 | 3 | 0.871 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
1666 | 1666 | CL3-513 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.965 | 9 | 1.233 | 3 | 0.92475 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1667 | 1667 | CL3-514 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 2.277 | 3 | 0.622 | 3 | 0.622 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
1668 | 1668 | CL3-515 | KERRY | KERRY | SS-634 | Inch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.778 | 7 | 0.258 | 3 | 0.258 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1669 | 1669 | CL3-516 | LIMERICK | LIMERICK | SS-378 | Foynes 38kV Substation | ESB Networks | 38000 | 38000 | low | 1.955 | 2 | 0.703 | 3 | 0.703 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007
1670 | 1670 | CL3-517 | LIMERICK | LIMERICK | SS-144 | Monateen 110kV Substation | EirGrid | 110000 |  |  | 6.628 | 7 | 2.567 | 3 | 1.9253 | 12.6 | 12.6 | 1785370 | 7 | 141696.0317 | 7.0574
1671 | 1671 | CL3-518 | LIMERICK | LIMERICK | SS-283 | Mungret | EirGrid | 110000 | 110000 | low | 2.492 | 3 | 1.214 | 3 | 0.9105 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674
1672 | 1672 | CL3-519 | CLARE | CLARE | SS-673 | Drumquin 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 3.723 | 4 | 0.601 | 3 | 0.601 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1673 | 1673 | CL3-520 | CLARE | CLARE | SS-673 | Drumquin 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 3.032 | 4 | 1.018 | 3 | 1.018 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1674 | 1674 | CL3-521 | CLARE | CLARE | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 17.9 | 18 | 0.612 | 3 | 0.612 | 4.2 | 4.2 | 1808740 | 1 | 430652.381 | 2.3221
1675 | 1675 | CL3-522 | CLARE | CLARE | SS-141 | Ennis North 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 13.238 | 14 | 3.107 | 3 | 2.3303 | 16.8 | 16.8 | 1331570 | 4 | 79260.119 | 12.6167
1676 | 1676 | CL3-523 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.133 | 6 | 3.191 | 3 | 2.3933 | 16.8 | 16.8 | 769410 | 4 | 45798.2143 | 21.8349
1677 | 1677 | CL3-524 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.455 | 8 | 2.541 | 3 | 1.9057 | 12.6 | 12.6 | 909950 | 4 | 72218.254 | 13.8469
1678 | 1678 | CL3-525 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.995 | 6 | 8.695 | 3 | 6.5213 | 46.2 | 46.2 | 2183320 | 11 | 47258.0087 | 21.1604
1679 | 1679 | CL3-526 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.087 | 12 | 5.519 | 3 | 4.1393 | 29.4 | 29.4 | 1413750 | 5 | 48086.7347 | 20.7958
1680 | 1680 | CL3-527 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.414 | 11 | 2.498 | 3 | 1.8735 | 12.6 | 12.6 | 1522250 | 3 | 120813.4921 | 8.2772
1681 | 1681 | CL3-528 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 12.726 | 13 | 1.094 | 3 | 1.094 | 4.2 | 4.2 | 2101570 | 7 | 500373.8095 | 1.9985
1682 | 1682 | CL3-529 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.096 | 11 | 1.141 | 3 | 1.141 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
1683 | 1683 | CL3-530 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.72 | 7 | 3.529 | 3 | 2.6467 | 16.8 | 16.8 | 839680 | 4 | 49980.9524 | 20.0076
1684 | 1684 | CL3-531 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.647 | 10 | 3.963 | 3 | 2.9722 | 21 | 21 | 1050490 | 4 | 50023.3333 | 19.9907
1685 | 1685 | CL3-532 | MAYO | MAYO | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 20.501 | 21 | 3.887 | 3 | 2.9152 | 21 | 21 | 1823460 | 4 | 86831.4286 | 11.5166
1686 | 1686 | CL3-533 | MAYO | GALWAY | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 19.671 | 20 | 0.941 | 3 | 0.941 | 4.2 | 4.2 | 1914140 | 1 | 455747.619 | 2.1942
1687 | 1687 | CL3-534 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 17.823 | 18 | 2.344 | 3 | 1.758 | 8.4 | 8.4 | 1854100 | 2 | 220726.1905 | 4.5305
1688 | 1688 | CL3-535 | GALWAY | GALWAY | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 18.09 | 19 | 1.022 | 3 | 1.022 | 4.2 | 4.2 | 1861440 | 1 | 443200 | 2.2563
1689 | 1689 | CL3-536 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 16.436 | 17 | 0.688 | 3 | 0.688 | 4.2 | 4.2 | 1756040 | 1 | 418104.7619 | 2.3917
1690 | 1690 | CL3-537 | GALWAY | GALWAY | SS-105 | Garroman 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.877 | 16 | 0.939 | 3 | 0.939 | 4.2 | 4.2 | 1703340 | 1 | 405557.1429 | 2.4657
1691 | 1691 | CL3-538 | MAYO | MAYO | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 17.894 | 18 | 4.17 | 3 | 3.1275 | 21 | 21 | 1612650 | 4 | 76792.8571 | 13.022
1692 | 1692 | CL3-539 | MAYO | MAYO | SS-233 | Cong 38kV station | ESB Networks | 38000 | 38000 | low | 18.107 | 19 | 1.514 | 3 | 1.1355 | 4.2 | 4.2 | 1861440 | 1 | 443200 | 2.2563
1693 | 1693 | CL3-540 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 17.296 | 18 | 1.008 | 3 | 1.008 | 4.2 | 4.2 | 1808740 | 1 | 430652.381 | 2.3221
1694 | 1694 | CL3-541 | GALWAY | GALWAY | SS-207 | Screeb 110kV Substation | EirGrid | 110000 |  |  | 12.464 | 13 | 1.151 | 3 | 1.151 | 4.2 | 4.2 | 2101570 | 7 | 500373.8095 | 1.9985
1695 | 1695 | CL3-542 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 23.74 | 24 | 0.719 | 3 | 0.719 | 4.2 | 4.2 | 2681270 | 7 | 638397.619 | 1.5664
1696 | 1696 | CL3-543 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 20.671 | 21 | 0.843 | 3 | 0.843 | 4.2 | 4.2 | 1966840 | 1 | 468295.2381 | 2.1354
1697 | 1697 | CL3-544 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 23.227 | 24 | 0.814 | 3 | 0.814 | 4.2 | 4.2 | 2681270 | 7 | 638397.619 | 1.5664
1698 | 1698 | CL3-545 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 23.214 | 24 | 1.487 | 3 | 1.1153 | 4.2 | 4.2 | 2681270 | 7 | 638397.619 | 1.5664
1699 | 1699 | CL3-546 | MAYO | MAYO | SS-461 | Westport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 18.716 | 19 | 1.534 | 3 | 1.1505 | 4.2 | 4.2 | 1861440 | 1 | 443200 | 2.2563
1700 | 1700 | CL3-547 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 29.767 | 30 | 1.22 | 3 | 0.915 | 4.2 | 4.2 | 2997470 | 7 | 713683.3333 | 1.4012
1701 | 1701 | CL3-548 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 25.087 | 26 | 4.013 | 3 | 3.0097 | 21 | 21 | 3421730 | 8 | 162939.5238 | 6.1372
1702 | 1702 | CL3-549 | MAYO | MAYO | SS-073 | Carrowbeg 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 27.731 | 28 | 3.555 | 3 | 2.6663 | 16.8 | 16.8 | 3562270 | 8 | 212039.881 | 4.7161
1703 | 1703 | CL3-550 | MAYO | MAYO | SS-317 | Newport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.898 | 12 | 2.296 | 3 | 1.722 | 8.4 | 8.4 | 1537900 | 2 | 183083.3333 | 5.462
1704 | 1704 | CL3-551 | MAYO | MAYO | SS-170 | Derrynadivva 38kV Substation | ESB Networks | 38000 | low | 38000 | 10.787 | 11 | 3.823 | 3 | 2.8672 | 16.8 | 16.8 | 1120760 | 4 | 66711.9048 | 14.9898
1705 | 1705 | CL3-552 | MAYO | MAYO | SS-317 | Newport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.975 | 10 | 5.846 | 3 | 4.3845 | 29.4 | 29.4 | 1236090 | 5 | 42043.8776 | 23.7847
1706 | 1706 | CL3-553 | MAYO | MAYO | SS-133 | Bellacorrick 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 12.74 | 13 | 5.267 | 3 | 3.9503 | 25.2 | 25.2 | 3108640 | 9 | 123358.7302 | 8.1064
1707 | 1707 | CL3-554 | SLIGO | SLIGO | SS-302 | Carrowleagh 38kV Substation | ESB Networks | 38000 | low | 38000 | 5.119 | 6 | 9.462 | 3 | 7.0965 | 50.4 | 50.4 | 2183320 | 11 | 43319.8413 | 23.0841
1708 | 1708 | CL3-555 | SLIGO | SLIGO | SS-075 | Cunghill 110kV Substation | EirGrid | 110000 | 110000 | medium | 8.035 | 9 | 3.563 | 3 | 2.6723 | 16.8 | 16.8 | 2227140 | 8 | 132567.8571 | 7.5433
1709 | 1709 | CL3-556 | SLIGO | SLIGO | SS-074 | Tobercurry 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.229 | 9 | 1.111 | 3 | 1.111 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1710 | 1710 | CL3-557 | SLIGO | SLIGO | SS-042 | Ballytivnan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 11.682 | 12 | 4.114 | 3 | 3.0855 | 21 | 21 | 1191030 | 4 | 56715.7143 | 17.6318
1711 | 1711 | CL3-558 | LEITRIM | LEITRIM | SS-227 | Bundoran 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.708 | 12 | 0.636 | 3 | 0.636 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
1712 | 1712 | CL3-559 | SLIGO | SLIGO | SS-031 | Sligo 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 4.082 | 5 | 0.644 | 3 | 0.644 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5
1713 | 1713 | CL3-560 | DONEGAL | DONEGAL | SS-250 | Kilcar 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 5.057 | 6 | 2.5 | 3 | 1.875 | 12.6 | 12.6 | 769410 | 4 | 61064.2857 | 16.3762
1714 | 1714 | CL3-561 | DONEGAL | DONEGAL | SS-252 | Killybegs 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 3.837 | 4 | 0.545 | 3 | 0.545 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1715 | 1715 | CL3-562 | MAYO | MAYO | SS-642 | Achill 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 20.885 | 21 | 0.947 | 3 | 0.947 | 4.2 | 4.2 | 1966840 | 1 | 468295.2381 | 2.1354
1716 | 1716 | CL3-563 | ROSCOMMON | ROSCOMMON | SS-206 | Boyle 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.298 | 8 | 0.684 | 3 | 0.684 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1717 | 1717 | CL3-564 | ROSCOMMON | ROSCOMMON | SS-166 | Tonroe 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 3.877 | 4 | 0.904 | 3 | 0.904 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581
1718 | 1718 | CL3-565 | SLIGO | LEITRIM | SS-128 | Garvagh Glebe 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 2.076 | 3 | 4.4 | 3 | 3.3 | 21 | 21 | 1550890 | 11 | 73851.9048 | 13.5406
1719 | 1719 | CL3-566 | LEITRIM | LEITRIM | SS-128 | Garvagh Glebe 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 3.924 | 4 | 0.305 | 3 | 0.305 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581
1720 | 1720 | CL3-567 | LEITRIM | LEITRIM | SS-534 | Garvagh Glebe 110kV Substation Extension | EirGrid | 110000 | 20000 | 110000 | 1.433 | 2 | 0.96 | 3 | 0.96 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341
1721 | 1721 | CL3-568 | CARLOW | CARLOW | SS-481 | Castledockrell 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 11.949 | 12 | 0.414 | 3 | 0.414 | 4.2 | 4.2 | 2048870 | 7 | 487826.1905 | 2.0499
1722 | 1722 | CL3-569 | CARLOW | WEXFORD | SS-481 | Castledockrell 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 9.698 | 10 | 1.694 | 3 | 1.2705 | 8.4 | 8.4 | 1943470 | 7 | 231365.4762 | 4.3222
1723 | 1723 | CL3-570 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.561 | 11 | 0.599 | 3 | 0.599 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
1724 | 1724 | CL3-571 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.19 | 8 | 1.071 | 3 | 1.071 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1725 | 1725 | CL3-572 | WICKLOW | WICKLOW | SS-600 | Rathdrum 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.722 | 7 | 1.005 | 3 | 1.005 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1726 | 1726 | CL3-573 | WICKLOW | WICKLOW | SS-699 | Ballycumber 38kV Substation | ESB Networks | 38000 | low | 38000 | 11.665 | 12 | 3.947 | 3 | 2.9603 | 21 | 21 | 1191030 | 4 | 56715.7143 | 17.6318
1727 | 1727 | CL3-574 | WICKLOW | WICKLOW | SS-062 | Stratford 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.948 | 6 | 1.028 | 3 | 1.028 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424
1728 | 1728 | CL3-575 | WICKLOW | WICKLOW | SS-010 | Fassaroe 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 12.405 | 13 | 0.535 | 3 | 0.535 | 4.2 | 4.2 | 2101570 | 7 | 500373.8095 | 1.9985
1729 | 1729 | CL3-576 | WICKLOW | WICKLOW | SS-616 | Ballinvally 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 2.489 | 3 | 0.648 | 3 | 0.648 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
1730 | 1730 | CL3-577 | WICKLOW | WICKLOW | SS-699 | Ballycumber 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.985 | 2 | 0.607 | 3 | 0.607 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007
1731 | 1731 | CL3-578 | KERRY | KERRY | SS-637 | Kilgarvan 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 6.059 | 7 | 0.657 | 3 | 0.657 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1732 | 1732 | CL3-579 | KERRY | KERRY | SS-668 | Coomataggart 110 kV Substation | EirGrid | 110000 | low | 110000 | 1.397 | 2 | 1.197 | 3 | 1.197 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341
1733 | 1733 | CL3-580 | CORK | CORK | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.31 | 4 | 1.422 | 3 | 1.0665 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1734 | 1734 | CL3-581 | CORK | CORK | SS-077 | Curraglass 38kV Substation | ESB Networks | 38000 | low | 38000 | 2.519 | 3 | 0.664 | 3 | 0.664 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
1735 | 1735 | CL3-582 | KERRY | KERRY | SS-071 | Coomagearlahy Substation | EirGrid | 110000 | medium-low | 110000 | 2.652 | 3 | 0.639 | 3 | 0.639 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674
1736 | 1736 | CL3-583 | KERRY | KERRY | SS-072 | Clonkeen 110kV Substation | EirGrid | 110000 |  |  | 2.391 | 3 | 0.823 | 3 | 0.823 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674
1737 | 1737 | CL3-584 | KERRY | KERRY | SS-072 | Clonkeen 110kV Substation | EirGrid | 110000 |  |  | 5.528 | 6 | 1.123 | 3 | 1.123 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424
1738 | 1738 | CL3-585 | KERRY | KERRY | SS-162 | Garrow 110kV Substation | EirGrid | 110000 | 38000 | 110000 | 3.611 | 4 | 1.05 | 3 | 1.05 | 4.2 | 4.2 | 1627270 | 7 | 387445.2381 | 2.581
1739 | 1739 | CL3-586 | KERRY | KERRY | SS-072 | Clonkeen 110kV Substation | EirGrid | 110000 |  |  | 5.537 | 6 | 1.101 | 3 | 1.101 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424
1740 | 1740 | CL3-587 | CORK | KERRY | SS-327 | Rathmore 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.212 | 7 | 0.646 | 3 | 0.646 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1741 | 1741 | CL3-588 | CORK | CORK | SS-161 | Gneeves 38kV Substation | ESB Networks | 38000 | low | 38000 | 7.137 | 8 | 2.316 | 3 | 1.737 | 8.4 | 8.4 | 909950 | 4 | 108327.381 | 9.2313
1742 | 1742 | CL3-589 | CORK | CORK | SS-096 | Boggeragh 110kV Substation | EirGrid | 110000 |  |  | 2.427 | 3 | 0.284 | 3 | 0.284 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674
1743 | 1743 | CL3-590 | CORK | CORK | SS-615 | Knockduff 110kv Substation | EirGrid | 110000 |  |  | 4.292 | 5 | 2.073 | 3 | 1.5547 | 8.4 | 8.4 | 1679970 | 7 | 199996.4286 | 5.0001
1744 | 1744 | CL3-591 | CORK | CORK | SS-096 | Boggeragh 110kV Substation | EirGrid | 110000 |  |  | 1.943 | 2 | 0.446 | 3 | 0.446 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341
1745 | 1745 | CL3-592 | WATERFORD | WATERFORD | SS-532 | Woodhouse 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 1.716 | 2 | 0.877 | 3 | 0.877 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341
1746 | 1746 | CL3-593 | TIPPERARY | LAOIS | SS-666 | 38kV Substation | ESB Networks | 38000 | low | 38000 | 3.453 | 4 | 0.719 | 3 | 0.719 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1747 | 1747 | CL3-594 | TIPPERARY | TIPPERARY | SS-666 | 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.258 | 2 | 0.401 | 3 | 0.401 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007
1748 | 1748 | CL3-595 | KILDARE | LAOIS | SS-034 | Athy 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 6.786 | 7 | 1.913 | 3 | 1.4347 | 8.4 | 8.4 | 1785370 | 7 | 212544.0476 | 4.7049
1749 | 1749 | CL3-596 | LIMERICK | LIMERICK | SS-069 | Garryspillane 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.7 | 5 | 0.46 | 3 | 0.46 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1750 | 1750 | CL3-597 | CLARE | CLARE | SS-116 | Ardnacrusha 110kV Substation | EirGrid | 110000 | low | 110000 | 8.285 | 9 | 1.211 | 3 | 0.90825 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213
1751 | 1751 | CL3-598 | GALWAY | GALWAY | SS-459 | Ballycrossaun 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.476 | 3 | 0.831 | 3 | 0.831 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
1752 | 1752 | CL3-599 | TIPPERARY | TIPPERARY | SS-483 | Birdhill 38kV Substation | ESB Networks | 38000 | 38000 | low | 1.799 | 2 | 0.336 | 3 | 0.336 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007
1753 | 1753 | CL3-600 | OFFALY | OFFALY | SS-551 | Dallow 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 4.925 | 5 | 0.317 | 3 | 0.317 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5
1754 | 1754 | CL3-601 | GALWAY | GALWAY | SS-459 | Ballycrossaun 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.377 | 4 | 0.436 | 3 | 0.436 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1755 | 1755 | CL3-602 | GALWAY | GALWAY | SS-502 | Ballinasloe 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 2.734 | 3 | 0.417 | 3 | 0.417 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
1756 | 1756 | CL3-603 | GALWAY | GALWAY | SS-269 | Shannonbridge 110kV Substation | EirGrid | 110000 | low | 110000 | 1.595 | 2 | 0.554 | 3 | 0.554 | 4.2 | 4.2 | 1340080 | 11 | 319066.6667 | 3.1341
1757 | 1757 | CL3-604 | GALWAY | GALWAY | SS-338 | Banagher 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.143 | 3 | 0.825 | 3 | 0.825 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
1758 | 1758 | CL3-605 | GALWAY | GALWAY | SS-269 | Shannonbridge 110kV Substation | EirGrid | 110000 | low | 110000 | 4.214 | 5 | 1.588 | 3 | 1.191 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5
1759 | 1759 | CL3-606 | OFFALY | OFFALY | SS-269 | Shannonbridge 110kV Substation | EirGrid | 110000 | low | 110000 | 7.047 | 8 | 1.723 | 3 | 1.2923 | 8.4 | 8.4 | 1838070 | 7 | 218817.8571 | 4.57
1760 | 1760 | CL3-607 | OFFALY | OFFALY | SS-269 | Shannonbridge 110kV Substation | EirGrid | 110000 | low | 110000 | 6.966 | 7 | 0.472 | 3 | 0.472 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525
1761 | 1761 | CL3-608 | OFFALY | OFFALY | SS-269 | Shannonbridge 110kV Substation | EirGrid | 110000 | low | 110000 | 8.204 | 9 | 1.022 | 3 | 1.022 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213
1762 | 1762 | CL3-609 | MEATH | MEATH | SS-376 | Kells 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.788 | 7 | 1.75 | 3 | 1.3125 | 8.4 | 8.4 | 839680 | 4 | 99961.9048 | 10.0038
1763 | 1763 | CL3-610 | OFFALY | OFFALY | SS-231 | Lumcloon 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.135 | 7 | 1.07 | 3 | 1.07 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1764 | 1764 | CL3-611 | OFFALY | OFFALY | SS-231 | Lumcloon 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.191 | 8 | 10.428 | 3 | 7.821 | 54.6 | 54.6 | 2604940 | 11 | 47709.5238 | 20.9602
1765 | 1765 | CL3-612 | OFFALY | OFFALY | SS-231 | Lumcloon 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.87 | 6 | 0.858 | 3 | 0.858 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1766 | 1766 | CL3-613 | OFFALY | WESTMEATH | SS-168 | Derryiron 110kV Substation | EirGrid | 110000 |  |  | 4.91 | 5 | 0.775 | 3 | 0.775 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5
1767 | 1767 | CL3-614 | OFFALY | WESTMEATH | SS-168 | Derryiron 110kV Substation | EirGrid | 110000 |  |  | 6.522 | 7 | 1.577 | 3 | 1.1827 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525
1768 | 1768 | CL3-615 | OFFALY | WESTMEATH | SS-059 | Kinnegad 110kV | EirGrid | 110000 |  |  | 4.547 | 5 | 1.792 | 3 | 1.344 | 8.4 | 8.4 | 1679970 | 7 | 199996.4286 | 5.0001
1769 | 1769 | CL3-616 | KILDARE | LAOIS | SS-034 | Athy 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 9.667 | 10 | 0.662 | 3 | 0.662 | 4.2 | 4.2 | 1943470 | 7 | 462730.9524 | 2.1611
1770 | 1770 | CL3-617 | KILDARE | OFFALY | SS-167 | Cushaling 110kV Substation | EirGrid | 110000 | low | 110000 | 4.152 | 5 | 3.41 | 3 | 2.5575 | 16.8 | 16.8 | 1946060 | 8 | 115836.9048 | 8.6328
1771 | 1771 | CL3-618 | KILDARE | KILDARE | SS-216 | Blake 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.442 | 6 | 2.046 | 3 | 1.5345 | 8.4 | 8.4 | 1732670 | 7 | 206270.2381 | 4.848
1772 | 1772 | CL3-619 | OFFALY | OFFALY | SS-167 | Cushaling 110kV Substation | EirGrid | 110000 | low | 110000 | 5.708 | 6 | 3.393 | 3 | 2.5447 | 16.8 | 16.8 | 2016330 | 8 | 120019.6429 | 8.332
1773 | 1773 | CL3-620 | OFFALY | OFFALY | SS-167 | Cushaling 110kV Substation | EirGrid | 110000 | low | 110000 | 7.357 | 8 | 0.372 | 3 | 0.372 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285
1774 | 1774 | CL3-621 | OFFALY | OFFALY | SS-469 | Portarlington 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.1 | 7 | 4.026 | 3 | 3.0195 | 21 | 21 | 839680 | 4 | 39984.7619 | 25.0095
1775 | 1775 | CL3-622 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 7.991 | 8 | 1.071 | 3 | 1.071 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285
1776 | 1776 | CL3-623 | ROSCOMMON | ROSCOMMON | SS-124 | Roscommon 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.179 | 7 | 0.448 | 3 | 0.448 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1777 | 1777 | CL3-624 | LONGFORD | LONGFORD | SS-563 | Ballymahon 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.757 | 5 | 0.529 | 3 | 0.529 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1778 | 1778 | CL3-625 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.104 | 8 | 0.431 | 3 | 0.431 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1779 | 1779 | CL3-626 | CAVAN | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.161 | 10 | 6.311 | 3 | 4.7332 | 33.6 | 33.6 | 1460390 | 6 | 43463.9881 | 23.0076
1780 | 1780 | CL3-627 | LEITRIM | LEITRIM | SS-097 | Corderry 110kV Substation | EirGrid | 110000 |  |  | 5.724 | 6 | 0.583 | 3 | 0.583 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424
1781 | 1781 | CL3-628 | LEITRIM | LEITRIM | SS-097 | Corderry 110kV Substation | EirGrid | 110000 |  |  | 4.539 | 5 | 0.304 | 3 | 0.304 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5
1782 | 1782 | CL3-629 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.687 | 5 | 1.223 | 3 | 0.91725 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1783 | 1783 | CL3-630 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.426 | 8 | 0.336 | 3 | 0.336 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1784 | 1784 | CL3-631 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.311 | 10 | 0.316 | 3 | 0.316 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
1785 | 1785 | CL3-632 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 11.148 | 12 | 0.178 | 3 | 0.178 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
1786 | 1786 | CL3-633 | CAVAN | CAVAN | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 13.253 | 14 | 0.624 | 3 | 0.624 | 4.2 | 4.2 | 1597940 | 1 | 380461.9048 | 2.6284
1787 | 1787 | CL3-634 | CAVAN | CAVAN | SS-110 | Corraclassy 110kV Substation | EirGrid | 110000 |  |  | 5.913 | 6 | 0.452 | 3 | 0.452 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424
1788 | 1788 | CL3-635 | CAVAN | LEITRIM | SS-110 | Corraclassy 110kV Substation | EirGrid | 110000 |  |  | 9.348 | 10 | 3.572 | 3 | 2.679 | 16.8 | 16.8 | 2297410 | 8 | 136750.5952 | 7.3126
1789 | 1789 | CL3-636 | LEITRIM | LEITRIM | SS-304 | Arigna 110kV Substation | EirGrid | 110000 | 110000 | 20000 | 10.487 | 11 | 2.433 | 3 | 1.8247 | 12.6 | 12.6 | 1996170 | 7 | 158426.1905 | 6.3121
1790 | 1790 | CL3-637 | LEITRIM | LEITRIM | SS-304 | Arigna 110kV Substation | EirGrid | 110000 | 110000 | 20000 | 9.407 | 10 | 2.701 | 3 | 2.0257 | 12.6 | 12.6 | 1943470 | 7 | 154243.6508 | 6.4832
1791 | 1791 | CL3-638 | LEITRIM | LEITRIM | SS-304 | Arigna 110kV Substation | EirGrid | 110000 | 110000 | 20000 | 4.862 | 5 | 0.539 | 3 | 0.539 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5
1792 | 1792 | CL3-639 | LEITRIM | LEITRIM | SS-304 | Arigna 110kV Substation | EirGrid | 110000 | 110000 | 20000 | 6.037 | 7 | 1.283 | 3 | 0.96225 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525
1793 | 1793 | CL3-640 | CAVAN | CAVAN | SS-110 | Corraclassy 110kV Substation | EirGrid | 110000 |  |  | 8.21 | 9 | 4.621 | 3 | 3.4658 | 21 | 21 | 2227140 | 8 | 106054.2857 | 9.4291
1794 | 1794 | CL3-641 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 4.509 | 5 | 1.173 | 3 | 1.173 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1795 | 1795 | CL3-642 | DONEGAL | DONEGAL | SS-688 | Clogher 110kV Substation | EirGrid | 110000 |  |  | 9.53 | 10 | 2.006 | 3 | 1.5045 | 8.4 | 8.4 | 1943470 | 7 | 231365.4762 | 4.3222
1796 | 1796 | CL3-643 | DONEGAL | DONEGAL | SS-688 | Clogher 110kV Substation | EirGrid | 110000 |  |  | 11.189 | 12 | 1.053 | 3 | 1.053 | 4.2 | 4.2 | 2048870 | 7 | 487826.1905 | 2.0499
1797 | 1797 | CL3-644 | DONEGAL | DONEGAL | SS-083 | Golagh 110kV Substation | EirGrid | 110000 | 38000 | 110000 | 10.141 | 11 | 3.925 | 3 | 2.9437 | 21 | 21 | 2367680 | 8 | 112746.6667 | 8.8694
1798 | 1798 | CL3-645 | DONEGAL | DONEGAL | SS-688 | Clogher 110kV Substation | EirGrid | 110000 |  |  | 7.895 | 8 | 0.869 | 3 | 0.869 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285
1799 | 1799 | CL3-646 | DONEGAL | DONEGAL | SS-684 | Tievebrack 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 11.207 | 12 | 3.235 | 3 | 2.4263 | 16.8 | 16.8 | 2437950 | 8 | 145116.0714 | 6.891
1800 | 1800 | CL3-647 | DONEGAL | DONEGAL | SS-688 | Clogher 110kV Substation | EirGrid | 110000 |  |  | 6.222 | 7 | 0.913 | 3 | 0.913 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525
1801 | 1801 | CL3-648 | DONEGAL | DONEGAL | SS-083 | Golagh 110kV Substation | EirGrid | 110000 | 38000 | 110000 | 5.815 | 6 | 1.144 | 3 | 1.144 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424
1802 | 1802 | CL3-649 | DONEGAL | DONEGAL | SS-688 | Clogher 110kV Substation | EirGrid | 110000 |  |  | 8.118 | 9 | 1.82 | 3 | 1.365 | 8.4 | 8.4 | 1890770 | 7 | 225091.6667 | 4.4426
1803 | 1803 | CL3-650 | DONEGAL | DONEGAL | SS-102 | Binbane 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.078 | 6 | 1.277 | 3 | 0.95775 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424
1804 | 1804 | CL3-651 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 4.767 | 5 | 2.178 | 3 | 1.6335 | 8.4 | 8.4 | 699140 | 4 | 83230.9524 | 12.0148
1805 | 1805 | CL3-652 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 1.881 | 2 | 0.333 | 3 | 0.333 | 4.2 | 4.2 | 488330 | 4 | 116269.0476 | 8.6007
1806 | 1806 | CL3-653 | TIPPERARY | WATERFORD | SS-630 | Lismore 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.579 | 9 | 5.912 | 3 | 4.434 | 29.4 | 29.4 | 1147260 | 5 | 39022.449 | 25.6263
1807 | 1807 | CL3-654 | TIPPERARY | TIPPERARY | SS-455 | Ardfinnan 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.115 | 8 | 8.175 | 3 | 6.1313 | 42 | 42 | 1237870 | 6 | 29473.0952 | 33.9292
1808 | 1808 | CL3-655 | TIPPERARY | TIPPERARY | SS-455 | Ardfinnan 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.27 | 7 | 0.86 | 3 | 0.86 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1809 | 1809 | CL3-656 | TIPPERARY | TIPPERARY | SS-455 | Ardfinnan 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.353 | 10 | 1.135 | 3 | 1.135 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
1810 | 1810 | CL3-657 | TIPPERARY | WATERFORD | SS-507 | Kilcloher 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.187 | 9 | 3.326 | 3 | 2.4945 | 16.8 | 16.8 | 980220 | 4 | 58346.4286 | 17.139
1811 | 1811 | CL3-658 | TIPPERARY | WATERFORD | SS-507 | Kilcloher 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.871 | 10 | 0.76 | 3 | 0.76 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
1812 | 1812 | CL3-659 | TIPPERARY | WATERFORD | SS-622 | Barranafaddock 38kV Substation | ESB Networks | 38000 | low | 38000 | 9.556 | 10 | 10.954 | 3 | 8.2155 | 58.8 | 58.8 | 3026560 | 11 | 51472.1088 | 19.428
1813 | 1813 | CL3-660 | TIPPERARY | TIPPERARY | SS-622 | Barranafaddock 38kV Substation | ESB Networks | 38000 | low | 38000 | 9.24 | 10 | 2.564 | 3 | 1.923 | 12.6 | 12.6 | 1469550 | 3 | 116630.9524 | 8.5741
1814 | 1814 | CL3-661 | TIPPERARY | WATERFORD | SS-455 | Ardfinnan 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.537 | 9 | 1.658 | 3 | 1.2435 | 8.4 | 8.4 | 1379800 | 2 | 164261.9048 | 6.0878
1815 | 1815 | CL3-662 | WATERFORD | WATERFORD | SS-659 | Spa Road 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 12.24 | 13 | 1.493 | 3 | 1.1198 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718
1816 | 1816 | CL3-663 | WATERFORD | WATERFORD | SS-659 | Spa Road 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 12.173 | 13 | 4.399 | 3 | 3.2992 | 21 | 21 | 1261300 | 4 | 60061.9048 | 16.6495
1817 | 1817 | CL3-664 | WATERFORD | WATERFORD | SS-659 | Spa Road 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.965 | 8 | 0.927 | 3 | 0.927 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1818 | 1818 | CL3-665 | WATERFORD | WATERFORD | SS-659 | Spa Road 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 6.394 | 7 | 1.91 | 3 | 1.4325 | 8.4 | 8.4 | 839680 | 4 | 99961.9048 | 10.0038
1819 | 1819 | CL3-666 | WATERFORD | WATERFORD | SS-659 | Spa Road 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 3.454 | 4 | 4.15 | 3 | 3.1125 | 21 | 21 | 628870 | 4 | 29946.1905 | 33.3932
1820 | 1820 | CL3-667 | WATERFORD | WATERFORD | SS-064 | Ballydine 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 7.385 | 8 | 1.165 | 3 | 1.165 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285
1821 | 1821 | CL3-668 | WATERFORD | WATERFORD | SS-505 | Kilmacthomas 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.802 | 9 | 1.419 | 3 | 1.0642 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1822 | 1822 | CL3-669 | WATERFORD | WATERFORD | SS-505 | Kilmacthomas 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.49 | 11 | 4.499 | 3 | 3.3742 | 21 | 21 | 1120760 | 4 | 53369.5238 | 18.7373
1823 | 1823 | CL3-670 | WATERFORD | WATERFORD | SS-205 | Dungarvan 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 9.594 | 10 | 4.244 | 3 | 3.183 | 21 | 21 | 2297410 | 8 | 109400.4762 | 9.1407
1824 | 1824 | CL3-671 | WATERFORD | WATERFORD | SS-205 | Dungarvan 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 12.85 | 13 | 2.059 | 3 | 1.5443 | 8.4 | 8.4 | 2101570 | 7 | 250186.9048 | 3.997
1825 | 1825 | CL3-672 | CORK | CORK | SS-193 | Charleville 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 4.099 | 5 | 0.686 | 3 | 0.686 | 4.2 | 4.2 | 1679970 | 7 | 399992.8571 | 2.5
1826 | 1826 | CL3-673 | LIMERICK | LIMERICK | SS-695 | Castlepook 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 2.406 | 3 | 0.627 | 3 | 0.627 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
1827 | 1827 | CL3-674 | CORK | LIMERICK | SS-695 | Castlepook 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 2.284 | 3 | 17.711 | 3 | 13.2832 | 92.4 | 92.4 | 1550890 | 11 | 16784.5238 | 59.5787
1828 | 1828 | CL3-675 | LIMERICK | LIMERICK | SS-695 | Castlepook 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 2.222 | 3 | 1.462 | 3 | 1.0965 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
1829 | 1829 | CL3-676 | TIPPERARY | TIPPERARY | SS-585 | Kilross Road 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.642 | 10 | 2.177 | 3 | 1.6328 | 8.4 | 8.4 | 1432500 | 2 | 170535.7143 | 5.8639
1830 | 1830 | CL3-677 | TIPPERARY | TIPPERARY | SS-585 | Kilross Road 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.186 | 10 | 2.65 | 3 | 1.9875 | 12.6 | 12.6 | 1469550 | 3 | 116630.9524 | 8.5741
1831 | 1831 | CL3-678 | TIPPERARY | TIPPERARY | SS-127 | Tipperary 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 9.424 | 10 | 5.185 | 3 | 3.8887 | 25.2 | 25.2 | 2842150 | 9 | 112783.7302 | 8.8665
1832 | 1832 | CL3-679 | TIPPERARY | TIPPERARY | SS-315 | Cahir 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 8.272 | 9 | 2.206 | 3 | 1.6545 | 8.4 | 8.4 | 1379800 | 2 | 164261.9048 | 6.0878
1833 | 1833 | CL3-680 | TIPPERARY | TIPPERARY | SS-315 | Cahir 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 11.786 | 12 | 19.966 | 3 | 14.9745 | 105 | 105 | 3448180 | 11 | 32839.8095 | 30.4508
1834 | 1834 | CL3-681 | TIPPERARY | LIMERICK | SS-257 | Kilshanny 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.062 | 11 | 3.94 | 3 | 2.955 | 21 | 21 | 1120760 | 4 | 53369.5238 | 18.7373
1835 | 1835 | CL3-682 | LIMERICK | LIMERICK | SS-257 | Kilshanny 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.646 | 9 | 1.834 | 3 | 1.3755 | 8.4 | 8.4 | 1379800 | 2 | 164261.9048 | 6.0878
1836 | 1836 | CL3-683 | LIMERICK | LIMERICK | SS-257 | Kilshanny 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.526 | 8 | 1.726 | 3 | 1.2945 | 8.4 | 8.4 | 909950 | 4 | 108327.381 | 9.2313
1837 | 1837 | CL3-684 | TIPPERARY | TIPPERARY | SS-347 | Glengoole 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.077 | 3 | 0.407 | 3 | 0.407 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
1838 | 1838 | CL3-685 | TIPPERARY | TIPPERARY | SS-347 | Glengoole 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.018 | 4 | 0.7 | 3 | 0.7 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1839 | 1839 | CL3-686 | TIPPERARY | TIPPERARY | SS-347 | Glengoole 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.582 | 5 | 1.894 | 3 | 1.4205 | 8.4 | 8.4 | 699140 | 4 | 83230.9524 | 12.0148
1840 | 1840 | CL3-687 | TIPPERARY | TIPPERARY | SS-347 | Glengoole 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.959 | 6 | 0.862 | 3 | 0.862 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1841 | 1841 | CL3-688 | TIPPERARY | TIPPERARY | SS-551 | Dallow 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.689 | 9 | 0.499 | 3 | 0.499 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213
1842 | 1842 | CL3-689 | TIPPERARY | TIPPERARY | SS-551 | Dallow 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.173 | 9 | 0.496 | 3 | 0.496 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213
1843 | 1843 | CL3-690 | LAOIS | LAOIS | SS-469 | Portarlington 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.825 | 9 | 0.419 | 3 | 0.419 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1844 | 1844 | CL3-691 | GALWAY | GALWAY | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.739 | 9 | 0.788 | 3 | 0.788 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1845 | 1845 | CL3-692 | GALWAY | GALWAY | SS-236 | Creagh 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 5.458 | 6 | 0.501 | 3 | 0.501 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1846 | 1846 | CL3-693 | CORK | CORK | SS-583 | Castletownroche 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.505 | 8 | 0.243 | 3 | 0.243 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1847 | 1847 | CL3-694 | WATERFORD | WATERFORD | SS-016 | Portlaw 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.572 | 4 | 1.174 | 3 | 1.174 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1848 | 1848 | CL3-695 | CARLOW | CARLOW | SS-492 | Graigue 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.552 | 9 | 1.156 | 3 | 1.156 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1849 | 1849 | CL3-696 | KILDARE | KILDARE | SS-035 | Athy South 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.878 | 7 | 0.481 | 3 | 0.481 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1850 | 1850 | CL3-697 | KILDARE | OFFALY | SS-469 | Portarlington 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.981 | 8 | 3.899 | 3 | 2.9242 | 21 | 21 | 909950 | 4 | 43330.9524 | 23.0782
1851 | 1851 | CL3-698 | GALWAY | GALWAY | SS-120 | Carhoon 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 9.281 | 10 | 0.748 | 3 | 0.748 | 4.2 | 4.2 | 1943470 | 7 | 462730.9524 | 2.1611
1852 | 1852 | CL3-699 | TIPPERARY | TIPPERARY | SS-594 | Kill Hill 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 8.476 | 9 | 0.816 | 3 | 0.816 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213
1853 | 1853 | CL3-700 | TIPPERARY | TIPPERARY | SS-185 | Anner 110kV Substation | EirGrid | 110000 | 110000 | low | 6.585 | 7 | 2.021 | 3 | 1.5157 | 8.4 | 8.4 | 1785370 | 7 | 212544.0476 | 4.7049
1854 | 1854 | CL3-701 | TIPPERARY | TIPPERARY | SS-295 | Doon 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 7.095 | 8 | 1.094 | 3 | 1.094 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285
1855 | 1855 | CL3-702 | WEXFORD | WEXFORD | SS-092 | Crane 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 7.884 | 8 | 0.431 | 3 | 0.431 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285
1856 | 1856 | CL3-703 | LIMERICK | LIMERICK | SS-596 | Cappamore 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.92 | 4 | 0.388 | 3 | 0.388 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1857 | 1857 | CL3-704 | GALWAY | GALWAY | SS-459 | Ballycrossaun 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.726 | 9 | 0.548 | 3 | 0.548 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1858 | 1858 | CL3-705 | TIPPERARY | OFFALY | SS-645 | Toomevara 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.876 | 4 | 0.883 | 3 | 0.883 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1859 | 1859 | CL3-706 | CLARE | CLARE | SS-134 | Ennistymon 38kV Substation | ESB Networks | 38000 | 38000 | low | 17.703 | 18 | 0.656 | 3 | 0.656 | 4.2 | 4.2 | 1808740 | 1 | 430652.381 | 2.3221
1860 | 1860 | CL3-707 | LAOIS | LAOIS | SS-537 | Monaincha 38kV Substation | ESB Networks | 38000 | 20000 | 38000 | 11.906 | 12 | 0.303 | 3 | 0.303 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
1861 | 1861 | CL3-708 | OFFALY | OFFALY | SS-084 | Birr 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.418 | 13 | 0.44 | 3 | 0.44 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718
1862 | 1862 | CL3-709 | OFFALY | OFFALY | SS-231 | Lumcloon 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.757 | 7 | 0.871 | 3 | 0.871 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1863 | 1863 | CL3-710 | OFFALY | WESTMEATH | SS-467 | Clara 38kV Substation | ESB Networks | 38000 | 38000 | 20000;10000 | 4.048 | 5 | 0.371 | 3 | 0.371 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1864 | 1864 | CL3-711 | GALWAY | GALWAY | SS-236 | Creagh 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.018 | 9 | 1.873 | 3 | 1.4047 | 8.4 | 8.4 | 1379800 | 2 | 164261.9048 | 6.0878
1865 | 1865 | CL3-712 | ROSCOMMON | ROSCOMMON | SS-236 | Creagh 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.568 | 10 | 0.805 | 3 | 0.805 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
1866 | 1866 | CL3-713 | CORK | CORK | SS-433 | Lee Bridge 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.57 | 13 | 1.1 | 3 | 1.1 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718
1867 | 1867 | CL3-714 | TIPPERARY | TIPPERARY | SS-348 | Furle 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.728 | 4 | 0.492 | 3 | 0.492 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1868 | 1868 | CL3-715 | GALWAY | CLARE | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.845 | 7 | 3.191 | 3 | 2.3933 | 16.8 | 16.8 | 839680 | 4 | 49980.9524 | 20.0076
1869 | 1869 | CL3-716 | OFFALY | OFFALY | SS-167 | Cushaling 110kV Substation | EirGrid | 110000 | low | 110000 | 5.289 | 6 | 1.166 | 3 | 1.166 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424
1870 | 1870 | CL3-717 | GALWAY | GALWAY | SS-439 | Loughrea 38kV Substation | ESB Networks | 38000 | 38000 | low | 15.644 | 16 | 1.594 | 3 | 1.1955 | 4.2 | 4.2 | 1703340 | 1 | 405557.1429 | 2.4657
1871 | 1871 | CL3-718 | LAOIS | LAOIS | SS-470 | Mountmellick 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.441 | 8 | 0.394 | 3 | 0.394 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1872 | 1872 | CL3-719 | GALWAY | GALWAY | SS-639 | Tonroe 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.124 | 9 | 0.375 | 3 | 0.375 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1873 | 1873 | CL3-720 | TIPPERARY | OFFALY | SS-084 | Birr 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.248 | 7 | 1.529 | 3 | 1.1467 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1874 | 1874 | CL3-721 | CORK | CORK | SS-261 | Milane Hill 38kV Station | ESB Networks | 38000 |  |  | 6.445 | 7 | 0.848 | 3 | 0.848 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1875 | 1875 | CL3-722 | GALWAY | GALWAY | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.737 | 12 | 0.582 | 3 | 0.582 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
1876 | 1876 | CL3-723 | CLARE | CLARE | SS-107 | Gort 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.418 | 13 | 0.608 | 3 | 0.608 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718
1877 | 1877 | CL3-724 | LIMERICK | LIMERICK | SS-588 | Kilmallock 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.57 | 6 | 0.479 | 3 | 0.479 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1878 | 1878 | CL3-725 | TIPPERARY | LAOIS | SS-053 | Ikerrin 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 6.671 | 7 | 2.629 | 3 | 1.9718 | 12.6 | 12.6 | 1785370 | 7 | 141696.0317 | 7.0574
1879 | 1879 | CL3-726 | TIPPERARY | TIPPERARY | SS-455 | Ardfinnan 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.234 | 10 | 0.49 | 3 | 0.49 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
1880 | 1880 | CL3-727 | KILKENNY | KILKENNY | SS-489 | Ballyhale 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.861 | 6 | 1.103 | 3 | 1.103 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1881 | 1881 | CL3-728 | KILKENNY | KILKENNY | SS-492 | Graigue 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.556 | 6 | 2.168 | 3 | 1.626 | 8.4 | 8.4 | 769410 | 4 | 91596.4286 | 10.9175
1882 | 1882 | CL3-729 | KILKENNY | KILKENNY | SS-492 | Graigue 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.425 | 3 | 0.809 | 3 | 0.809 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
1883 | 1883 | CL3-730 | KILKENNY | KILKENNY | SS-492 | Graigue 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.355 | 6 | 1.918 | 3 | 1.4385 | 8.4 | 8.4 | 769410 | 4 | 91596.4286 | 10.9175
1884 | 1884 | CL3-731 | OFFALY | OFFALY | SS-530 | Esker 110kV Substation | EirGrid | 110000 | 20000 | 110000 | 5.893 | 6 | 0.534 | 3 | 0.534 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424
1885 | 1885 | CL3-732 | LIMERICK | LIMERICK | SS-527 | Rathkeale 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.726 | 5 | 1.034 | 3 | 1.034 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1886 | 1886 | CL3-733 | TIPPERARY | TIPPERARY | SS-043 | Thurles 110kV Substation | EirGrid | 110000 |  |  | 5.455 | 6 | 0.727 | 3 | 0.727 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424
1887 | 1887 | CL3-734 | GALWAY | GALWAY | SS-236 | Creagh 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 10.654 | 11 | 4.748 | 3 | 3.561 | 25.2 | 25.2 | 1324920 | 5 | 52576.1905 | 19.02
1888 | 1888 | CL3-735 | CORK | CORK | SS-577 | Whitechurch 38kV Substation | ESB Networks | 38000 | 38000 | low | 9.557 | 10 | 3.947 | 3 | 2.9603 | 21 | 21 | 1050490 | 4 | 50023.3333 | 19.9907
1889 | 1889 | CL3-736 | CLARE | CLARE | SS-483 | Birdhill 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.057 | 11 | 0.748 | 3 | 0.748 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
1890 | 1890 | CL3-737 | CLARE | CLARE | SS-503 | Scariff 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.932 | 8 | 4.787 | 3 | 3.5903 | 25.2 | 25.2 | 1058430 | 5 | 42001.1905 | 23.8088
1891 | 1891 | CL3-738 | CLARE | CLARE | SS-483 | Birdhill 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.593 | 9 | 0.887 | 3 | 0.887 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1892 | 1892 | CL3-739 | LAOIS | LAOIS | SS-275 | Mountrath ESB Telecoms 38kV Radio Site | ESB Networks | 38000 | 38000 | low | 5.981 | 6 | 0.379 | 3 | 0.379 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1893 | 1893 | CL3-740 | GALWAY | GALWAY | SS-235 | Lisheeny 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.388 | 11 | 1.654 | 3 | 1.2405 | 8.4 | 8.4 | 1485200 | 2 | 176809.5238 | 5.6558
1894 | 1894 | CL3-741 | OFFALY | WESTMEATH | SS-168 | Derryiron 110kV Substation | EirGrid | 110000 |  |  | 8.639 | 9 | 1.059 | 3 | 1.059 | 4.2 | 4.2 | 1890770 | 7 | 450183.3333 | 2.2213
1895 | 1895 | CL3-742 | WATERFORD | WATERFORD | SS-482 | Foxhole 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.814 | 4 | 0.49 | 3 | 0.49 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1896 | 1896 | CL3-743 | TIPPERARY | TIPPERARY | SS-347 | Glengoole 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.046 | 3 | 0.788 | 3 | 0.788 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
1897 | 1897 | CL3-744 | CLARE | CLARE | SS-149 | Tulla 38kV Substation | ESB Networks | 38000 |  |  | 5.327 | 6 | 0.516 | 3 | 0.516 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1898 | 1898 | CL3-745 | KERRY | KERRY | SS-706 | Scartaglin 38kV Substation | ESB Networks | 38000 | low | 38000 | 5.847 | 6 | 0.619 | 3 | 0.619 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1899 | 1899 | CL3-746 | TIPPERARY | TIPPERARY | SS-645 | Toomevara 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.373 | 13 | 2.481 | 3 | 1.8607 | 12.6 | 12.6 | 1627650 | 3 | 129178.5714 | 7.7412
1900 | 1900 | CL3-747 | OFFALY | OFFALY | SS-066 | Thornsberry 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 7.115 | 8 | 0.21 | 3 | 0.21 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285
1901 | 1901 | CL3-748 | CLARE | CLARE | SS-503 | Scariff 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 6.185 | 7 | 0.814 | 3 | 0.814 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1902 | 1902 | CL3-749 | OFFALY | OFFALY | SS-311 | Clonminch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 7.476 | 8 | 0.422 | 3 | 0.422 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1903 | 1903 | CL3-750 | LAOIS | LAOIS | SS-311 | Clonminch 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 8.966 | 9 | 0.576 | 3 | 0.576 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1904 | 1904 | CL3-751 | LAOIS | LAOIS | SS-275 | Mountrath ESB Telecoms 38kV Radio Site | ESB Networks | 38000 | 38000 | low | 6.773 | 7 | 0.544 | 3 | 0.544 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1905 | 1905 | CL3-752 | KERRY | KERRY | SS-337 | Knockaneden 38kV Substation | ESB Networks | 38000 | low | 38000 | 17.489 | 18 | 0.41 | 3 | 0.41 | 4.2 | 4.2 | 1808740 | 1 | 430652.381 | 2.3221
1906 | 1906 | CL3-753 | OFFALY | OFFALY | SS-168 | Derryiron 110kV Substation | EirGrid | 110000 |  |  | 2.766 | 3 | 0.323 | 3 | 0.323 | 4.2 | 4.2 | 1574570 | 7 | 374897.619 | 2.6674
1907 | 1907 | CL3-754 | LEITRIM | LEITRIM | SS-304 | Arigna 110kV Substation | EirGrid | 110000 | 110000 | 20000 | 7.753 | 8 | 0.244 | 3 | 0.244 | 4.2 | 4.2 | 1838070 | 7 | 437635.7143 | 2.285
1908 | 1908 | CL3-755 | CAVAN | LEITRIM | SS-508 | Ballyconnell 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.745 | 8 | 0.544 | 3 | 0.544 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1909 | 1909 | CL3-756 | ROSCOMMON | SLIGO | SS-206 | Boyle 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 6.039 | 7 | 0.594 | 3 | 0.594 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1910 | 1910 | CL3-757 | ROSCOMMON | SLIGO | SS-206 | Boyle 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 5.963 | 6 | 0.271 | 3 | 0.271 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1911 | 1911 | CL3-758 | ROSCOMMON | ROSCOMMON | SS-206 | Boyle 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 12.101 | 13 | 1.905 | 3 | 1.4287 | 8.4 | 8.4 | 1590600 | 2 | 189357.1429 | 5.281
1912 | 1912 | CL3-759 | ROSCOMMON | ROSCOMMON | SS-171 | Castlerea 38kV Substation | ESB Networks | 38000 | 38000 | low | 4.479 | 5 | 0.267 | 3 | 0.267 | 4.2 | 4.2 | 699140 | 4 | 166461.9048 | 6.0074
1913 | 1913 | CL3-760 | ROSCOMMON | ROSCOMMON | SS-171 | Castlerea 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.96 | 7 | 0.448 | 3 | 0.448 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1914 | 1914 | CL3-761 | SLIGO | SLIGO | SS-042 | Ballytivnan 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 6.652 | 7 | 0.913 | 3 | 0.913 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1915 | 1915 | CL3-762 | LEITRIM | LEITRIM | SS-178 | Manorhamilton 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 9.196 | 10 | 0.484 | 3 | 0.484 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
1916 | 1916 | CL3-763 | ROSCOMMON | ROSCOMMON | SS-206 | Boyle 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 6.216 | 7 | 0.665 | 3 | 0.665 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1917 | 1917 | CL3-764 | SLIGO | SLIGO | SS-031 | Sligo 110kV Substation | EirGrid | 110000 | 110000 | 38000 | 5.826 | 6 | 0.731 | 3 | 0.731 | 4.2 | 4.2 | 1732670 | 7 | 412540.4762 | 2.424
1918 | 1918 | CL3-765 | GALWAY | GALWAY | SS-175 | Ballygar 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.87 | 3 | 1.51 | 3 | 1.1325 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
1919 | 1919 | CL3-766 | GALWAY | GALWAY | SS-175 | Ballygar 38kV Substation | ESB Networks | 38000 | 38000 | low | 6.566 | 7 | 0.557 | 3 | 0.557 | 4.2 | 4.2 | 839680 | 4 | 199923.8095 | 5.0019
1920 | 1920 | CL3-767 | ROSCOMMON | ROSCOMMON | SS-696 | Sliabh Bawn 110kV Substation | EirGrid | 110000 | low | 110000 | 5.094 | 6 | 7.086 | 3 | 5.3145 | 37.8 | 37.8 | 2621410 | 10 | 69349.4709 | 14.4197
1921 | 1921 | CL3-768 | ROSCOMMON | ROSCOMMON | SS-575 | Aghamore 38kV Substation | ESB Networks | 38000 | 38000 | low | 12.766 | 13 | 0.428 | 3 | 0.428 | 4.2 | 4.2 | 1545240 | 1 | 367914.2857 | 2.718
1922 | 1922 | CL3-769 | WEXFORD | LONGFORD | SS-247 | Edgeworthstown 38kV Substation | ESB Networks | 38000 | 38000 | low | 7.115 | 8 | 0.753 | 3 | 0.753 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1923 | 1923 | CL3-770 | WEXFORD | LONGFORD | SS-247 | Edgeworthstown 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.774 | 11 | 1.297 | 3 | 0.97275 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
1924 | 1924 | CL3-771 | WESTMEATH | WESTMEATH | SS-247 | Edgeworthstown 38kV Substation | ESB Networks | 38000 | 38000 | low | 10.873 | 11 | 0.525 | 3 | 0.525 | 4.2 | 4.2 | 1439840 | 1 | 342819.0476 | 2.917
1925 | 1925 | CL3-772 | WESTMEATH | WESTMEATH | SS-246 | Loughanalla 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 9.619 | 10 | 0.353 | 3 | 0.353 | 4.2 | 4.2 | 1387140 | 1 | 330271.4286 | 3.0278
1926 | 1926 | CL3-773 | WESTMEATH | WESTMEATH | SS-246 | Loughanalla 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.685 | 8 | 1.27 | 3 | 0.9525 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1927 | 1927 | CL3-774 | WESTMEATH | WESTMEATH | SS-246 | Loughanalla 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 7.755 | 8 | 0.424 | 3 | 0.424 | 4.2 | 4.2 | 909950 | 4 | 216654.7619 | 4.6156
1928 | 1928 | CL3-775 | WEXFORD | LONGFORD | SS-067 | Finnea 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.646 | 6 | 3.912 | 3 | 2.934 | 21 | 21 | 769410 | 4 | 36638.5714 | 27.2936
1929 | 1929 | CL3-776 | WESTMEATH | WESTMEATH | SS-067 | Finnea 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.088 | 6 | 0.585 | 3 | 0.585 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1930 | 1930 | CL3-777 | WEXFORD | LONGFORD | SS-067 | Finnea 38kV Substation | ESB Networks | 38000 | 38000 | low | 2.894 | 3 | 0.632 | 3 | 0.632 | 4.2 | 4.2 | 558600 | 4 | 133000 | 7.5188
1931 | 1931 | CL3-778 | MEATH | MEATH | SS-067 | Finnea 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.119 | 6 | 0.458 | 3 | 0.458 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1932 | 1932 | CL3-779 | LONGFORD | LONGFORD | SS-247 | Edgeworthstown 38kV Substation | ESB Networks | 38000 | 38000 | low | 5.535 | 6 | 1.273 | 3 | 0.95475 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1933 | 1933 | CL3-780 | LONGFORD | LONGFORD | SS-067 | Finnea 38kV Substation | ESB Networks | 38000 | 38000 | low | 11.015 | 12 | 0.717 | 3 | 0.717 | 4.2 | 4.2 | 1492540 | 1 | 355366.6667 | 2.814
1934 | 1934 | CL3-781 | WESTMEATH | WESTMEATH | SS-517 | Delvin 38kV Substation | ESB Networks | 38000 | 38000 | low | 3.116 | 4 | 0.729 | 3 | 0.729 | 4.2 | 4.2 | 628870 | 4 | 149730.9524 | 6.6786
1935 | 1935 | CL3-782 | WESTMEATH | MEATH | SS-517 | Delvin 38kV Substation | ESB Networks | 38000 | 38000 | low | 8.97 | 9 | 0.537 | 3 | 0.537 | 4.2 | 4.2 | 1334440 | 1 | 317723.8095 | 3.1474
1936 | 1936 | CL3-783 | WESTMEATH | WESTMEATH | SS-059 | Kinnegad 110kV | EirGrid | 110000 |  |  | 6.292 | 7 | 0.764 | 3 | 0.764 | 4.2 | 4.2 | 1785370 | 7 | 425088.0952 | 2.3525
1937 | 1937 | CL3-784 | WESTMEATH | WESTMEATH | SS-526 | Newbrook 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 5.966 | 6 | 0.427 | 3 | 0.427 | 4.2 | 4.2 | 769410 | 4 | 183192.8571 | 5.4587
1938 | 1938 | CL3-785 | MONAGHAN | CAVAN | SS-466 | Cootehill 38kV Substation | ESB Networks | 38000 | 38000 | 10000 | 3.181 | 4 | 1.646 | 3 | 1.2345 | 8.4 | 8.4 | 628870 | 4 | 74865.4762 | 13.3573
1939 | 1939 | CL3-786 | MAYO | MAYO | SS-317 | Newport 38kV Substation | ESB Networks | 38000 | 38000 | 20000 | 12.066 | 13 | 2.632 | 3 | 1.974 | 12.6 | 12.6 | 1627650 | 3 | 129178.5714 | 7.7412

## ETRI_Cost
Tsiropoulos I, Tarvydas, D, Zucker, A, Cost development of low carbon energy technologies - Scenario-based cost trajectories to 2050, 2017 Edition, EUR 29034 EN, Publications Office of the European Union, Luxembourg, 2018, ISBN 978-92-79-77479-9, doi:10.2760/490059, JRC109894.
Wind energy
Input assumptions on learning rate method for onshore wind energy
|  |  | Unit | 2015 | 2020 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050
| Global deployment | Baseline | GW | 403.6677 | 606.1493 | 766.3975 | 926.6458 | 1073.6547 | 1220.6637 | 1370.5899 | 1520.5162
|  | Diversified | GW | 403.6677 | 785 | 1222.5 | 1660 | 2043 | 2426 | 2731.5 | 3037
|  | ProRES | GW | 403.6677 | 783.8804 | 1483.7708 | 2183.6612 | 2842.8862 | 3502.1113 | 3972.8269 | 4443.5425
| Global capacity additions | Baseline | GW/year | 45 | 40 | 38 | 37 | 57 | 71 | 65 | 74
|  | Diversified | GW/year | 45 | 76 | 77 | 109 | 107 | 115 | 129 | 147
|  | ProRES | GW/year | 45 | 76 | 133 | 159 | 165 | 167 | 185 | 212
| Learning rate | Reference | % | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5%
|  | High | % | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10%
|  | Low | % | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2%
| Lifetime | - | Years | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Input assumptions on learning rate method for offshore wind energy
|  |  | Unit | 2015 | 2020 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050
| Global deployment | Baseline | GW | 11.6367 | 29.8487 | 38.2874 | 46.726 | 60.0416 | 73.3571 | 90.6381 | 107.9191
|  | Diversified | GW | 11.6367 | 37.9091 | 79.9545 | 122 | 194.5 | 267 | 352 | 437
|  | ProRES | GW | 11.6367 | 36.5152 | 181.5043 | 326.4934 | 570.1989 | 813.9044 | 972.5537 | 1131.2029
| Global capacity additions | Baseline | GW/year | 2 | 4 | 2 | 2 | 3 | 3 | 5 | 7
|  | Diversified | GW/year | 2 | 5 | 5 | 12 | 14 | 15 | 17 | 24
|  | ProRES | GW/year | 2 | 5 | 21 | 37 | 49 | 49 | 44 | 26
| Learning rate | Reference | % | 11% | 11% | 8% | 5% | 5% | 5% | 5% | 5%
|  | High | % | 20% | 20% | 15% | 10% | 10% | 10% | 10% | 10%
|  | Low | % | 5% | 5% | 5% | 2% | 2% | 2% | 2% | 2%
| Lifetime | - | Years | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Capital investment cost trajectories of onshore wind turbines (low specific capacity, high hub height)
|  |  | Unit | 2015 | 2020 | 2030 | 2040 | 2050
| Capital investment costs | Baseline | EUR 2015/kW | 1850 | 1800 | 1730 | 1670 | 1630
|  | Diversified | EUR 2015/kW | 1850 | 1760 | 1660 | 1600 | 1560
|  | ProRES | EUR 2015/kW | 1850 | 1760 | 1630 | 1560 | 1520
|  | Min | EUR 2015/kW | 1850 | 1670 | 1430 | 1310 | 1230
|  | Max | EUR 2015/kW | 1850 | 1830 | 1800 | 1780 | 1760
| O&M costs | - | %CAPEX | 3% | 3% | 3% | 3% | 3%
Capital investment cost trajectories of onshore wind turbines (medium specific capacity, medium hub height)
|  |  | Unit | 2015 | 2020 | 2030 | 2040 | 2050
| Capital investment costs | Baseline | EUR 2015/kW | 1350 | 1310 | 1260 | 1220 | 1190
|  | Diversified | EUR 2015/kW | 1350 | 1290 | 1210 | 1170 | 1130
|  | ProRES | EUR 2015/kW | 1350 | 1290 | 1190 | 1140 | 1110
|  | Min | EUR 2015/kW | 1350 | 1220 | 1040 | 960 | 900
|  | Max | EUR 2015/kW | 1350 | 1330 | 1320 | 1300 | 1280
| O&M costs | - | %CAPEX | 3% | 3% | 3% | 3% | 3%
Capital investment cost trajectories of onshore wind turbines (high specific capacity, low hub height)
|  |  | Unit | 2015 | 2020 | 2030 | 2040 | 2050
| Capital investment costs | Baseline | EUR 2015/kW | 1090 | 1060 | 1020 | 980 | 960
|  | Diversified | EUR 2015/kW | 1090 | 1040 | 980 | 940 | 920
|  | ProRES | EUR 2015/kW | 1090 | 1040 | 960 | 920 | 890
|  | Min | EUR 2015/kW | 1090 | 990 | 840 | 770 | 730
|  | Max | EUR 2015/kW | 1090 | 1080 | 1060 | 1050 | 1040
| O&M costs | - | %CAPEX | 3% | 3% | 3% | 3% | 3%
Capital investment cost trajectories of offshore wind turbines (monopole, medium distance to shore)
|  |  | Unit | 2015 | 2020 | 2030 | 2040 | 2050
| Capital investment costs | Baseline | EUR 2015/kW | 3500 | 2990 | 2850 | 2750 | 2640
P-RNW-WIN-OF02 |  | Diversified | EUR 2015/kW | 3500 | 2870 | 2570 | 2430 | 2330
|  | ProRES | EUR 2015/kW | 3500 | 2890 | 2310 | 2150 | 2100
|  | Min | EUR 2015/kW | 3500 | 2390 | 1550 | 1350 | 1280
|  | Max | EUR 2015/kW | 3500 | 3260 | 3180 | 3140 | 3090
| O&M costs | - | %CAPEX | 2% | 2% | 2% | 2% | 2%
Capital investment cost trajectories of offshore wind turbines (jacket, medium distance to shore)
|  |  | Unit | 2015 | 2020 | 2030 | 2040 | 2050
| Capital investment costs | Baseline | EUR 2015/kW | 3600 | 3070 | 2940 | 2830 | 2710
|  | Diversified | EUR 2015/kW | 3600 | 2950 | 2650 | 2490 | 2390
|  | ProRES | EUR 2015/kW | 3600 | 2970 | 2370 | 2220 | 2160
|  | Min | EUR 2015/kW | 3600 | 2460 | 1600 | 1390 | 1320
|  | Max | EUR 2015/kW | 3600 | 3360 | 3280 | 3230 | 3170
| O&M costs | - | %CAPEX | 2% | 2% | 2% | 2% | 2%
Capital investment cost trajectories of offshore wind turbines (floating, long distance to shore)
|  |  | Unit | 2015 | 2020 | 2030 | 2040 | 2050
| Capital investment costs | Baseline | EUR 2015/kW | 5500 | 4690 | 4490 | 4330 | 4140
|  | Diversified | EUR 2015/kW | 5500 | 4510 | 4040 | 3810 | 3660
|  | ProRES | EUR 2015/kW | 5500 | 4540 | 3620 | 3390 | 3300
|  | Min | EUR 2015/kW | 5500 | 3760 | 2440 | 2120 | 2010
|  | Max | EUR 2015/kW | 5500 | 5130 | 5000 | 4930 | 4850
| O&M costs | - | %CAPEX | 2% | 2% | 2% | 2% | 2%
Input assumptions on learning rate method for photovoltaics
|  |  | Unit | 2015 | 2020 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050
| Global deployment | Baseline | GW | 220 | 424.2725 | 533.5946 | 642.9167 | 833.7305 | 1024.5444 | 1244.4583 | 1464.3722
|  | Diversified | GW | 220 | 491.6364 | 826.8182 | 1162 | 1851 | 2540 | 3482 | 4424
|  | ProRES | GW | 220 | 732.0746 | 1785.3218 | 2838.5691 | 3913.0396 | 4987.5101 | 5866.1956 | 6744.881
| Global capacity additions | Baseline | GW/year | 36.2459 | 40.8279 | 23.4352 | 21.1967 | 25.578 | 93.8711 | 91.5764 | 60.6523
|  | Diversified | GW/year | 36.2459 | 54.3007 | 52.4342 | 82.5415 | 128.6777 | 190.0459 | 242.5007 | 241.0342
|  | ProRES | GW/year | 36.2459 | 102.3883 | 174.4386 | 247.7633 | 232.6818 | 240.23 | 283.3748 | 344.9264
| Learning rate | Reference | % | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20%
|  | High | % | 23% | 23% | 23% | 23% | 23% | 23% | 23% | 23%
|  | Low | % | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10%
| Lifetime | - | Years | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Capital investment cost trajectories of utility-scale photovoltaics with one-axis tracking
|  |  | Unit | 2015 | 2020 | 2030 | 2040 | 2050
| Capital investment costs | Baseline | EUR 2015/kW | 1120 | 910 | 790 | 640 | 550
P-RNW-SOL-PV03 |  | Diversified | EUR 2015/kW | 1120 | 860 | 650 | 500 | 410
|  | ProRES | EUR 2015/kW | 1120 | 760 | 490 | 400 | 350
|  | Min | EUR 2015/kW | 1120 | 710 | 430 | 340 | 280
|  | Max | EUR 2015/kW | 1120 | 1010 | 950 | 860 | 800
| O&M costs | - | %CAPEX | 2.3% | 2.3% | 2.3% | 2.3% | 2.3%
Capital investment cost trajectories of utility-scale photovoltaics without tracking
|  |  | Unit | 2015 | 2020 | 2030 | 2040 | 2050
| Capital investment costs | Baseline | EUR 2015/kW | 1020 | 830 | 720 | 580 | 500
P-RNW-SOL-PV02 |  | Diversified | EUR 2015/kW | 1020 | 790 | 600 | 450 | 370
|  | ProRES | EUR 2015/kW | 1020 | 690 | 450 | 370 | 320
|  | Min | EUR 2015/kW | 1020 | 650 | 390 | 310 | 260
|  | Max | EUR 2015/kW | 1020 | 920 | 870 | 780 | 730
| O&M costs | - | %CAPEX | 1.7% | 1.7% | 1.7% | 1.7% | 1.7%
Capital investment cost trajectories of commercial-scale PV, flat surface
|  |  | Unit | 2015 | 2020 | 2030 | 2040 | 2050
| Capital investment costs | Baseline | EUR 2015/kW | 1140 | 920 | 810 | 650 | 560
P-RNW-SOL-PV01 |  | Diversified | EUR 2015/kW | 1140 | 880 | 670 | 510 | 410
|  | ProRES | EUR 2015/kW | 1140 | 770 | 500 | 410 | 350
|  | Min | EUR 2015/kW | 1140 | 720 | 430 | 350 | 290
|  | Max | EUR 2015/kW | 1140 | 1030 | 970 | 880 | 810
| O&M costs | - | %CAPEX | 2.5% | 2.5% | 2.5% | 2.5% | 2.5%
Capital investment cost trajectories of residential-scale PV, inclined surface
|  |  | Unit | 2015 | 2020 | 2030 | 2040 | 2050
| Capital investment costs | Baseline | EUR 2015/kW | 1360 | 1100 | 960 | 780 | 670
|  | Diversified | EUR 2015/kW | 1360 | 1050 | 800 | 600 | 490
|  | ProRES | EUR 2015/kW | 1360 | 920 | 600 | 490 | 420
|  | Min | EUR 2015/kW | 1360 | 860 | 520 | 410 | 350
|  | Max | EUR 2015/kW | 1360 | 1230 | 1150 | 1050 | 970
| O&M costs | - | %CAPEX | 2% | 2% | 2% | 2% | 2%
Solar thermal electricity
Input assumptions on learning rate method for solar thermal electricity
|  |  | Unit | 2015 | 2020 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050
| Global deployment | Baseline | GW | 4.659 | 8.2512 | 15.0153 | 21.7795 | 44.2465 | 66.7134 | 100.2314 | 133.7494
|  | Diversified | GW | 4.659 | 55.5455 | 129.2727 | 203 | 384 | 565 | 752 | 939
|  | ProRES | GW | 4.659 | 31.2167 | 217.9766 | 404.7365 | 694.4169 | 984.0973 | 1228.6729 | 1473.2485
| Global capacity additions | Baseline | GW/year | 0.67972 | 0.71844 | 1.1238 | 1.6657 | 3.4019 | 5.7531 | 6.1471 | 8.6582
|  | Diversified | GW/year | 0.67972 | 10.1773 | 8.0909 | 21.4838 | 34 | 38.5683 | 36.8797 | 48.7773
|  | ProRES | GW/year | 0.67972 | 5.3115 | 19.0235 | 55.7643 | 58.9661 | 57.0743 | 53.7279 | 50.0936
| Learning rate | Reference | % | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7%
|  | High | % | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10%
|  | Low | % | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4%
| Lifetime | - | Years | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Capital investment cost trajectories of parabolic trough with storage
|  |  | Unit | 2015 | 2020 | 2030 | 2040 | 2050
| Capital investment costs | Baseline | EUR 2015/kW | 6000 | 5650 | 5100 | 4530 | 4200
|  | Diversified | EUR 2015/kW | 6000 | 4630 | 4040 | 3630 | 3420
|  | ProRES | EUR 2015/kW | 6000 | 4920 | 3760 | 3430 | 3280
|  | Min | EUR 2015/kW | 6000 | 4120 | 3040 | 2660 | 2490
|  | Max | EUR 2015/kW | 6000 | 5800 | 5470 | 5120 | 4910
| O&M costs | - | %CAPEX | 1.7% | 1.7% | 1.7% | 1.7% | 1.7%
Capital investment cost trajectories of solar tower with storage
|  |  | Unit | 2015 | 2020 | 2030 | 2040 | 2050
| Capital investment costs | Baseline | EUR 2015/kW | 5280 | 4970 | 4480 | 3990 | 3690
|  | Diversified | EUR 2015/kW | 5280 | 4070 | 3560 | 3190 | 3010
|  | ProRES | EUR 2015/kW | 5280 | 4330 | 3310 | 3010 | 2880
|  | Min | EUR 2015/kW | 5280 | 3620 | 2680 | 2340 | 2190
|  | Max | EUR 2015/kW | 5280 | 5110 | 4820 | 4510 | 4320
| O&M costs | - | %CAPEX | 1.7% | 1.7% | 1.7% | 1.7% | 1.7%
Geothermal energy
Input assumptions on learning rate method for geothermal energy
|  |  | Unit | 2015 | 2020 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050
| Global deployment | Baseline | GW | 11.848 | 18.1573 | 23.3078 | 28.4583 | 36.2244 | 43.9904 | 54.674 | 65.3577
|  | Diversified | GW | 11.848 | 24.5455 | 37.2727 | 50 | 70.5 | 91 | 118 | 145
|  | ProRES | GW | 11.848 | 28.2956 | 82.4163 | 136.537 | 230.8791 | 325.2212 | 405.2954 | 485.3696
| Global capacity additions | Baseline | GW/year | 0.34464 | 1.2619 | 1.0212 | 2.7047 | 1.4924 | 1.9732 | 2.3211 | 3.5589
|  | Diversified | GW/year | 0.34464 | 2.5395 | 2.0909 | 4.6657 | 4.0722 | 4.487 | 6.3446 | 7.3395
|  | ProRES | GW/year | 0.34464 | 3.2895 | 8.1911 | 15.1229 | 19.101 | 18.9951 | 18.4676 | 17.1963
| Learning rate | Reference | % | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5%
|  | High | % | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10%
|  | Low | % | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2%
| Lifetime | - | Years | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Capital investment cost trajectories of flash geothermal
|  |  | Unit | 2015 | 2020 | 2030 | 2040 | 2050
| Capital investment costs | Baseline | EUR 2015/kW | 3540 | 3430 | 3260 | 3160 | 3060
P-RNW-GEO01 |  | Diversified | EUR 2015/kW | 3540 | 3350 | 3150 | 3020 | 2910
|  | ProRES | EUR 2015/kW | 3540 | 3320 | 2940 | 2760 | 2680
|  | Min | EUR 2015/kW | 3540 | 3100 | 2420 | 2130 | 2000
|  | Max | EUR 2015/kW | 3540 | 3500 | 3430 | 3390 | 3340
| O&M costs | - | %CAPEX | 2% | 2% | 2% | 2% | 2%
Capital investment cost trajectories of Organic Rankine Cycle (binary) geothermal
|  |  | Unit | 2015 | 2020 | 2030 | 2040 | 2050
| Capital investment costs | Baseline | EUR 2015/kW | 6970 | 6750 | 6410 | 6230 | 6030
P-RNW-GEO02 |  | Diversified | EUR 2015/kW | 6970 | 6600 | 6190 | 5950 | 5720
|  | ProRES | EUR 2015/kW | 6970 | 6540 | 5790 | 5440 | 5270
|  | Min | EUR 2015/kW | 6970 | 6110 | 4760 | 4190 | 3930
|  | Max | EUR 2015/kW | 6970 | 6880 | 6740 | 6670 | 6580
| O&M costs | - | %CAPEX | 2% | 2% | 2% | 2% | 2%
Capital investment cost trajectories of Enhanced Geothermal System
|  |  | Unit | 2015 | 2020 | 2030 | 2040 | 2050
| Capital investment costs | Baseline | EUR 2015/kW | 11790 | 11420 | 10840 | 10540 | 10200
|  | Diversified | EUR 2015/kW | 11790 | 11170 | 10480 | 10060 | 9680
|  | ProRES | EUR 2015/kW | 11790 | 11050 | 9800 | 9210 | 8920
|  | Min | EUR 2015/kW | 11790 | 10330 | 8060 | 7090 | 6650
|  | Max | EUR 2015/kW | 11790 | 11640 | 11410 | 11280 | 11140
| O&M costs | - | %CAPEX | 2% | 2% | 2% | 2% | 2%
Ocean energy
Input assumptions on learning rate method for ocean energy
|  |  | Unit | 2015 | 2020 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050
| Global deployment | Baseline | GW | 0.5335 | 0.6409 | 1.922 | 3.2031 | 7.9781 | 12.7532 | 23.16 | 33.5669
|  | Diversified | GW | 0.5335 | 2.0909 | 4.5455 | 7 | 24.5 | 42 | 112 | 182
|  | ProRES | GW | 0.5335 | 10.7977 | 52.8796 | 94.9615 | 206.5501 | 318.1388 | 434.8203 | 551.5018
| Global capacity additions | Baseline | GW/year | 0.05254 | 0.074501 | 0.16362 | 0.34996 | 0.93398 | 1.1031 | 1.7 | 2.9763
|  | Diversified | GW/year | 0.05254 | 0.3645 | 0.18182 | 0.80114 | 2.4525 | 4.9645 | 10.1818 | 18.8011
|  | ProRES | GW/year | 0.05254 | 2.1059 | 5.2899 | 11.544 | 22.1286 | 24.6653 | 30.318 | 33.1885
| Learning rate | Reference | % | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10%
|  | High | % | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
|  | Low | % | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7%
| Lifetime | - | Years | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Capital investment cost trajectories of tidal range
|  |  | Unit | 2015 | 2020 | 2030 | 2040 | 2050
| Capital investment costs | Baseline | EUR 2015/kW | 6160 | 5680 | 4630 | 3760 | 3230
|  | Diversified | EUR 2015/kW | 6160 | 4920 | 4140 | 3150 | 2520
|  | ProRES | EUR 2015/kW | 6160 | 3890 | 2800 | 2320 | 2090
|  | Min | EUR 2015/kW | 6160 | 3030 | 1830 | 1370 | 1170
|  | Max | EUR 2015/kW | 6160 | 5830 | 5060 | 4390 | 3950
| O&M costs | - | %CAPEX | 6.3% | 6.5% | 5.6% | 6.3% | 4.9%
Capital investment cost trajectories of tidal stream
|  |  | Unit | 2015 | 2020 | 2030 | 2040 | 2050
| Capital investment costs | Baseline | EUR 2015/kW | 7840 | 7230 | 5900 | 4790 | 4120
P-RNW-OCE-TID02 |  | Diversified | EUR 2015/kW | 7840 | 6260 | 5270 | 4000 | 3210
|  | ProRES | EUR 2015/kW | 7840 | 4950 | 3560 | 2950 | 2660
|  | Min | EUR 2015/kW | 7840 | 3850 | 2320 | 1740 | 1480
|  | Max | EUR 2015/kW | 7840 | 7420 | 6440 | 5580 | 5030
| O&M costs | - | %CAPEX | 6.3% | 6.5% | 5.6% | 6.3% | 4.9%
Capital investment cost trajectories of wave energy
|  |  | Unit | 2015 | 2020 | 2030 | 2040 | 2050
| Capital investment costs | Baseline | EUR 2015/kW | 7910 | 7300 | 5950 | 4830 | 4150
P-RNW-OCE-WAV01 |  | Diversified | EUR 2015/kW | 7910 | 6310 | 5320 | 4040 | 3240
|  | ProRES | EUR 2015/kW | 7910 | 4990 | 3600 | 2980 | 2690
|  | Min | EUR 2015/kW | 7910 | 3890 | 2350 | 1750 | 1500
|  | Max | EUR 2015/kW | 7910 | 7480 | 6500 | 5630 | 5070
| O&M costs | - | %CAPEX | 4% | 4% | 3.5% | 4% | 4%
Hydropower
Input assumptions on learning rate method for hydropower
|  |  | Unit | 2015 | 2020 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | Input assumptions on learning rate method for natural gas combined cycle plants with CCS, post-combustion | [10 empty] | Learning rate method input assumptions for biomass IGCC plants with CCS, pre-combustion
| Global deployment | Baseline | GW | 1207.8528 | 1234.5284 | 1297.2784 | 1360.0284 | 1435.9835 | 1511.9387 | 1583.9051 | 1655.8715 |  |  | Unit | 2015 | 2020 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 |  |  | Unit | 2015 | 2020 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050
|  | Diversified | GW | 1207.8528 | 1245.8182 | 1411.4091 | 1577 | 1720 | 1863 | 2028 | 2193 | Global installed capacity | Baseline | GW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Global installed capacity | Baseline | GW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | ProRES | GW | 1207.8528 | 1315.6587 | 1356.2528 | 1396.847 | 1421.0211 | 1445.1952 | 1474.1695 | 1503.1437 |  | Diversified | GW | 0 | 0 | 1.7701 | 21.7001 | 72.4863 | 145.7324 | 224.634 | 285.9324 |  | Diversified | GW | 0 | 0 | 0.62264 | 1.7352 | 9.3802 | 33.991 | 99.675 | 162.2248
| Global capacity additions | Baseline | GW/year | 36.6543 | 5.3351 | 12.0709 | 13.0291 | 13.8658 | 16.5162 | 15.3436 | 13.443 | Global capacity additions | Baseline | GW/year | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Global capacity additions | Baseline | GW/year | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Diversified | GW/year | 36.6543 | 7.5931 | 33.6364 | 32.6 | 22.6 | 34.6 | 33.6 | 32.4 |  | Diversified | GW/year | 0 | 0 | 0.35402 | 3.986 | 10.1572 | 14.6492 | 15.7803 | 12.2597 |  | Diversified | GW/year | 0 | 0 | 0.12453 | 0.22251 | 1.529 | 4.9221 | 13.2613 | 12.7325
|  | ProRES | GW/year | 36.6543 | 21.5612 | 9.8227 | 6.415 | 5.4351 | 4.2345 | 5.2793 | 6.3104 | Learning rate | Reference | % | 2.2% | 2.2% | 2.2% | 2.2% | 2.2% | 2.2% | 2.2% | 2.2% | Learning rate | Reference | % | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5%
| Learning rate | Reference | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% |  | High | % | 3.6% | 3.6% | 3.6% | 3.6% | 3.6% | 3.6% | 3.6% | 3.6% |  | High | % | 7.6% | 7.6% | 7.6% | 7.6% | 7.6% | 7.6% | 7.6% | 7.6%
|  | High | % | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% |  | Low | % | 1.2% | 1.2% | 1.2% | 1.2% | 1.2% | 1.2% | 1.2% | 1.2% |  | Low | % | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5%
|  | Low | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Lifetime | - | Years | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Lifetime | - | Years | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
| Lifetime | - | Years | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
| Capital investment cost trajectories of large-scale low-cost hydropower and dam | [12 empty] | Unit | 2015 | 2020 | 2030 | 2040 | 2050 | [5 empty] | Unit | 2015 | 2020 | 2030 | 2040 | 2050
|  |  | Unit | 2015 | 2020 | 2030 | 2040 | 2050 |  |  |  | Capital investment costs | Baseline | EUR 2015/kW | - | - | 1510 | 1510 | 1510 |  |  |  | Capital investment costs | Baseline | EUR 2015/kW | - | - | 5800 | 5800 | 5800
| Capital investment costs | Baseline | EUR 2015/kW | 1090 | 1090 | 1090 | 1090 | 1090 |  |  |  |  | Diversified | EUR 2015/kW |  | - | 1390 | 1310 | 1280 |  |  |  |  | Diversified | EUR 2015/kW |  | - | 5380 | 4310 | 3840
|  | Diversified | EUR 2015/kW | 1090 | 1090 | 1090 | 1080 | 1080 |  |  |  |  | Min | EUR 2015/kW |  | - | 1320 | 1190 | 1150 |  |  |  |  | Min | EUR 2015/kW |  | - | 5160 | 3680 | 3070
|  | ProRES | EUR 2015/kW | 1090 | 1090 | 1090 | 1090 | 1090 |  |  |  |  | Max | EUR 2015/kW |  | - | 1510 | 1510 | 1510 |  |  |  |  | Max | EUR 2015/kW |  | - | 5800 | 5800 | 5800
|  | Min | EUR 2015/kW | 1090 | 1090 | 1080 | 1080 | 1070 |  |  |  | O&M costs | - | %CAPEX | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% |  |  |  | O&M costs | - | %CAPEX | 2.3% | 2.3% | 2.3% | 2.3% | 2.3%
|  | Max | EUR 2015/kW | 1090 | 1090 | 1090 | 1090 | 1090
| O&M costs | - | %CAPEX | 0.5% | 0.5% | 0.5% | 0.5% | 0.5%
Capital investment cost trajectories of large-scale high-cost hydropower and dam
|  |  | Unit | 2015 | 2020 | 2030 | 2040 | 2050
| Capital investment costs | Baseline | EUR 2015/kW | 3500 | 3500 | 3490 | 3490 | 3480
P-RNW-HYD-DAM01 |  | Diversified | EUR 2015/kW | 3500 | 3500 | 3490 | 3480 | 3470
|  | ProRES | EUR 2015/kW | 3500 | 3500 | 3490 | 3490 | 3490
|  | Min | EUR 2015/kW | 3500 | 3490 | 3470 | 3460 | 3440
|  | Max | EUR 2015/kW | 3500 | 3500 | 3500 | 3500 | 3500
| O&M costs | - | %CAPEX | 0.5% | 0.5% | 0.5% | 0.5% | 0.5%
Capital investment cost trajectories of medium-scale low-cost hydropower and dam
|  |  | Unit | 2015 | 2020 | 2030 | 2040 | 2050
| Capital investment costs | Baseline | EUR 2015/kW | 1410 | 1410 | 1410 | 1410 | 1400
|  | Diversified | EUR 2015/kW | 1410 | 1410 | 1400 | 1400 | 1400
|  | ProRES | EUR 2015/kW | 1410 | 1410 | 1410 | 1410 | 1410
|  | Min | EUR 2015/kW | 1410 | 1410 | 1400 | 1390 | 1390
|  | Max | EUR 2015/kW | 1410 | 1410 | 1410 | 1410 | 1410
| O&M costs | - | %CAPEX | 0.5% | 0.5% | 0.5% | 0.5% | 0.5%
Capital investment cost trajectories of medium-scale high-cost hydropower and dam
|  |  | Unit | 2015 | 2020 | 2030 | 2040 | 2050
| Capital investment costs | Baseline | EUR 2015/kW | 4000 | 4000 | 3990 | 3990 | 3980
P-RNW-HYD-DAM02 |  | Diversified | EUR 2015/kW | 4000 | 4000 | 3980 | 3970 | 3970
|  | ProRES | EUR 2015/kW | 4000 | 4000 | 3990 | 3990 | 3990
|  | Min | EUR 2015/kW | 4000 | 3990 | 3970 | 3950 | 3930
|  | Max | EUR 2015/kW | 4000 | 4000 | 4000 | 4000 | 4000
| O&M costs | - | %CAPEX | 0.5% | 0.5% | 0.5% | 0.5% | 0.5%
Capital investment cost trajectories of small-scale low-cost hydropower and dam
|  |  | Unit | 2015 | 2020 | 2030 | 2040 | 2050
| Capital investment costs | Baseline | EUR 2015/kW | 1740 | 1740 | 1740 | 1730 | 1730
|  | Diversified | EUR 2015/kW | 1740 | 1740 | 1730 | 1730 | 1730
|  | ProRES | EUR 2015/kW | 1740 | 1740 | 1740 | 1740 | 1730
|  | Min | EUR 2015/kW | 1740 | 1740 | 1730 | 1720 | 1710
|  | Max | EUR 2015/kW | 1740 | 1740 | 1740 | 1740 | 1740
| O&M costs | - | %CAPEX | 1% | 1% | 1% | 1% | 1%
Capital investment cost trajectories of small-scale high-cost hydropower and dam
|  |  | Unit | 2015 | 2020 | 2030 | 2040 | 2050
| Capital investment costs | Baseline | EUR 2015/kW | 5000 | 5000 | 4990 | 4980 | 4980
P-RNW-HYD-DAM03 |  | Diversified | EUR 2015/kW | 5000 | 5000 | 4980 | 4970 | 4960
|  | ProRES | EUR 2015/kW | 5000 | 4990 | 4990 | 4990 | 4980
|  | Min | EUR 2015/kW | 5000 | 4990 | 4960 | 4940 | 4910
|  | Max | EUR 2015/kW | 5000 | 5000 | 5000 | 5000 | 5000
| O&M costs | - | %CAPEX | 1% | 1% | 1% | 1% | 1%
Capital investment cost trajectories of run-of-river plants
|  |  | Unit | 2015 | 2020 | 2030 | 2040 | 2050
| Capital investment costs | Baseline | EUR 2015/kW | 3000 | 3000 | 2990 | 2990 | 2990
P-RNW-HYD-ROR04 |  | Diversified | EUR 2015/kW | 3000 | 3000 | 2990 | 2980 | 2970
|  | ProRES | EUR 2015/kW | 3000 | 3000 | 2990 | 2990 | 2990
|  | Min | EUR 2015/kW | 3000 | 2990 | 2980 | 2960 | 2950
|  | Max | EUR 2015/kW | 3000 | 3000 | 3000 | 3000 | 3000
| O&M costs | - | %CAPEX | 0.5% | 0.5% | 0.5% | 0.5% | 0.5%
Biomass heat and power
Input assumptions on learning rate method for biomass heat and power
|  |  | Unit | 2015 | 2020 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050
| Global deployment | Baseline | GW | 84.0222 | 182.0787 | 204.2258 | 226.373 | 250.4981 | 274.6232 | 312.4253 | 350.2275
|  | Diversified | GW | 84.0222 | 245 | 326.5 | 408 | 557.5 | 707 | 916.5 | 1126
|  | ProRES | GW | 84.0222 | 193.8579 | 293.112 | 392.3662 | 475.286 | 558.2058 | 652.1021 | 745.9984
| Global capacity additions | Baseline | GW/year | 5.0339 | 19.6113 | 11.3267 | 5.4271 | 6.8788 | 11.6807 | 26.7928 | 19.2661
|  | Diversified | GW/year | 5.0339 | 32.1956 | 25.001 | 15.494 | 29.0756 | 39.6339 | 78.9956 | 62.001
|  | ProRES | GW/year | 5.0339 | 21.9671 | 24.0025 | 23.5941 | 19.7535 | 22.3239 | 42.4351 | 41.0931
| Learning rate | Reference | % | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5%
|  | High | % | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7%
|  | Low | % | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2%
| Lifetime | - | Years | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Capital investment cost trajectories of biomass subcritical steam turbine CHP plant
|  |  | Unit | 2015 | 2020 | 2030 | 2040 | 2050
| Capital investment costs | Baseline | EUR 2015/kW | 3600 | 3400 | 3310 | 3230 | 3120
|  | Diversified | EUR 2015/kW | 3600 | 3330 | 3180 | 3050 | 2910
|  | ProRES | EUR 2015/kW | 3600 | 3380 | 3190 | 3100 | 2980
|  | Min | EUR 2015/kW | 3600 | 3220 | 3020 | 2850 | 2660
|  | Max | EUR 2015/kW | 3600 | 3520 | 3480 | 3450 | 3400
| O&M costs | - | %CAPEX | 2% | 2% | 2% | 2% | 2%
Capital investment cost trajectories of gasified biomass CHP plant
|  |  | Unit | 2015 | 2020 | 2030 | 2040 | 2050
| Capital investment costs | Baseline | EUR 2015/kW | 5300 | 5010 | 4870 | 4760 | 4590
|  | Diversified | EUR 2015/kW | 5300 | 4900 | 4680 | 4490 | 4280
|  | ProRES | EUR 2015/kW | 5300 | 4980 | 4700 | 4560 | 4390
|  | Min | EUR 2015/kW | 5300 | 4740 | 4450 | 4190 | 3920
|  | Max | EUR 2015/kW | 5300 | 5180 | 5130 | 5080 | 5010
| O&M costs | - | %CAPEX | 2% | 2% | 2% | 2% | 2%
Capital investment cost trajectories of biomass-fired Organic Rankine Cycle
|  |  | Unit | 2015 | 2020 | 2030 | 2040 | 2050
| Capital investment costs | Baseline | EUR 2015/kW | 4700 | 4440 | 4320 | 4220 | 4070
|  | Diversified | EUR 2015/kW | 4700 | 4340 | 4150 | 3980 | 3800
|  | ProRES | EUR 2015/kW | 4700 | 4420 | 4160 | 4040 | 3900
|  | Min | EUR 2015/kW | 4700 | 4200 | 3950 | 3720 | 3480
|  | Max | EUR 2015/kW | 4700 | 4600 | 4540 | 4510 | 4440
| O&M costs | - | %CAPEX | 2% | 2% | 2% | 2% | 2%
Capital investment cost trajectories of anaerobic digestion plants
|  |  | Unit | 2015 | 2020 | 2030 | 2040 | 2050
| Capital investment costs | Baseline | EUR 2015/kW | 3100 | 2930 | 2850 | 2780 | 2680
P-RNW-AB-BIO04 |  | Diversified | EUR 2015/kW | 3100 | 2860 | 2740 | 2630 | 2510
|  | ProRES | EUR 2015/kW | 3100 | 2910 | 2750 | 2670 | 2570
|  | Min | EUR 2015/kW | 3100 | 2770 | 2600 | 2450 | 2290
|  | Max | EUR 2015/kW | 3100 | 3030 | 3000 | 2970 | 2930
| O&M costs | - | %CAPEX | 4% | 4% | 4% | 4% | 4%
Carbon Capture and Storage
Input assumptions on learning rate method for pulverised coal plants with CCS, post-combustion
|  |  | Unit | 2015 | 2020 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050
| Global installed capacity | Baseline | GW | 0 | 0 | 0.19914 | 1.2041 | 2.2342 | 3.2901 | 5.3724 | 10.4941
|  | Diversified | GW | 0 | 0 | 5.8038 | 42.3077 | 137.1224 | 266.6627 | 345.9952 | 283.9047
| Global capacity additions | Baseline | GW/year | 0 | 0 | 0.039827 | 0.201 | 0.20602 | 0.21117 | 0.41645 | 1.0244
|  | Diversified | GW/year | 0 | 0 | 1.1608 | 7.3008 | 18.9629 | 25.9081 | 15.8665 | 0
| Learning rate | Reference | % | 2.1% | 2.1% | 2.1% | 2.1% | 2.1% | 2.1% | 2.1% | 2.1%
|  | High | % | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5%
|  | Low | % | 1.1% | 1.1% | 1.1% | 1.1% | 1.1% | 1.1% | 1.1% | 1.1%
| Lifetime | - | Years | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
|  |  | Unit | 2015 | 2020 | 2030 | 2040 | 2050
| Capital investment costs | Baseline | EUR 2015/kW | - | - | 2760 | 2680 | 2580
*P-TH-SC-COA-CCS04 |  | Diversified | EUR 2015/kW |  | - | 2740 | 2590 | 2570
|  | Min | EUR 2015/kW |  | - | 2630 | 2400 | 2360
|  | Max | EUR 2015/kW |  | - | 2830 | 2790 | 2740
| O&M costs | - | %CAPEX | 2.1% | 2.1% | 2.1% | 2.1% | 2.1%
Input assumptions on learning rate method for pulverised coal plants with CCS, oxyfuel
|  |  | Unit | 2015 | 2020 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050
| Global installed capacity | Baseline | GW | 0 | 0 | 0.19914 | 1.2041 | 2.2342 | 3.2901 | 5.3724 | 10.4941
|  | Diversified | GW | 0 | 0 | 5.8038 | 42.3077 | 137.1224 | 266.6627 | 345.9952 | 283.9047
| Global capacity additions | Baseline | GW/year | 0 | 0 | 0.039827 | 0.201 | 0.20602 | 0.21117 | 0.41645 | 1.0244
|  | Diversified | GW/year | 0 | 0 | 1.1608 | 7.3008 | 18.9629 | 25.9081 | 15.8665 | 0
| Learning rate | Reference | % | 2.8% | 2.8% | 2.8% | 2.8% | 2.8% | 2.8% | 2.8% | 2.8%
|  | High | % | 4.4% | 4.4% | 4.4% | 4.4% | 4.4% | 4.4% | 4.4% | 4.4%
|  | Low | % | 1.4% | 1.4% | 1.4% | 1.4% | 1.4% | 1.4% | 1.4% | 1.4%
| Lifetime | - | Years | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Capital investment cost trajectories of pulverised coal plants with CCS, oxyfuel
|  |  | Unit | 2015 | 2020 | 2030 | 2040 | 2050
| Capital investment costs | Baseline | EUR 2015/kW | - | - | 2710 | 2600 | 2480
*P-TH-SC-COA-CCS05 |  | Diversified | EUR 2015/kW |  | - | 2690 | 2490 | 2470
|  | Min | EUR 2015/kW |  | - | 2560 | 2270 | 2240
|  | Max | EUR 2015/kW |  | - | 2810 | 2750 | 2690
| O&M costs | - | %CAPEX | 2.3% | 2.3% | 2.3% | 2.3% | 2.3%
Input assumptions on learning rate method for lignite IGCC plants with CCS, pre-combustion
|  |  | Unit | 2015 | 2020 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050
| Global installed capacity | Baseline | GW | 0 | 0 | 0.19914 | 1.2041 | 2.2342 | 3.2901 | 5.3724 | 10.4941
|  | Diversified | GW | 0 | 0 | 5.8038 | 42.3077 | 137.1224 | 266.6627 | 345.9952 | 283.9047
| Global capacity additions | Baseline | GW/year | 0 | 0 | 0.039827 | 0.201 | 0.20602 | 0.21117 | 0.41645 | 1.0244
|  | Diversified | GW/year | 0 | 0 | 1.1608 | 7.3008 | 18.9629 | 25.9081 | 15.8665 | 0
| Learning rate | Reference | % | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5%
|  | High | % | 7.6% | 7.6% | 7.6% | 7.6% | 7.6% | 7.6% | 7.6% | 7.6%
|  | Low | % | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5%
| Lifetime | - | Years | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
|  |  | Unit | 2015 | 2020 | 2030 | 2040 | 2050
| Capital investment costs | Baseline | EUR 2015/kW | - | - | 3920 | 3640 | 3340
*P-TH-IGCC-PEA-CCS05 |  | Diversified | EUR 2015/kW |  | - | 3870 | 3380 | 3310
|  | Min | EUR 2015/kW |  | - | 3570 | 2900 | 2810
|  | Max | EUR 2015/kW |  | - | 4200 | 4040 | 3880
| O&M costs | - | %CAPEX | 2.2% | 2.2% | 2.2% | 2.2% | 2.2%
Input assumptions on learning rate method for coal IGCC plants with CCS, pre-combustion
|  |  | Unit | 2015 | 2020 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050
| Global installed capacity | Baseline | GW | 0 | 0 | 0.19914 | 1.2041 | 2.2342 | 3.2901 | 5.3724 | 10.4941
|  | Diversified | GW | 0 | 0 | 5.8038 | 42.3077 | 137.1224 | 266.6627 | 345.9952 | 283.9047
| Global capacity additions | Baseline | GW/year | 0 | 0 | 0.039827 | 0.201 | 0.20602 | 0.21117 | 0.41645 | 1.0244
|  | Diversified | GW/year | 0 | 0 | 1.1608 | 7.3008 | 18.9629 | 25.9081 | 15.8665 | 0
| Learning rate | Reference | % | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5%
|  | High | % | 7.6% | 7.6% | 7.6% | 7.6% | 7.6% | 7.6% | 7.6% | 7.6%
|  | Low | % | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5%
| Lifetime | - | Years | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
|  |  | Unit | 2015 | 2020 | 2030 | 2040 | 2050
| Capital investment costs | Baseline | EUR 2015/kW | - | - | 2580 | 2390 | 2200
*P-TH-IGCC-COA-CCS06 |  | Diversified | EUR 2015/kW |  | - | 2540 | 2220 | 2180
|  | Min | EUR 2015/kW |  | - | 2350 | 1900 | 1850
|  | Max | EUR 2015/kW |  | - | 2760 | 2660 | 2550
| O&M costs | - | %CAPEX | 3% | 3% | 3% | 3% | 3%
Learning rate method input assumptions for biomass IGCC plants with CCS, pre-combustion
|  |  | Unit | 2015 | 2020 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050
| Global installed capacity | Baseline | GW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Diversified | GW | 0 | 0 | 0.62264 | 1.7352 | 9.3802 | 33.991 | 99.675 | 162.2248
| Global capacity additions | Baseline | GW/year | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Diversified | GW/year | 0 | 0 | 0.12453 | 0.22251 | 1.529 | 4.9221 | 13.2613 | 12.7325
| Learning rate | Reference | % | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5%
|  | High | % | 7.6% | 7.6% | 7.6% | 7.6% | 7.6% | 7.6% | 7.6% | 7.6%
|  | Low | % | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5%
| Lifetime | - | Years | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Capital investment cost trajectories of biomass IGCC plants with CCS, pre-combustion
|  |  | Unit | 2015 | 2020 | 2030 | 2040 | 2050
| Capital investment costs | Baseline | EUR 2015/kW | - | - | 5800 | 5800 | 5800
|  | Diversified | EUR 2015/kW |  | - | 5380 | 4310 | 3840
|  | Min | EUR 2015/kW |  | - | 5160 | 3680 | 3070
|  | Max | EUR 2015/kW |  | - | 5800 | 5800 | 5800
| O&M costs | - | %CAPEX | 2.3% | 2.3% | 2.3% | 2.3% | 2.3%
Input assumptions on learning rate method for natural gas combined cycle plants with CCS, post-combustion
|  |  | Unit | 2015 | 2020 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050
| Global installed capacity | Baseline | GW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Diversified | GW | 0 | 0 | 1.7701 | 21.7001 | 72.4863 | 145.7324 | 224.634 | 285.9324
| Global capacity additions | Baseline | GW/year | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Diversified | GW/year | 0 | 0 | 0.35402 | 3.986 | 10.1572 | 14.6492 | 15.7803 | 12.2597
| Learning rate | Reference | % | 2.2% | 2.2% | 2.2% | 2.2% | 2.2% | 2.2% | 2.2% | 2.2%
|  | High | % | 3.6% | 3.6% | 3.6% | 3.6% | 3.6% | 3.6% | 3.6% | 3.6%
|  | Low | % | 1.2% | 1.2% | 1.2% | 1.2% | 1.2% | 1.2% | 1.2% | 1.2%
| Lifetime | - | Years | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Capital investment cost trajectories of natural gas combined cycle plants with CCS, post-combustion
|  |  | Unit | 2015 | 2020 | 2030 | 2040 | 2050
| Capital investment costs | Baseline | EUR 2015/kW | - | - | 1510 | 1510 | 1510
*P-TH-CCGT-GAS-CCS04 |  | Diversified | EUR 2015/kW |  | - | 1390 | 1310 | 1280
|  | Min | EUR 2015/kW |  | - | 1320 | 1190 | 1150
|  | Max | EUR 2015/kW |  | - | 1510 | 1510 | 1510
| O&M costs | - | %CAPEX | 2.5% | 2.5% | 2.5% | 2.5% | 2.5%